Section 22 1343.16 
Facility Wet-Well Packaged Sewage Pumping Stations (Interior)

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 3 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Mechanical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

  - *************************************************************************************************************

Part 1 - GENERAL

SECTION INCLUDES

Submersible pumps, basin, and equipment for sanitary sewer lift station.

Pump Materials

Pump Construction

Performance

Protective Coating

Accessories

Motor Control Center

related requiremnts

Section << 01 2500 - Substitution Procedures>>.

Section << 01 3300 - Submittal Procedures>>.

REFERENCE STANDARDS

ASTM A48/A48M - Standard Specification for Gray Iron Castings.

ASTM A276/A276M - Standard Specification for Stainless Steel Bars and Shapes.

NEMA EN 10250 - Enclosures for Electrical Equipment (1000 Volts Maximum).

NEMA MG 00001 - Motors and Generators.

SUBMITTALS

Submit the following in accordance with Section << 01 3300 - Submittal Procedures>>:

Catalog data.

Pump curves.

Operation and maintenance data.

Theory of operation.

Test procedure.

Operating procedures.

Maintenance requirements.

Warranties.

WARRANTY

Manufacturer's printed warranties shall apply to pumps.

Provide two year warranty after installation, including parts and labor.

Provide for repairs to be performed at the manufacturer's authorized warranty repair station located within a 200 mile radius of this Project.

LANL PERFORMED WORK

LANL Utilities will perform acceptance inspection, testing, adjusting and tie-in of lift station. See PART 3.

Part 2 - PRODUCTS

MANUFACTURERS

ABS (Piranha “S” Series), Homa, Sta-Rite, Hydromatic; provide grinder pump series.

Product options and substitutions

Alternate products may be accepted; follow Section ​<< 01 2500 - Substitution Procedures>>​.

PERFORMANCE AND DESIGN REQUIREMENTS

See EQUIPMENT SCHEDULE in PART 3.

Pumps shall be readily removable and replaceable without de-watering wet well or disconnecting any piping in wet well.

PUMP MATERIALS

Motor housing, casing, discharge elbow, and other components: Gray cast iron, <<ASTM A48/A48M>>, ANSI Class 30.

Impeller: <<ASTM A48/A48M>> cast iron or <<ASTM A276/A276M>> 440C stainless steel, hardened.  Replaceable impeller wear ring.

Cutters: <<ASTM A276/A276M>> 440C stainless steel, hardened.

Shaft: Stainless steel.

Motor:

Rotor bars and short circuit rings: Aluminum.

Windings: Copper.

Stator winding and lead insulation: <<NEMA MG 00001>> Class F.

Mechanical Seals:

Lower: Tungsten carbide/tungsten carbide.

Upper: Tungsten carbide/carbon.

Case Wear Ring: Steel with molded nitrile rubber.

Exposed Nuts and Bolts, Hardware: ANSI 304 stainless steel.

PUMP CONSTRUCTION

Water tight sealing rings against machined surfaces.

Cable Entry Design:

Seal: Torque-free mechanical compression type with strain relief.  Submersible cable entry shall be field replaceable without replacing cable.

Seal junction chamber from motor area.

Pump Motor:

Dip and bake stator three times in NEMA Class F varnish and heat shrink fit into the stator housing.  Do not use designs requiring penetration of stator housing.

Pump Shaft Bearings

Permanently lubricated heavy duty, single row ball bearings.

Minimum B10 Bearing Life: 20,000 hours at any point on head-capacity curve.

Mechanical Seals: Tandem independent and run in a standard motor oil reservoir.

Impeller: Dynamically balanced, double shrouded, non-clog, with vane capable of handling solids, unless otherwise scheduled.

Provide sliding guide bar bracket unit to guide on at least two rails which is an integral part of pump unit.  Do not permit any portion of the pump or guidance system to bear on sump floor.  Do not use guide cables.

Provide metal-to-metal discharge pump/elbow connection seal.  Do not use diaphragm or O-ring type seals.

PERFORMANCE

Pump Motor:

Enclosed submersible type.

3-phase motor.

Non-overloading throughout pump curve.

Capable of running dry indefinitely without damage.

Motor shall be rated for the site elevation.

PROTECTIVE COATING

Pump Exterior: Enamel or epoxy coating finish.

ACCESSORIES

      - ***************************************************************************************

      - Designer to select one of the two following paragraphs. If selecting the second, include all subparagraphs below it.

      - ***************************************************************************************

Pump accessories supplied by pump manufacturer.

      - *** OR ***

Provide pump accessories required for proper installation and/or as recommended by manufacturer, including the following:

Upper and intermediate guide bar brackets with stainless steel nuts and bolts.

Stainless steel guide rails and brackets with stainless steel nuts and bolts.

Stainless steel lift chain.

Safety chain hook.

Cable holder for pump cable and float cable.

Cable support grip.

Anchorage.

Cable rack for level control floats.

Self-weighted float switches.

Check valve, resilient seated, low resistance ball operation.

Plug valve, eccentric, flanged ends, line size, BUNA packing, neoprene plug facings, lever handle, DeZurik series 100, Fig. No. 118.

Standard discharge connection.

Controls

RACO Verbatim – including the following.

Enclosure – <<NEMA EN 10250>> Type 4X.

Environmental – Heater.

Local alarm relay output.

Milltronics Hydro-Ranger 200, Part No. 7ML1034 - 1AA1 with Echomax XPS-10 transducer, Part No. 7ML1115 - 0CA31.

<<NEMA EN 10250>> Type 4X enclosure box for mounting of RACO Verbatim outside of, but attached to, motor control center.  Provide connections in motor control center for RACO Verbatim unit.

Telephone line grounding/terminator box, Hoffman No. A-1086CHQRFG, with 1/2 inch plywood backing plate mounted inside. Mount box beside and connect to the RACO Verbatim box with 3/4 inch conduit nipple.

RACO Verbatim enclosure and backplate, Hoffman No. A-201608LP and No. A-20P16.

MOTOR CONTROL CENTER

      - ***************************************************************************************

      - Designer to select one of the two following paragraphs.

      - ***************************************************************************************

Duplex pump control panel supplied by pump supplier.

Manufacturer: << E.G. Pumps Controls; or  Hydromatic Q-panel>>.

      - *** OR ***

Provide duplex pump controls required for proper installation and/or as recommended by manufacturer and mounted inside equipment room, including the following:

If MCC is required provide it with separate cubicle to accommodate Milltronics unit with glass view port on door.

Two pump Circuit Breakers:  UL interrupting rating not less than 14,000 amperes RMS symmetrical at 480 volts or 22,000 amperes RMS symmetrical at 240 volts.

Two NEMA rated, full voltage non-reversing motor starters.

Duplex Logic Chassis (an anodized aluminum sub-assembly) with Logic Panel Including:

Two Hand-Off-Auto selector switches.

Two run pilot lights (red).

Two off pilot lights (green).

Level alarm pilot light.

Alarm silence pushbutton.

Motor over temperature sensor – shut pump down.

LED status indication pilot lights for each relay function.

Ground lugs for pump and service connections.

Enclosure Type 3R.

Additional control breaker - 15 amp, 1 pole.

Control power transformer - 2 KVA, 16.7 amps.

Phase Monitor Relay, 200-240 volt or 440-480 volt, 3 phase as required; capable of detecting loss of a single phase, under-voltage, over voltage, and voltage unbalance. Alarm will be sent to the RACO Verbatim unit.

Lightning surge arrestor.

Elapsed time meter for each pump.

Lag pump time delay relay.

Seal failure relay with pilot light.

Audible Alarm horn, 93 dB at 20 feet.

Alarm beacon with flasher.

Alarm memory circuit to maintain alarm beacon until manually reset.

Alarm and control enclosure.

Additional isolated dry contacts:

Motor over-temperature (2) - contact type form "C".

Motor overload trip (2) - contact type normally open.

Seal failure (2) - contact type form "C".

Power failure - contact type form "C".

High level float status light.

High level float test switch.

Local control panel disconnect. Mount beside, but exterior to, the control panel.

Main breaker.

Operating voltage sign and station name.

PART 3 - EXECUTION

iNSTALLATION

Install pumps, basin, and equipment in accordance with manufacturer's instructions and Subcontract Drawings.

Install pumps level, plumb, accurately aligned, with leak-proof pump connection, and easily removed without entering wet well.

Make no splices in cable.

Furnish and install all power connections to and from the motor control center, control panel, and monitors in accordance with provisions of Division 16 and the manufacturer’s instructions.

Provide communications link between the lift station monitoring/controls panel and the building automation system PC.  Links, monitors, and controls shall be compatible with the building automation system.  System shall be installed and available for testing during the Acceptance Inspection.

HIGH LEVEL FLOAT

Suspend on bracket per manufacturers instructions and as shown on Drawings.

Make no splices in cable.

Adjust float level per manufacturer’s instructions.

MANUFACTURER'S ON-SITE SERVICE

Arrange for a factory trained service engineer to be present to check installation and operation.

Arrange for a factory trained service engineer to provide a minimum of 4 hours per pump station of training to operating personnel on operation and maintenance of pumping equipment.

Provide a report by the service engineer certifying that equipment has been installed and is operating correctly.

LANL ACCEPTANCE INSPECTION, TESTING, ADJUSTING, AND TIE-IN

LANL Subcontract Technical Representative (STR) will contact LANL’s Facilities Management Representative at least 10 working days in advance to witness and accept the following:

Inspection, testing, and adjusting of alarms and controls on lift station.

Inspection of lift station for compliance with drawings and specifications.

LANL STR to ensure all drains or buildings connected to the lift station has an approved WPF (Waste Profile Form) for discharge to the sanitary sewer for all anticipated wastewaters.

EQUIPMENT SCHEDULE

Site elevation: 7500 feet.

Pump Model ​<< _______>>​ with Impeller Model ​<< _______>>​.

GPM/TDH (feet): << _______>>.

HP: << _______>>.

Discharge Pipe (inches): << _______>>.

RPM: << _______>>.

Volts/Phase: << _______>>.

Max motor Input at design point (KW): << _______>>.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 22 1343.16, REV. 3, DATED APRIL 15, 2026.