Section 22 1413 
Facility Storm Drainage Piping

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 4 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Mechanical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

      - Refer to Section ​<< 33 4000 - Storm Drainage Utilities>>​ for Site Storm Drainage Utilities.

  - *************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

Building storm drainage piping, fittings, and accessories within 5 feet of building wall.

        - ******************************************************************************

        - The following subparagraphs are designer choices.

        - ******************************************************************************

Storm Drainage Piping, Above Ground

Roof Drains

Cleanouts

related requirements

Section << 01 2500 - Substitution Procedures>>.

Section << 01 3300 - Submittal Procedures>>.

Section ​<< 07 8400 - Firestopping>>​.

Section ​<< 22 0529 - Hangers and Supports for Plumbing Piping and Equipment>>​.

Section ​<< 22 0554 - Identification for Plumbing,  HVAC, and Fire Piping and Equipment>>​.

Section ​<< 22 0713 - Plumbing and HVAC Insulation>>​.

Section ​<< 22 0813 - Testing Piping Systems>>​.

reference standards

ASME A112.6.4 - Roof, Deck, and Balcony Drains.

ASME A112.36.2 - Cleanouts.

ASTM A74 - Standard Specification for Cast Iron Soil Pipe and Fittings.

ASTM C564 - Standard Specification for Rubber Gaskets for Cast Iron Soil Pipe and Fittings.

ASTM D2564 - Standard Specification for Solvent Cements for Poly(Vinyl Chloride) (PVC) Plastic Piping Systems.

ASTM D2665 - Standard Specification for Poly(Vinyl Chloride) (PVC) Plastic Drain, Waste, and Vent Pipe and Fittings.

ASTM D2855 - Standard Practice for the Two-Step (Primer and Solvent Cement) Method of Joining Poly (Vinyl Chloride) (PVC) or Chlorinated Poly (Vinyl Chloride) (CPVC) Pipe and Piping Components with Tapered Sockets.

ASTM D3034 - Standard Specification for Type PSM Poly(Vinyl Chloride) (PVC) Sewer Pipe and Fittings.

ASTM F656 - Standard Specification for Primers for Use in Solvent Cement Joints of Poly(Vinyl Chloride) (PVC) and Chlorinated Poly(Vinyl Chloride) (CPVC) Plastic Pipe and Fittings.

CISPI 301 - Standard Specification for Hubless Cast Iron Soil Pipe and Fittings for Sanitary and Storm Drain, Waste, and Vent Piping Applications.

CISPI 310 - Specification for Coupling for Use in Connection with Hubless Cast Iron Soil Pipe and Fittings for Sanitary and Storm Drain, Waste, and Vent Piping Applications.

IAPMO (UPC) - Uniform Plumbing Code.

NSF/ANSI 14 - Plastic Piping System Components and Related Materials.

SUBMITTALS

Submit the following in accordance with Section << 01 3300 - Submittal Procedures>>:

Catalog data on pipe materials, fittings, and accessories.

Manufacturer's Installation Instructions for piping and accessories.

      - ***************************************************************************************

      - The following Article is activated automatically based on PVC piping material selections made in Article Storm Drainage Piping, Above Ground in PART 2.

      - ***************************************************************************************

QUALITY ASSURANCE

Comply with <<NSF/ANSI 14>> for PVC piping components.

PART 2 - PRODUCTS

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section << 01 2500 - Substitution Procedures>>.

      - ***************************************************************************************

      - Retain the following three Articles based on project-scope.

      - ***************************************************************************************

STORM DRAINAGE PIPING, ABOVE GROUND

      - ***************************************************************************************

      - The following four paragraphs are designer choices.

      - ***************************************************************************************

Cast Iron Pipe and Fittings: <<CISPI 301>> hubless, service weight.

Joints:  <<CISPI 310>>, neoprene gaskets and stainless steel clamp/shield assemblies.

Cast Iron Pipe and Fittings: <<ASTM A74>>, service weight, bell and spigot ends.

Joints:  Hub and spigot, CISPI HSN compression type with <<ASTM C564>>, neoprene gaskets.

PVC Pipe and Fittings: <<ASTM D3034>>, SDR 35, polyvinyl chloride (PVC) material.

Joints:  <<ASTM D2855>>​, solvent weld with <<ASTM D2564>> solvent cement and <<ASTM F656>>  primer.

PVC Pipe and Fittings: <<ASTM D2665>>, polyvinyl chloride (PVC) material.

Joints:  <<ASTM D2855>>, solvent weld with <<ASTM D2564>> solvent cement and <<ASTM F656>>  primer.

ROOF DRAINS

      - ***************************************************************************************

      - Edit the following descriptive specifications to identify Project requirements and to eliminate conflicts with manufacturer’s specification.

      - Select roof drains determined by roof construction, expected rainfall, etc.  Refer to manufacturer’s catalog data for selection criteria.

      - ***************************************************************************************

<<ASME A112.6.4>>, Cast iron body and strainer with removable dome​​<< with vandal proof screws; or  None - N/A>>​​.

CLEANOUTS

      - ***************************************************************************************

      - Edit the following descriptive specifications to identify Project requirements and to eliminate conflicts with manufacturer’s specification.

      - Select cleanouts to suit project.  Refer to manufacturer’s catalog data for selection criteria.

      - ***************************************************************************************

<<ASME A112.36.2>>, Cast iron cleanout assembly with ​<< heavy duty;  round; or  square>>​ adjustable, scoriated, ​<< cast iron; or  nickel bronze>>​ cover ​<< with threaded spanner wrench cover; or  with stainless steel access cover secured with machine screw>>​, ​<< and a no-hub outlet;  and a speed-set outlet; or  and an inside caulk outlet>>​.

PART 3 - EXECUTION

PREPARATION

Ream pipe ends and remove burrs.

INSTALLATION

Extend cleanouts to finish floor or wall surface. Lubricate threaded cleanout plugs with non-hardening thread lubricant. Ensure clearance at cleanout for snaking drainage system

Install floor cleanouts at elevation to accommodate finished floor.

Route piping in orderly manner and maintain gradient. Route parallel and perpendicular to walls.

Install piping penetrating roofed areas to maintain integrity of roof assembly.

Install bell and spigot pipe with bell end upstream.

      - ***************************************************************************************

      - The following paragraph is a designer choice.

      - ***************************************************************************************

Sleeve and caulk pipes penetrating exterior walls or interior bearing walls.  Provide waterproof installation for exterior walls.  Provide UL/FM approved through-penetration firestop system when penetrating fire-rated barriers (e.g., walls, floors, etc.). See Section ​​<< 07 8400 - Firestopping>>​​​.

Test piping system with water in accordance with Section ​<< 22 0813 - Testing Piping Systems>>​, at the pressures and durations indicated below.

Storm Water Piping

Storm water piping inside building to 5 Feet outside building: Test with water in accordance with <<IAPMO (UPC)>>.  Fill the entire system with water to the point of overflowing.  Keep water in system for at least 1 hour before inspection starts.  If the system is tested in segments, no piping (except the uppermost 10 feet of the system) shall have been subjected to a test of less than 10 foot head of water.

Acceptable Alternative:  Test with air at 5 psig and hold pressure for at least 15 minutes.

Note: pneumatic testing may not be used for plastic piping.

Label piping in accordance with Section ​<< 22 0554 - Identification for Plumbing,  HVAC, and Fire Piping and Equipment>>​​.

Support piping in accordance with Section ​<< 22 0529 - Hangers and Supports for Plumbing Piping and Equipment>>​.

Insulate piping system in accordance with Section ​<< 22 0713 - Plumbing and HVAC Insulation>>​.

Provide splash blocks under downspout nozzle when required to control erosion.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 22 1413, REV. 4, DATED APRIL 15, 2026.