Section 22 1500 
Compressed-Air Systems

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 7 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Pressure Safety/Mechanical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

      - ==========================================================

      - This template was developed to meet the requirements of ASME B31.9-2020.  Use with a different edition will require a detailed review of the code and LANL ESM Chapter 17 - Pressure Safety.  Note that some items listed in this section may have pressure or temperature ratings below that of the limits of the scope of the code. It is the designer’s responsibility to select components compatible with the design parameters of the piping system.

      - The designer is encouraged to review LANL ESM Chapters 6 - Mechanical, 13 - Welding, Joining & NDE, and 17 - Pressure Safety.

      - NOTE for systems with pressures greater than 150 psig:  These must be constructed to ASME B31.3, Process Piping and this section edited by Design Agency to reflect the requirements of the selected code edition, including verifying that all material specified meets the design pressure/temperature requirements. If designing to ASME B31.3, designer may opt to use Section ​<< 40 0504 - Process Piping>>​ in lieu of this section.

      - For compressed air component details, refer to LANL Mechanical Standard Detail ST-D2090-1, Sheets 1 through 4.

      - Seismic: To properly edit this section for Project-specific seismic requirements, refer to author notes that say/begin with “Seismic” and the “Seismic Specification Editing Guide Mechanical Components” and flowchart posted with the templates for guidance.

  - *************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

      - ***************************************************************************************

      - The following paragraphs are designer choices based on project-specific requirements.

      - ***************************************************************************************

Copper Tubing and Fittings (up to 2 inches)

Steel Pipe and Fittings (up to 2 inches)

Steel Pipe and Fittings (greater than 2 inches)

Valves

Strainer

Flexible Connectors

Prefilter, High-Efficiency Coalescing

Afterfilter, High-Efficiency Particulate

Automatic Drain Valve

Oil/Water Separator

Regenerative Air Dryer

Refrigerated Air Dryer (Air-Cooled)

Pressure Gauge

Pressure Regulators

Dew Point Test Fittings

Pressure Relief Valves

Air Receiver

Air Compressor or Packaged System (1/4 through 30 HP)

      - ***************************************************************************************

      - The following Section << 01 4000 - Quality Requirements - Non-Nuclear>> and Section << 01 4216 - Definitions>> are not referenced in the body of this Section. Including them are a designer choice.

      - ***************************************************************************************

RELATED REQUIREMENTS

Section << 01 2500 - Substitution Procedures>>

Section << 01 3300 - Submittal Procedures>>

Section << 01 4000 - Quality Requirements - Non-Nuclear>>​

Section << 01 4115 - Pressure Safety Submittals>>

Section << 01 4216 - Definitions>>

Section << 01 4444 - Offsite Welding, Brazing and Joining Requirements>>

Section << 01 4455 - Onsite Welding, Brazing and Joining Requirements>>

Section << 01 4525 - Non-Destructive Examination (NDE) Requirements>>

Section << 01 4631 - Welding, Brazing, and Soldering of Pressure Systems>>

Section << 01 4731 - Flange Assembly for Pressure Systems>>​

Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>, for requirements pertaining to << manufacturer’s certification; and  special certification>>.

Section ​<< 05 0520 - Post-Installed Concrete and Grouted Masonry Anchors - Normal Confidence>>​

Section << 07 8400 - Firestopping>>

Section << 22 0529 - Hangers and Supports for Plumbing Piping and Equipment>>

Section << 22 0548.23 - Vibration and Seismic Controls for Mechanical Systems>> for<< seismic-design criteria,; or  None - N/A>> submittal requirements, devices for seismic restraint, and installation requirements for these devices.

Section << 22 0554 - Identification for Plumbing,  HVAC, and Fire Piping and Equipment>>

Section << 22 0713 - Plumbing and HVAC Insulation>>

Section << 22 0813 - Testing Piping Systems>>

      - ***************************************************************************************

      - In the listing below, designer shall eliminate codes and standards that are not applicable to the project and add other codes and standards that are. The referenced standards editions are based on the code of record ASME B31.9-2020 and ASME BPVC-2023. If the Code of Record for the project refers to a different version of ASME B31.9 & ASME BPVC, the designer is responsible to update the years/editions for the invoked standards. If the invoked standards editions do not comply with those referenced by the Code of Record, EOR needs to evaluate and verify those for equal or better. For the standards without an edition/year, the latest edition is to be used. In addition, the designer must ensure the code and standards editions align between sections in the project specification package and the project design drawings.

      - Note: ASCE 7 edition is based on Code of Record IBC 2021.

      - ***************************************************************************************

REFERENCE STANDARDS

ASCE 7 - Minimum Design Loads and Associated Criteria for Buildings and Other Structures.

ASME B1.20.1 - Pipe Threads, General Purpose, Inch.

ASME B16.3 - Malleable Iron Threaded Fittings: Classes 150 and 300.

ASME B16.5 - Pipe Flanges and Flanged Fittings:  NPS 1/2 Through NPS 24 Metric/Inch Standard.

ASME B16.9 - Factory-Made Wrought Buttwelding Fittings.

ASME B16.18 - Cast Copper Alloy Solder Joint Pressure Fittings.

ASME B16.22 - Wrought Copper and Copper Alloy Solder-Joint Pressure Fittings.

ASME B16.34 - Valves — Flanged, Threaded, and Welding End.

ASME B16.39 - Malleable Iron Threaded Pipe Unions:  Classes 150, 250, and 300.

ASME B31.9 - Building Services Piping.

ASME B40.100 - Pressure Gauges and Gauge Attachments.

ASME BPVC-IX - Boiler and Pressure Vessel Code, Section IX - Qualification Standard for Welding, Brazing, and Fusing Procedures; Welders; Brazers; and Welding, Brazing, and Fusing Operators.

ASME BPVC-VIII-1 - Boiler and Pressure Vessel Code, Section VIII, Division 1: Rules for Construction of Pressure Vessels.

ASME BPVC-XIII - Boiler and Pressure Vessel Code, Section XIII: Rules for Overpressure Protection.

ASTM A53/A53M - Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless - 2016 (ASME B31.3), 2012 (ASME B31.9).

ASTM A105/A105M - Standard Specification for Carbon Steel Forgings for Piping Applications - 2014 (ASME B31.9).

ASTM A197/A197M - Standard Specification for Cupola Malleable Iron - 2000(R2015) (ASME B31.9).

ASTM A216/A216M - Standard Specification for Steel Castings, Carbon, Suitable for Fusion Welding, for High-Temperature Service - 2007 (ASME B31.9).

ASTM A234/A234M - Standard Specification for Piping Fittings of Wrought Carbon Steel and Alloy Steel for Moderate and High Temperature Service - 2002 (ASME B31.3), 2015 (ASME B31.9).

ASTM B68/B68M - Standard Specification for Seamless Copper Tube, Bright Annealed - 2002 (ASME B31.3), 2011 (ASME B31.9).

ASTM B75/B75M - Standard Specification for Seamless Copper Tube - 2002 (ASME B31.3), 2011 (ASME B31.9).

ASTM B88 - Standard Specification for Seamless Copper Water Tube - 2003 (ASME B31.3), 2014 (ASME B31.9).

ASTM B280 - Standard Specification for Seamless Copper Tube for Air Conditioning and Refrigeration Field Service - 2008 (ASME B31.3), 2018 (ASME B31.5), 2016 (ASME B31.9).

ISO 1217 - Displacement Compressors - Acceptance Tests.

ISO 8573-1 - Compressed Air — Part 1: Contaminants and Purity Classes.

MSS SP-25 - Standard Marking System for Valves, Fittings, Flanges, and Unions - 2018 (ASME B31.3), 2013 (ASME B31.9).

MSS SP-72 - Ball Valves with Flanged or Butt-Welding Ends for General Service - 2010a (ASME B31.3 & B31.9).

MSS SP-80 - Bronze Gate, Globe, Angle, and Check Valves - 2013 (ASME B31.9).

MSS SP-110 - Ball Valves Threaded, Socket-Welding, Solder Joint, Grooved and Flared Ends - 2010 (ASME B31.9).

MSS SP-136 - Ductile Iron Swing Check Valves - 2020 (ASME B31.9).

NMAC - New Mexico Administrative Code.

SUBMITTALS

Submit the following per Section << 01 3300 - Submittal Procedures>>:

Action Submittals:

Product Data: Include the Manufacturer’s name, model number, parts list, and brief description of equipment and its basic operational features — i.e., data sheet, spec sheet, etc.  Include air compressor performance data at 7,500 ft elevation (LANL site-specific condition).

        - ******************************************************************************

        - The following subparagraph should only be retained when welded, brazed, or soldered joining methods are selected by the Designer.

        - ******************************************************************************

Per the requirements of Section(s) << 01 4444 - Offsite Welding, Brazing and Joining Requirements; and  01 4455 - Onsite Welding, Brazing and Joining Requirements>>, submit:

          - **********************************************************************

          - For high-risk applications such as ML-1 or ML-2, add submittals for "Weld Filler Material Control Procedures" and "Filler Material Certified Material Test Reports (CMTRs)" when required. Add "Post-Weld Heat Treatment Procedures" when required.

          - **********************************************************************

          - *******Note: Only required as a submittal for Onsite welding, when subcontractor not using LANL WPS/PQR*******

Welding Procedure Specification (WPS) and supporting Procedure Qualification Record (PQR).

          - ********Note: Only required as a submittal for Onsite welding, when subcontractor not tested at LANL*******

Welder Performance Qualification Records (WPQR) including continuity.

Per the requirements of Section ​​​​​<< 01 4525 - Non-Destructive Examination (NDE) Requirements>>​​​​​​, submit

Written Practice or Procedure for Qualification and Certification of NDE Personnel

NDE Personnel Qualification Records

NDE Procedures

NDE Procedure Qualification Records (Note: this is not required per <<ASME B31.9>> unless requested by EOR)

NDE Report(s)

NTIP submitted under Section ​​​<< 01 4525 - Non-Destructive Examination (NDE) Requirements>>​​​.

Before fabrication, submit:

Proof of journeyman certificate of competence in accordance with <<NMAC>> 14.6.6.11

Leak test plan submitted under Section ​​​<< 22 0813 - Testing Piping Systems>>​​​.

Cleaning procedures for joint assembly preparation

After fabrication, submit examination records per <<ASME B31.9>> para. 936.3.

Informational Submittals:

Spare Parts and Maintenance Materials list

Installation, Operation, & Maintenance Manual

Warranties

        - ******************************************************************************

        - The following two subparagraphs shall be retained when, respectively, an ASME pressure vessel (whether standalone or part of a compressor package) or an air compressor are specified in the project.

        - ******************************************************************************

Manufacturer’s data report form for ASME pressure vessels (e.g., ASME Form U-1) showing National Board registration.

At closeout: Maintenance Material Submittals

Air compressor inlet air filters, two for each compressor

Belts: ​<< One; or  Two>>​ for each belt-driven compressor

QUALITY ASSURANCE

Material and Installation: Conform to <<ASME B31.9>> for systems operating at pressure of 150 psig or less and at temperature of 200 degrees F or less.

Performance of rotary air compressor shall be tested and rated per CAGI (Compressed Air and Gas Institute) rotary compressor performance verification program (<<ISO 1217>>).

Air quality classification shall be Class ​<< 0;  1;  2;  3; or  4>>​, according to <<ISO 8573-1>>​.

Welders Certification and Qualified Procedure Standards shall be per <<ASME BPVC-IX>>. Welding per Section(s) << 01 4444 - Offsite Welding, Brazing and Joining Requirements; and  01 4455 - Onsite Welding, Brazing and Joining Requirements>>.

NDE Personnel Certification and NDE Procedures shall be per Section << 01 4525 - Non-Destructive Examination (NDE) Requirements>>.

Valve Identification:  Each valve shall bear markings per <<MSS SP-25>>, including manufacturer’s name or trademark, the material of construction, and symbols to indicate the service conditions for which the manufacturer rates the valve.

Component identification shall follow LANL ESM Chapter 1 - General, Section 200, Item Numbering and Labeling. At existing facilities, component labeling conventions are to be continued to be used to avoid confusion.

Design pressure and temperature of piping systems within this Section is provided in the Pressure Safety Implementation Plan, contained in ​<< Drawing Number; or  Document Number>>​ ​<< _______>>​ .

WARRANTY

Provide a minimum of 1-year manufacturer’s warranty, parts and labor, for air compressor system.

PART 2 - PRODUCTS

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Sections << 01 2500 - Substitution Procedures>> and << 01 4115 - Pressure Safety Submittals>>.

Proposal of unlisted components as substituted products is strongly discouraged and shall be evaluated per Section << 01 2500 - Substitution Procedures>>. Substitutions will be allowed only if the Subcontractor can demonstrate that the product can meet the same code requirements of the item specified in the design. Costs associated with evaluation of substituted unlisted components shall be the responsibility of the Subcontractor.

      - ***************************************************************************************

      - The seismic exemptions noted below are based on ASCE 7-16. If the Code of Record for the project refers to a different version of ASCE 7, the Designer is responsible to check the seismic design requirements per that applicable edition.

      - ***************************************************************************************

SEISMIC PERFORMANCE REQUIREMENTS

Piping systems with trapeze assemblies/rod hangers that meet the requirements per <<ASCE 7>>, Section 13.6.7.3 are seismically exempt.

For piping systems not meeting the above exemption, Structural EOR shall design seismic supports per LANL ESM Chapter 5 - Structural, Section II; <<ASCE 7>>, Chapter 13; <<ASME B31.9>><< ; Section  01 8734 - Seismic Qualification of Nonstructural Components (IBC);  ; Section 22 0548.23 - Vibration and Seismic Controls for Mechanical Systems; or  None - N/A>>.

      - ***************************************************************************************

      - On Welding, brazing, soldering:  When specifying joints, consider that welding, brazing, or soldering reduces the tube rating to the fully annealed condition. Welding, brazing, soldering shall meet Section << 01 4631 - Welding, Brazing, and Soldering of Pressure Systems>>.

      - On flanges:  Use Section << 01 4731 - Flange Assembly for Pressure Systems>>.  Use ASME PCC-1, Pressure Boundary Bolted Flange Joint Assembly, for ASME B16.5 flanges.

      - On copper tubing: Designer shall match ASTM spec and the tempers available within that spec to the allowable Conditions listed in ASME B31.9 Table I-1. For example, note that O50 (light annealed) and O60 (soft annealed) may not meet the ASME B31.9 callout for “Annealed” (O61).

      - The following PART 2 Articles are designer choices based on project-specific conditions. Within each Article, paragraphs related to pipe material types, fitting types, component size ranges, etc. are designer choices based on project-specific requirements.

      - ***************************************************************************************

COPPER TUBING AND FITTINGS (UP TO 2 INCHES)

Copper tubing ​<< ASTM B68/B68M;  ASTM B75/B75M;  ASTM B88; or  ASTM B280>>​, Alloy ​<< 102; or  122>>​, Temper ​<< O50;  O60;  O61;  O62;  H55;  H58; or  H80>>​.

Braze Joints

Fittings: ​​<< ASME B16.22; or  ASME B16.18>>​​.

Unions: <<ASME B16.22>>, Class 150, bronze unions with braze joints.

Solder joints

Fittings: ​<< ASME B16.22; or  ASME B16.18>>​​.

Unions: <<ASME B16.22>>, Class 150, bronze unions with solder joints.

        - ******************************************************************************

        - The use of Nibco Press is only permitted when using oil-free or oil-less air compressors. Viega ProPress is permitted when using oiled compressors with FKM or HNBR sealing elements.

        - Nibco PressG are compatible regardless of oil content but may require additional approval prior to use. Consult the LANL ESM Ch. 17 - Pressure Safety, Approved ASME Unlisted Material/Component List and Approval Process under Chapter References and Resources to see if it is pre-approved without additional evaluation.

          - Application is restricted to ASTM B88 hard drawn tubing (Types K & L) or ASTM B280.

          - Fittings: [Nibco PressG].

        - ******************************************************************************

Press Joints:

Application is restricted to <<ASTM B88>> hard drawn tubing (Types K and L) between 1/2 and 4 inches nominal.

Fittings: ​<< Viega ProPress with FKM sealing elements;  Viega ProPress with HNBR sealing elements; or  Nibco Press>>​.

STEEL PIPE AND FITTINGS (UP TO 2 INCHES)

      - ***************************************************************************************

      - Carbon steel piping is not recommended for compressed air quality Class 1 or Class 2 (in accordance with LANL ESM Chapter 6 - Mechanical, Section D20).

      - ***************************************************************************************

Pipe: Black steel,<<ASTM A53/A53M>>, Type << E;  F; or  S>> grade << A; or  B>>, wall thickness<< standard wall; or  ___>>.

Threaded Joints:

Fittings: <<ASTM A197/A197M>> malleable iron, <<ASME B16.3>> threaded type <<ASME B1.20.1>> Class<< 150; or  300>>.

Unions: Ferrous Pipe: <<ASME B16.39>>, malleable iron, threaded unions type <<ASME B1.20.1>>​ Class << 150;  250; or  300>>.

STEEL PIPE AND FITTINGS (GREATER THAN 2 INCHES, UP TO 4 INCHES)

Pipe: Black steel, <<ASTM A53/A53M>>, Type << E;  F; or  S>>, grade << A; or  B>>, wall thickness<< standard wall; or  ___>>.

Welded Joints: Steel, <<ASTM A234/A234M>>, Grade WPB, Schedule 40, butt-welding type, <<ASME B16.9>>.

Bolted Joints: <<ASME B16.5>> forged carbon steel, <<ASTM A105/A105M>>. Flange hardware per Section << 01 4731 - Flange Assembly for Pressure Systems>>.

      - ***************************************************************************************

      - All the following components (disregarding ASME BPVC items) are either standard piping components (listed items) per ASME B31.9 para. 926 or have previously LANL approved unlisted component evaluations in accordance with ASME B31.9 para. 904.7.

      - The types of components shown may be a non-exhaustive list. Any substitutions or additions shall be ASME B31.9 compliant. All previously LANL approved ASME B31.9 components are available in LANL ESM Ch. 17 - Pressure Safety, Approved ASME Unlisted Material/Component List and Approval Process under Chapter References and Resources.

      - Provide safe access or remote operators where valves and fittings are not exposed or installed over 7 feet in height above finished floor.

      - Provide ball valves at low points of piping system. Provide ball valves on strainer drain ports.

      - Information on valves below are provided for soldered/brazed/threaded/flanged connections. If using press joints, replace applicable entries with information on press joint valves.

      - ***************************************************************************************

VALVES

Ball Valves up to 2 inches.

Manufacturer: Nibco, Series 585-70.

<<MSS SP-110>>, << 600; or  250>> psi non-shock cold working pressure (CWP) pressure rating.

Bronze, two-piece body, chrome-plated brass ball, full port, Teflon seats and stuffing box ring, blowout proof stem, lever handle, << solder;  threaded; or  press>> ends.

Ball Valves above 2 inches.

Manufacturer: Nibco, Series F-510-CS-R-66-FS.

<<MSS SP-72>>, one piece carbon steel body, full port ball, <<ASME B16.5>> class 150 flange, 285 psig non-shock cold working pressure (CWP) pressure rating.

      - ***************************************************************************************

      - Swing check valves may not be used in reciprocating air compressor service. Swing-type check valves NPS 4 or larger are not recommended for vertical installation.

      - ***************************************************************************************

Swing Check Valves up to 3 inches.

Manufacturer: Nibco 413 Series.

<<MSS SP-80>>, Type << 1; or  2>> bronze, horizontal swing, Y-pattern, renewable seat and disc, 200 psig non-shock cold working pressure (CWP) pressure rating, << solder;  threaded; or  press>> ends.

Swing Check Valves above 3 inches.

Manufacturer: Nibco F-938-31.

<<MSS SP-136>>​, Class 150 raised face flanges, ductile iron body, 235 psig pressure rating at 200 degrees F, bolted bonnet, bronze trim.

STRAINERs

      - ***************************************************************************************

      - Designer to select strainers with body materials compatible with selected piping materials.

      - Nibco 221 series wye strainers may require additional approval prior to use. Consult the LANL ESM Ch. 17 - Pressure Safety, Approved ASME Unlisted Material/Component List and Approval Process under Chapter References and Resources to see if it is pre-approved without additional evaluation.

        - Manufacturer: Nibco

        - Model number: [T-221][S-221][PF-221]

        - Size: [½][_____] inch

        - End connections: [threaded type ASME B1.20.1][solder type][press type]

        - Mesh perforations: 20-mesh stainless steel wire screen

        - Pressure rating: minimum 200 psig non-shock cold working pressure (CWP) rating.

      - ***************************************************************************************

Bronze wye-type strainers up to 2 inches.

Manufacturer: Watts

Model number: << LF777; or  LFS777>>.

Size: << 1/2; or  _______>> inch

Body: Lead Free cast copper silicon

End connections: ​<< Threaded; or  Solder>>​.

Mesh/Perforations:

<< 20; or  _______>>-mesh stainless steel wire mesh liner

<< 1/32; or  _______>>​ inch stainless steel perforated screens

Pressure rating: minimum 200 psig non-shock cold working pressure (CWP) rating.

Steel wye-type strainers.

Specification: <<ASME B16.34>>

Manufacturer: << ANIX; or  Spirax Sarco>>

Model Number: << YS41H5F Series; or  Fig 34HP>>

Size: << 1/2;  8; or  _______>> inch

Body: <<ASTM A216/A216M>>​ Gr. WCB cast carbon steel

End connections: << Butt weld; or  ASME B16.5 Class 600 flange>>.

Mesh/Perforations: << _______>>.

Pressure rating: <<ASME B16.34>> Class << 150;  300; or  600>>.

Temperature range: up to 302 degrees F minimum.

FLEXIBLE CONNECTOR

Manufacturer: << Universal Hose & Braid; or  Swagelok>>

Model: << Anaconda model ____;  FM;  FJ; or  FL>>

Material: << Bronze; or  Stainless Steel>> braided hose

End connections: ​<< Copper ends conforming to ASME B16.18 and ASME B16.22; or  Male pipe thread ends>>​

Diameter: << _______>> inch

Length: << _______>> inch

Pressure rating: << _______>> psig

      - ***************************************************************************************

      - If individual components listed below (Articles Prefilter, High-Efficiency Coalescing; Afterfilter, High-Efficiency Particulate; Automatic Drain Valve; Oil/Water Separator; Regenerative Air Dryer; Refrigerated Air Dryer (Air Cooled)) are furnished by the compressor manufacturer as part of a packaged system, those components should be listed in paragraph Compressor Accessories in article Air Compressor or Packaged System (1/4 to 30 HP). The manufacturer (not the vendor) is to provide any line sets required to link the compressor system items.

      - When selecting filter and housing (Articles Prefilter, High-Efficiency Coalescing and Afterfilter, High-Efficiency Particulate), assume maximum flow conditions at the minimum operating pressure. Match inlet and outlet connections to system pipe size.

      - Filters are restricted to bowl-type housings less than 6” diameter without additional approval (up to approx. 3” NPS inlet/outlet connections). Filters larger than 6” diameter shall be ASME Section VIII Division 1 pressure vessels or obtain approval via code-equivalency evaluation.

      - ***************************************************************************************

PREFILTER, HIGH-EFFICIENCY COALESCING

Manufacturer/Series/Filter Grade:

        - ******************************************************************************

        - The following two subparagraphs are designer choices.

        - ******************************************************************************

Van Air, Housing Series F200, Filter Grade C

Pneumatics Products, Housing Series P2001, Filter Grade SU

High-efficiency coalescing filter efficiency 99.99 percent at 0.6 microns, maximum oil carryover 0.008 ppm by weight, maximum inlet temperature 125 degrees F, maximum clean dry pressure drop 1.50 psid.  Housing maximum working pressure 250 psig at 225 degrees F, furnish with optional two-sided color-coded pressure differential indicator, and without internal float drain.

In/Out Connection: ​<< ______>>​ inches ​<< NPT; or  _______>>​

Flow Capacity: << _______>> scfm at << _______>>  psig

AFTERFILTER, HIGH-EFFICIENCY PARTICULATE

Manufacturer/Series/Filter Grade:

        - ******************************************************************************

        - The following two subparagraphs are designer choices.

        - ******************************************************************************

Van Air, Housing Series F200, Filter Grade RC

Pneumatics Products, Housing Series P2001, Filter Grade AF

High-efficiency particulate filter efficiency 99.99 percent at 0.9 microns, maximum inlet temperature 150 degrees F, maximum clean dry pressure drop 1.50 psid. Housing maximum working pressure 250 psig at 225 degrees F, furnish with optional two-sided color-coded pressure differential indicator, and without internal float drain.

In/Out Connection: ​<< _______>>​ inches ​<< NPT; or  _______>>​

Flow Capacity: << _______>> scfm at << _______>> psig

      - ***************************************************************************************

      - Automatic Drain Valves: Gardner Denver AED series and Zeks 2702 series automatic drain valves may require additional approve prior to use. Consult the ESM Ch. 17 Approved ASME Unlisted Material/Component List and Approval Process under Chapter References and Resources to see if it is pre-approved without additional evaluation.

      - Manufacturer: [Gardner Denver] [Zeks]

      - Model number: [ ]

      - Size: [½][_____] inch

      - Valve Type: [Direct Acting][Internal Pilot Operated Diaphragm][External Pilot Operated Diaphragm]

      - Electrical connections: [115][230] VAC, NEMA 4 enclosure

      - For drain valve listed by Van Air below, although approved for use, is not energy efficient.

      - ***************************************************************************************

AUTOMATIC DRAIN VALVE

Manufacturer: Van Air

Model: EDV-115

Size: << 1/4 inch female NPT; or  1/2 inch male NPT>>

Valve Type: Solenoid ball valve with integral strainer

Electrical Connections: 115 VAC, Lexan enclosure

      - ***************************************************************************************

      - Consult with separator manufacturers’ representative for application and sizing information.

      - ***************************************************************************************

OIL/WATER SEPARATOR

Provide a commercial oil/water separator that will treat condensate waste to discharge no more than 10 ppm of residual oil.  Operates at ambient pressure.

Manufacturers:

Atlas Copco, Model OSC

Sullair, SP Series.

<< _______>>

REGENERATIVE AIR DRYER

Manufacturers:

        - ******************************************************************************

        - The following three subparagraphs are designer choices.

        - ******************************************************************************

Van Air, ​​<< Model HLS-; or  HL->>​​​​<< ____>>​​.

Pneumatic Products, DHA/CDA Series, Model ​<< _______>>​.

<< _______>>.

Heatless, regenerative dryer, minus 40 degrees F pressure dew point, solid state controller, twin towers, with adsorbent desiccant, purge exhaust valve and muffler, drain connection and cycle saver control option that adjusts dryer purge to actual moisture load condition and includes failure to switch (FTS) alarm. <<ASME BPVC-VIII-1>> “U” stamped. NBIC numbered and registered.

Capacity: << _______>> scfm at << _______>> psig

Power Voltage: << _______>> V, << _______>>  phase, 60 Hz.

      - ***************************************************************************************

      - ASME B31.5 does not apply to any self-contained or unit systems subject to the requirements of Underwriters Laboratories or other nationally recognized testing laboratory. Selection outside of this exclusion may require ASME B31.5 piping.

      - ***************************************************************************************

REFRIGERATED AIR DRYER (AIR-COOLED)

Manufacturers:

        - ******************************************************************************

        - The following three subparagraphs are designer choices.

        - ******************************************************************************

Van Air, ​​<< Model RD; or  _______>>​​.

Hankison, Model ​<< HPR; or  HPRN>>​.

<< _______>>.

Refrigerated air dryer, air cooled condenser, 35-38 degrees F pressure dew point, indoor installation (ambient temperature 40-100 degrees F), automatic drain valve, and charged with ​<< R-134A; or  _______>>​.

Capacity: << _______>> scfm at << _______>> degrees F inlet temperature and << _______>>  psig inlet pressure.

Power Requirements: << _______>> V, << _______>> phase, 60 Hz.

Inlet/Outlet Connection Size: << _______>> inch

      - ***************************************************************************************

      - Overpressure protection must be provided on Bourdon-tube, dial-indicating pressure gauges that operate at pressures greater than 15 psig by one of the following means:

        - Pressure gauges approved per UL 404.

        - Tempered safety glass, plastic, or shielded face, AND a blowout back or plug.

      - Pressure gauges that serve primarily a pressure indication for over pressure protection (i.e., not used for process data collection) should have a range of at least 1.25 times, but no more than twice the set pressure of the relief device as recommended in ASME Section VIII, Div. 1, Nonmandatory Appendix M, Para. M-14.

      - Refer to manufacturer’s recommendations for pressure ranges. Generally, a range of twice the expected normal operating pressure is recommended, with a maximum working pressure not exceeding 75 percent of the range.

      - Provide pressure gage on discharge piping from each air compressor and on each receiver tank. Consider the need for temperature measuring devices during design as well.

      - ***************************************************************************************

PRESSURE GAUGE

Manufacturer: Ashcroft, Type 1009

Gauge: <<ASME B40.100>>, Accuracy Grade 1A, minimum 2-1/2 inch dial, 1/4 inch <<ASME B1.20.1>> NPT brass bottom connection, phosphor bronze bourdon tube, maximum plus or minus 1 percent accuracy full scale, stainless steel case, process temperature limit of -40 degrees F to 250 degrees F, and with stainless steel tube.

Required options: Dry gauge, pressure relief blowout plug, acrylic or shatter-proof glass

Range: ​​<< ___ psi; or  per drawings>>​​​.

Required options: Dry gauge, pressure relief blowout plug, acrylic or shatter-proof glass

        - ******************************************************************************

        - The following subparagraph is a designer choice.

        - ******************************************************************************

Isolation Valve: 1/4 inch brass plug, minimum 250 psi working pressure valve. Manufacturer: ​​<< ____>>​​ Part No. ​​<< ____>>​​.

PRESSURE REGULATORS

Manufacturer/Model: << Norgren 11-002 series,; or  Swagelok K series,>> Part Number << _______>>

Inlet Size: ​<< 1/4 in; or  _______>>​

Outlet Size: ​<< 1/4 in; or  _______>>​

Flow Coefficient (Cv): << 0.20; or  _______>>

Maximum Inlet Pressure: << 500 psig; or  _______>>

Delivery Pressure Range: ​<< _______>>​ to ​<< _______>>​​ psig

Pressure Gauges: ​<< Outlet only;  Inlet and outlet; or  None>>​

Location:  Above grade

Assembly Methods: <<ASME B1.20.1>> NPT threads

DEW POINT TEST FITTING

Manufacturer: Pete’s Plug

Description: 316 stainless steel, 1/4 inch, suitable for use in 150 psig systems. Provide extra-long (XL) plug when pipe insulation exceeds 1 in. thickness.

      - ***************************************************************************************

      - Overpressure protection shall meet the requirements of LANL ESM Chapter 17 - Pressure Safety, Section PS-REQUIREMENTS, paragraphs 8.5 and 8.6. See also Attachment GUIDE-1 for guidance on performing overpressure protection evaluations for compressed air systems.

      - Note that if a compressed air receiver is included as part of an off-the-shelf compressed air package, there will be a manufacturer-specified and installed relief device and the piping system designer is not responsible for the sizing of this valve. However, the designer is responsible for ensuring this relief valve (1) would limit system pressure with ASME code scope limits (150 psig for ASME B31.9) and (2) would sufficiently protect any downstream piping components from exceeding their pressure rating. Supplemental overpressure protection on the downstream piping is often necessary to stay within ASME B31.9 code scope because it is common for compressed air packages with air receivers to include a relief valve set in the 165-200 psig range.

      - Common relief device manufacturers for compressed air service include Kingston, Control Devices, Conrader, and Aquatrol.

      - Relief device shall be installed in a location that relieves away from personnel.

      - ***************************************************************************************

PRESSURE RELIEF VALVES

Manufacturer/Model: ​​<< Kingston KSV25;  Control Devices SW10;  Conrader SRV390; or  _______>>​​.

Description: << Brass; or  Stainless Steel>> body, <<ASME BPVC-XIII>>  “UV” stamped relief device

Inlet Size: << 1/4;  1; or  _______>> inch.

Set Pressure: << 125;  135;  45; or  _______>> psig.

Location: Above grade. Installation location shall be indicated on design drawings.

End connections: << NPT; or  _______>>.

Manufacturers rating: << 69; or  _______>> SCFM air.

AIR RECEIVER

Manufacturer: ​​<< Hanson Tank;  Samuel Pressure Vessel Group; or  _______>>​​

Description: Carbon steel tank built and tested to <<ASME BPVC-VIII-1>>, “U” stamped. NBIC numbered and registered.

Configuration: ​<< Vertical tank with ring base; or  Horizontal tank with saddles>>​, ​<< NPT; or  ASME B16.5 Class 150 Flange>>​​ inlet and outlet connections, factory exterior primer coating, ​<< unpainted;  powder coated; and  epoxy coated>>​ interior coating.

Size: ​​<< _______>>​​ gallons, rated at ​​<< _______>>​​ psi, ​​<< _______>>​​ diameter x ​​<< _______>>​​ long.

Seismic Design Category: ​​<< Select from the drop down menu;  D;  C; or  _______>>​​.

      - ***************************************************************************************

      - Consult with manufacturer’s representative, commercial guide specs, and the LANL ESM Chapter 6 - Mechanical when editing the article below. Verify compressor capacity (discharge pressure and flow rate) can meet the pressure and flow demands at LANL elevation of 7,500 ft. Furnish compressors with an after cooler, mechanical separator and an intake air filter silencer. If sound control is a factor, an intake filter silencer, muffler or sound enclosure may be required. Furnish duplex compressors with hour meters. For air compressors of greater than 30HP, a separate section for air compressors may be used.

      - ***************************************************************************************

AIR COMPRESSOR OR PACKAGED SYSTEM (1/4 THROUGH 30 HP)

Manufacturer:

        - ******************************************************************************

        - The following subparagraphs are designer choices.

        - ******************************************************************************

Atlas Copco

Sullair

Ingersoll Rand

Quincy

<< _______>>

Compressor:

Type: << Reciprocating single stage;  Reciprocating two stage;  Rocking piston;  Diaphragm;  Rotary vane;  Rotary screw; or  Rotary scroll>>, << lubricated;  non-lubricated; or  oil-less>>

Controls: ​<< Constant speed- start stop controls; or  Variable speed controls>>​.

Drive: ​<< Electric motor, _______ V, ___ Phase;  Diesel engine; or  _______>>​.

Mounting: << Base mounted;  Tank mounted; or  Portable>>.

Size: << _______>> HP.

Discharge pressure: << _______>> psig rated for 7,500 ft elevation.

Delivery capacity: << ______>> scfm (14.5 psia, 68 degrees F and 0 percent relative humidity).

Other Options: << Diagnostic control devices-high air temperature shutdown, low oil level shutdown;  belt guard;  intake filter;  after cooler; and  motor starter>>.

      - ***************************************************************************************

      - The following is a designer choice. See note above regarding callouts for manufacturer-provided compressor package accessories, if applicable.

      - ***************************************************************************************

Compressor Accessories (components furnished by the compressor manufacturer):

Refrigerated air dryer

Filters

Air receiver with relief valve

<< _______>>

PART 3 - EXECUTION

PREPARATION

Square, ream pipe and tube ends. Remove burrs.

      - ***************************************************************************************

      - Consult manufacturer’s recommendation for the use of acids and cleaning agents to prevent damage.

      - Ensure safeguards are taken to protect personnel from hazards of cleaning, which may include but not be limited to flying particulates, corrosive chemicals, and harmful vapors.

      - A suitable chemical and/or mechanical cleaning method shall be used, if necessary, to clean all surfaces to be fabricated.

      - ***************************************************************************************

Cleaning

Remove scale and dirt on inside and outside before assembly.

Cleaning will consist of removing all non-adhering material such as loose scale, sand, rust, cutting chips, grinding residue, etc. from the inside of the piping assembly by suitable means. This level of cleaning will allow the presence of mill scale and surface rust.

        - ******************************************************************************

        - Specify any special cleaning requirements below.

        - ******************************************************************************

​​<< _______>>​​.

Prepare piping connections to equipment with flanges or unions.

Fastener materials shall be free of nicks, burrs, chips, dirt, and damage (inspect threads, shank, and nuts). All damaged fasteners must be replaced.

INSTALLATION

General

Install piping in conformance with <<ASME B31.9>>.

Follow the equipment manufacturer’s installation requirements.

        - ******************************************************************************

        - The following two subparagraphs are designer choices.

        - ******************************************************************************

Install compressor unit on concrete housekeeping pad.

Install compressor unit on vibration isolators. Level and bolt in place. See ​<< Section 05 0520 - Post-Installed Concrete and Grouted Masonry Anchors - Normal Confidence; or  drawings>>​ for anchors.

Install air piping/tubing with a slope of at least 1 inch per 100 feet or less downward in direction of flow.

Install piping to maintain headroom and neither interfere with use of space nor take more space than necessary.

Group piping whenever practical at common elevations.

Label piping system per Section << 22 0554 - Identification for Plumbing,  HVAC, and Fire Piping and Equipment>>.

        - ******************************************************************************

        - The following is a designer choice.

        - ******************************************************************************

Insulate piping system per Section ​<< 22 0713 - Plumbing and HVAC Insulation>>​. Provide clearance for installation of insulation and access to valves and fittings.

Install piping hangers and supports per Section << 22 0529 - Hangers and Supports for Plumbing Piping and Equipment>>​.

        - ******************************************************************************

        - The following is a designer choice.

        - ******************************************************************************

Sleeve and caulk pipes penetrating exterior walls or interior bearing walls. Provide waterproof installation for exterior walls. Provide UL/FM approved through-penetration firestop system when penetrating fire rated barriers (e.g., walls, floors, etc.). See Section ​<< 07 8400 - Firestopping>>​.

Install piping to allow for expansion and contraction without stressing pipe, joints, or connected equipment.

Provide clearance for installation of insulation and access to valves and fittings.

Provide access where valves and other equipment are not exposed.

Install valves with stems upright or horizontal, not inverted.

Install gauges vertically.

Install branch take-offs to outlets from top of main, with shutoff valve after take-off.

Provide drip legs and drain traps at end of each main and branch and at low points of piping system.

Keep open ends of pipe free from scale and dirt. Whenever work is suspended during construction, protect open ends with temporary plugs, caps, or residue-free tape.

Route condensate drains to the oil/water separator. Route drain from the oil/water separator to the nearest floor drain.

Install compressed air couplings, female quick connectors, and pressure gages << where branch outlets are indicated; or  as indicated on drawings>>.

Install flexible connections where shown on drawings.

Welded, brazed, or soldered joints

Welded, brazed, or soldered joining of piping/tubing and components shall be per Section << 01 4631 - Welding, Brazing, and Soldering of Pressure Systems>>.

When welding, brazing, or soldering piping/tubing to a valve, follow manufacturer’s instructions to prevent heat damage to valve internals.

Press joints

Assemble press joints per manufacturer installation instructions using the tooling required by the manufacturer.

          - **********************************************************************

          - Select only one of the subparaghs below when specifying press joints.

          - **********************************************************************

Installation Manual Viega ProPress®, www.viega.us, latest edition

          - *** OR ***

NIBCO® Press System ® — Installation Instructions, www.nibco.com, latest edition

Threaded joints

Assemble  <<ASME B1.20.1>> threaded pipe joints as follows:

No more than six and no less than two threads visible after makeup of the joint.

No severe chipping or tearing of visible threads.

Bolted joints

Assemble flanges per Section << 01 4731 - Flange Assembly for Pressure Systems>>.

EXAMINATION, INSPECTION, AND TESTING

All welding, brazing, and soldering: Examined, inspected, and tested in accordance with Section(s) << 01 4631 - Welding, Brazing, and Soldering of Pressure Systems>><< and 01 4525 - Non-Destructive Examination (NDE) Requirements; or  None - N/A>>.

Externally the pressure system shall be free of weld slag, flux, and weld spatter.

Examination activities to verify the quality of the work must be performed by persons other than those who performed the activity being examined. Such persons must not report directly to the immediate supervisors responsible for work being examined.

The fabrication documentation must have evidence of the examination, submitted per Article Submittals.

Contact the LANL Owners’ Inspector to determine the initial inspection points (minimum hold points).

LANL Owner’s Inspector shall have access to any and all design, fabrication, manufacture, fabrication, heat treatment, assembly, erection, examination, testing, records, documentation and other project information or activities to verify that all required examinations and testing have been completed and to inspect the piping to the extent necessary to be satisfied that it conforms to all applicable examination requirements of the Code and of the engineering design and to perform the role defined in <<ASME B31.9>>.

LANL Owner’s Inspector is the final authority on acceptance of the project examinations and leak tests.

      - ***************************************************************************************

      - ASME B31.9 does not specify a minimum pneumatic test pressure beyond the “not more than 10 psig” preliminary test pressure required by para. 937.4.3. See ASME B31.9 Interpretations B31.9-18-01 and B31.9-18-02 for more information.

      - However, LANL requires that the test pressure be, at minimum, the normal operating pressure for the system.

      - Leak testing of the connections between existing piping and new piping defined below are based in ESM Ch. 17 Section PS-REQUIREMENTS 10.3, Pressure and Leak Testing.

      - ***************************************************************************************

Pressure test piping system per Section << 22 0813 - Testing Piping Systems>>, at the test pressures and durations listed below.

        - ******************************************************************************

        - The following two subparagraphs are designer choices.

        - ******************************************************************************

Compressed Air (Less than 150 psig design pressure)

Test with air at << _______>> psig per <<ASME B31.9>>, paragraph 937.4, holding test pressure for at least << 10; or  _______>> minutes. After hold duration, reduce to the lower of operating or design pressure before checking for leaks.

Instrument Air (Less than 150 psig design pressure)

Test with air at ​<< _______>>​ psig per <<ASME B31.9>>, paragraph 937.4, holding test pressure for at least ​<< 10; or  _______>>​  minutes. After hold duration, reduce to the lower of operating or design pressure before checking for leaks.

        - ******************************************************************************

        - The following is a designer choice.

        - ******************************************************************************

For modifications to existing piping test the connection between new and existing at normal operating pressure. Bring system up to operating pressure gradually. Visually examine the piping for leaks at one-half the system operating pressure. Perform a final examination at the system operating pressure. No leaking from the piping indicates that the system meets the requirement of the project.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 22 1500, REV. 7, DATED APRIL 15, 2026.