SECTION 22 0529

HANGERS AND SUPPORTS FOR PLUMBING PIPING AND EQUIPMENT

*************************************************************************************************************

LANL MASTER SPECIFICATION

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Mechanical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.
*************************************************************************************************************

PART 1	GENERAL

  - SECTION INCLUDES

A.	Furnish and install pipe hangers, supports, hanger rods, inserts, and sleeves, and other positive fastenings for mechanical non-structural components such that gravity loads are safely transferred to the structure.

  - Related REQUIREMENTS

- Refer to Section 22 0548 - Vibration and Seismic Controls for Plumbing piping and equipment for seismic control / protection requirements for mechanical non-structural components.

  - SUBMITTALS

    - Submit the following in accordance with subcontract submittal procedures:

- Manufacturer’s catalog data of hangers and supports including load capacity.

- Shop Drawings showing system layout with location including critical dimensions, sizes, and pipe hanger and support locations and detail of trapeze hangers.

- Manufacturer’s installation instruction for special procedures and assembly of components if required.

      - Certification of offsite welders and qualified welding procedure per Section 01 4444 (follow 01 4455 for onsite work).

  - QUALITY ASSURANCE

- Hangers and supports shall conform to the requirements of the following codes and standards as applicable:

- ASME B31.1, Power Piping

- ASME B31.3, Process Piping

- ASME B31.9, Building Services Piping

- Uniform Mechanical Code, (UMC)

- Uniform Plumbing Code, (UPC)

- NFPA-13, Standard for the Installation of Sprinkler System

- Qualify welding processes and welding operators in accordance with AWS D1.1 “Structural Welding Code - Steel” for hangers and supports.

PART 2	PRODUCTS

2.1	PRODUCT OPTIONS AND SUBSTITUTIONS

A.	Alternate products may be accepted; follow Section 01 2500, Substitution Procedures

2.2	PIPE HANGERS AND SUPPORTS

A.	Hangers for Pipe Sizes 1/2 to 1-1/2 inches: Malleable iron or carbon steel, adjustable swivel, split ring.

B.	Hangers for Cold Pipe Sizes 2 inches and over: Carbon steel, adjustable, clevis.

C.	Hangers for Hot Pipe Sizes 2 to 4 inches: Carbon steel, adjustable, clevis.

D.	Hangers for Hot Pipe Sizes 6 inches and over: Adjustable steel yoke, cast iron roll, double hanger.

E.	Multiple or Trapeze Hangers: Steel channels with welded spacers and hanger rods.

F.	Multiple or Trapeze Hangers for Hot Pipe Sizes 6 inches and over: Steel channels with welded spacers and hanger rods, cast iron roll.

G.	Wall Support for Pipe Sizes to 3 inches: Strut clamp or cast iron hook.

H.	Wall Support for Pipe Sizes 4 inches and over: Welded steel bracket and wrought steel clamp.

- Wall Support for Hot Pipe Sizes 6 inches and over: Welded steel bracket and wrought steel clamp with adjustable steel yoke and cast iron roll.

J.	Vertical Support: Steel riser clamp.

K.	Floor Support for Cold Pipe: Cast iron adjustable pipe saddle, lock nut, nipple, floor flange, and concrete pier or steel support.

L.	Floor Support for Hot Pipe Sizes to 4 inches: Cast iron adjustable pipe saddle, lock nut, nipple, floor flange, and concrete pier or steel support.

M.	Floor Support for Hot Pipe Sizes 6 inches and over: Adjustable cast iron roll and stand, steel screws, and concrete pier or steel support.

N.	Copper Pipe Support: Copper-plated, carbon steel ring.

2.3	HANGER RODS

- Mild steel threaded both ends, threaded on one end, or continuous threaded.

- Rods for trapeze hangers shall be a minimum 3/8-inch.  The use of pipe hooks, chains, perforated iron strapping, or wire for pipe supports are NOT permitted.

2.4	INSERTS

A.	Malleable iron case of galvanized steel shell and expander plug for threaded connection with lateral adjustment; top slot for reinforcing rods; lugs for attachment to forms; size inserts to suit threaded hanger rods.

2.5	SLEEVES

A.	Sleeves for Pipes through Non-Fire Rated Beams, Walls, Footings, and Floors:  Steel pipe or 18 gage galvanized steel.

B.	Sleeves for Pipes through Fire Rated and Fire Resistive Floors, Walls, and Roof: Prefabricated fire rated sleeves including seals, approved by a nationally recognized testing laboratory (UL listed).

C.	Sleeves for Ductwork: Galvanized steel.

PART 3	EXECUTION

*************************************************************************************************************

NOTE: Verify that supporting structural elements are adequate to support the imposed hanger load.

*************************************************************************************************************

3.1	INSERTS

A.	Install inserts for placement in concrete forms.

B.	Install inserts for suspending hangers from reinforced concrete slabs and sides of reinforced concrete beams.

C.	Provide hooked rod to concrete reinforcement section for inserts carrying pipe over 4 inches.

D.	Where concrete slabs form finished ceiling, locate inserts flush with slab surface.

- Where inserts are omitted, drill through concrete slab from below and provide through-bolt with recessed square steel plate and nut.

3.2	PIPE HANGERS AND SUPPORTS

A.	Support piping to maintain its alignment, and prevent sagging.

B.	Place hangers within 12 inches of each horizontal elbow.

C.	Support vertical piping with riser clamps secured to the piping and resting on the building structure at each floor.

D.	Install hangers to provide minimum 1/2 inches space between finished covering and adjacent work.

E.	Use hangers with 1-1/2 inches minimum vertical adjustment.

F.	Where several pipes can be installed in parallel and at same elevation, provide multiple or trapeze hangers.

G.	Support riser piping independently of connected horizontal piping.

H.	Provide copper plated hangers and supports for copper piping.

I.	Provide insulation continuous through hangers and rollers.  Protect insulation by steel shields in accordance with Section 22 0713, Plumbing and HVAC Insulation.

J.	Provide hangers on piping on each side of, and within 6 inches of, hubless pipe couplings so the couplings will bear no weight.

K.	Provide supports that allow free axial movement and only support the weight of the piping or tubing. Provide additional hangers or brackets to support valves, flanges, specialties, etc., to prevent excessive deflection.

L.	Prime coat exposed steel hangers and supports.  Refer to Section 09 9100, Painting.  Hangers and supports located in crawl spaces, pipe shafts, and suspended ceiling spaces are not considered exposed.

3.3	SLEEVES

- Provide sleeves for all pipe penetrations through walls, roof, or slab above grade.

- Neatly cut holes in existing walls, floors, or roof for placement of sleeves.  Place sleeve and grout and caulk annular space to provide finished appearance.

- Extend sleeves through floor slab 2 inches above finished floor level.  Caulk sleeves full depth and provide floor plate.

- Seal space between pipe and sleeve watertight for all sleeves penetrating the roof.

- Where piping or ductwork penetrates a fire rated wall or floor, provide fire-stopping insulation so that the assembly when complete retains the fire rating of construction penetrated by the sleeve.

3.4	HANGER SPACING

*************************************************************************************************************

The hanger spacing tables are for straight runs of standard and heavier steel pipe, and Type L and heavier copper tube.  They are not intended to be used as specifications for all installations.  These do not apply where span calculations are made or where there are concentrated loads between supports.

For Victaulic flexible systems and other piping material, consult with the manufacturer for suggested hanger spacing.  For Victaulic rigid couplings used in steel piping systems, the spacing below may be used.

*************************************************************************************************************

A.	Plumbing Piping - Water, Gas, Drain, Waste and Vent (DWV)

- Comply with the requirements of the Uniform Plumbing Code, (IAPMO), Hangers and Supports.

B.	Fire Protection Piping

1.	Comply with the requirements of NFPA-13, for hanger spacing and materials.

C.	Steam/Condensate Piping Inside Building, up to 15 psig.

1.	Comply with the requirements of ASME B31.9, Building Services Piping.

2.	Maximum Hanger Spacing:

| Steel Pipe Size (Inches) | 1 | 1 ¼ | 1 ½ | 2 | 3 | 4 | 6 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Spacing (Feet) | 9 | 11 | 13 | 15 | 17 | 21 | 25 | 28 |

D.	Steam/Condensate Piping Outside Building, up to 150 psig.

1.	Comply with the requirements of ASME B31.1, Power Piping.

2.	Maximum Hanger Spacing

| Steel Pipe Size (Inches) | 1 | 1 ¼ | 1 ½ | 2 | 3 | 4 | 6 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Spacing (Feet) | 9 | 9 | 9 | 13 | 15 | 17 | 21 | 24 |

E.	Water Building Services Piping, up to 150 psig (Heating, Cooling, and Tower Water)

1.	Comply with the requirements of ASME B31.9, Building Services Piping.

2.	Maximum Hanger Spacing

| Size (Inches) | Less Than 1 | 1 | 1 ¼ | 1 ½ | 2 | 3 | 4 | 6 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Spacing (Feet) Steel Pipe | 6 | 9 | 11 | 12 | 13 | 15 | 17 | 20 | 21 |
| Spacing (Feet) Copper Tube | 5 | 7 | 7 | 8 | 9 | 10 | 12 | 14 | 16 |

F.	Air and Laboratory Gas Building Services Piping, up to 150 psig

1.	Comply with the requirements of ASME B31.9, Building Services Piping.

2.	Maximum Hanger Spacing:

| Size (Inches) | 1/4 to 1/2 | 5/8 to 7/8 | 1 | 1 ¼ | 1 ½ | 2 | 3 | 4 | 6 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Spacing (Feet) Steel Pipe | 6 | 6 | 9 | 11 | 13 | 15 | 17 | 21 | 25 | 28 |
| Spacing (Feet) Copper/SS Tube | 3 | 5 | 7 | 9 | 10 | 12 | 15 | 17 | 21 | 24 |

G.	Refrigeration Piping

1.	Comply with the requirements of the Uniform Mechanical Code, (ICBO) Refrigeration Supports.

3.5	HANGER ROD SIZE

A.	Plumbing (UPC) Piping (Water, Gas, DWV)

| Pipe Size (Inches) | ½ - 4 | 5 - 8 |
| --- | --- | --- |
| Rod Size (Inches) | 3/8 | 1/2 |

B.	HVAC Piping (Steam, Condensate, Water, Air, Laboratory Gas)

| Pipe or Tubing Size (Inches) | 3/8 - 2 | 2 ½ - 3 ½ | 4 - 5 | 6 – 8 | 10 - 12 |
| --- | --- | --- | --- | --- | --- |
| Rod Size (Inches) | 3/8 | 1/2 | 5/8 | 3/4 | 7/8 |

END OF SECTION

*****************************************************************

Do not delete the following reference information:

*****************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 22 0529 Rev. 3, dated September 1, 2009.