SECTION 22 0548

VIBRATION AND Seismic CONTROLS 
FOR PLUMBING PIPING AND EQUIPMENT

*************************************************************************************************************

LANL MASTER SPECIFICATION

Word file at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Structural Specifications POC.  Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

This Section deals with requirements for vibration control / isolation, and Performance Category (PC)-1 and PC-2 seismic control / protection, of mechanical nonstructural components.

Refer to LANL ESM Chapter 5, Sect. III, for seismic design and control for PC-3 and PC-4 nonstructural components.

Use this specification in conjunction with Section 13 4800 Sound, Vibration, and Seismic Control.

*************************************************************************************************************

GENERAL

*************************************************************************************************************

The intent of this Section is to provide for adequate resistance to lateral forces induced by earthquakes for mechanical nonstructural components and systems so as to preclude injury or impeded egress of personnel.

In addition, if required by IBC and other Project Record Documents, this Section is intended to ensure 1) Operability of active mechanical nonstructural components and / or 2) Containment of hazardous material by / in mechanical nonstructural components, following the design seismic event.

*************************************************************************************************************

SECTION INCLUDES

Provide hangers, supports, anchors, concrete bases, vibration isolators, sleeves, inserts, seals, and other positive fastenings for mechanical nonstructural components such that in-service loads and seismic forces are safely transferred to the structure and relative seismic displacements of the components are adequately accommodated.

1.2	ITEMS NOT COVERED BY THIS SECTION

A.	Fire Protection Systems

1.  Seismic protection of piping for fire suppression systems shall be installed per those Sections.

1.3      SYSTEM DESCRIPTION

    - General Requirements

      - The requirements for seismic control measures described in this Section shall be applied to the mechanical nonstructural components and systems listed below.

    - Mechanical Nonstructural Components

*************************************************************************************************************

The author must ensure that the list below includes all mechanical nonstructural components requiring seismic control.  Delete the items which are not part of the project and add items which are not included in the list.

*************************************************************************************************************

      - Include the following mechanical nonstructural components, as well as the associated seismic control, to the extent required on plans or in other sections of these specifications:

        - Piping

        - Ductwork

        - Air-side HVAC

        - Wet-side HVAC

        - Pressure Vessels

        - Pumps

        - Compressors

        - Roof-mounted Stacks

        - [______]

*************************************************************************************************************

Edit 1.4 to match project conditions; add items to list as required; delete items not included in the Project.  Delete paragraph if there are no nonstructural components that must maintain containment and /or active nonstructural components that must remain operable.

It may be necessary to note the equipment IDs for the particular items (e.g. BHW-1, CWR-B, etc.) that must meet the requirements of this paragraph.

Seismic control does not guarantee that a nonstructural component is rugged enough to maintain containment, or that an active nonstructural component is rugged enough to remain operable, following the design seismic event.  When such additional capability is required, the component must be certified as being able to do so by the manufacturer / supplier in accordance with the design structural-engineer-of-record’s direction.

*************************************************************************************

1.4      Nonstructural Component CERTIFICations

    - The following items furnished under this Subcontract are a) Mechanical nonstructural components that have hazardous content, and / or b) Active mechanical nonstructural components that have to remain operable and shall be certified by the manufacturer / supplier as being able to maintain containment, and / or remain operable, following the design seismic event.  Certification shall be in accordance with the Project’s Statement of Special Inspections document.

Pump Controller [PC-A,…]

Boiler [BHW-1,…]

Chiller [CWR-B,…]

Air-Conditioner, Refrigerant [ACR-3,…]

Expansion Tanks [TX-E,…]

[___________]

*************************************************************************************************************

Edit 1.5 to match project requirements.

*************************************************************************************************************

1.5       SUBMITTALS

    - Submit the following per Project submittal procedures.

Catalog Data: Submit catalog data for each type of product specified.  Include information substantiating equivalent corrosion resistance to zinc coated steel of alternative treatment, finish, or inherent material characteristic.

Material List: Submit hanger and support schedule showing manufacturer's figure number, size, spacing, features, and application for each required type of hanger, support, sleeve, seal, and fastener to be used.

*************************************************************************************************************

Edit D to match project conditions; add items to list as required; delete items not included in the Project.

*************************************************************************************************************

Shop Drawings: Submit shop drawings showing details of fabricated hangers, supports, and seismic control of all mechanical nonstructural components such as the ones listed below.  Provide detail drawings along with catalog cuts, templates, and erection and installation details, as appropriate, for the components listed below. Submittals shall be complete in detail; shall indicate thickness, type, grade, class of metal, and dimensions; and shall show construction details, reinforcement, anchorage, and installation with relation to the building construction.

1.  Boilers and furnaces	2.  Storage Tanks (Fuel, Oil, Water, etc.)  inside of, or on top of, buildings

3.  Water Heaters				4.  Expansion Air Separator Tanks

5.  Valves and Fittings for Piping		6.  Heat Exchangers

7.  Steam-fed Kitchen Appliances		8.  Water Chiller Units

9.  Thermal Storage Units	10.  Cooling Towers inside of, or on top of, buildings

11.  Air and Refrigerant Compressors	12.  Refrigerant Piping

13.  Air Handling Units			14.  Pumps with Motors

15.  Lab Scrubbers				16.  Large Commercial Dryers

17.  Pollution Control Equipment		18.  Gas Dryers

19.  Ducts					20.  Flash Tanks

21.  Unit Heaters				22.  Accumulator Tank

23.  Exhaust and Return Fans		24.  Solar Heating Units

25.  Fuel Piping Outside of Buildings		26.  All Water Supply Systems

27.  Storm and Sanitary Sewer Systems	28.  All Process Piping

29.  Pneumatic Tube Distribution System      30.  Cold Storage Refrigeration Systems

31.  Condenser Water Piping Outside the Building

32.  Chilled Water Distribution Systems Outside of Buildings

33.  Heat Distribution Systems (Supply, Return, and Condensate Return) Outside of Buildings

34.  All Piping Inside the Building Except as Specifically Stated Above Under "Items Not Covered By This Section”

35.  [___________]

*************************************************************************************************************

Delete E if not required by Project.

*************************************************************************************************************

Nonstructural Component Certifications: Submit manufacturer’s / supplier’s component certification indicating compliance with the Project’s Statement of Special Inspections document.

products

*************************************************************************************************************

In corrosive environments, appropriate materials must be used.  Dissimilar metals must be isolated.

If deemed necessary, author should include reference to other specification sections containing provisions for pipe pressure and temperature ratings.

*************************************************************************************************************

  - General

Refer to Section 13 4800, Sound, Vibration and Seismic Control for general seismic control products.

Substitutions

Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

  - Flexible CouplingS

Flexible couplings shall have 1-1/2 times the pressure and temperature ratings as adjoining pipe.

Flexible ball jointS

Flexible ball joints shall have cast or wrought steel casing and ball parts capable of 360-degree rotation with not less than 15-degree angular movement.

flexible mechanical joints

Mechanical couplings for steel or cast iron pipe shall have 1-1/2 times the pressure and temperature ratings as adjoining pipe, be of the sleeve type and shall provide a tight flexible joint under all reasonable conditions, such as pipe movement caused by expansion, contraction, slight settling or shifting of the ground, minor variations in trench gradients, and traffic vibrations. Where permitted in other sections of these specifications, joints utilizing split-half couplings with grooved or shouldered pipe ends may be used.

Sleeve-type couplings shall be used for joining plain-end pipe sections. The coupling shall consist of one steel middle ring, two steel followers, two gaskets, and necessary steel bolts and nuts to compress the gaskets.

manufactured ball jointS

Manufactured ball joints shall be as recommended by the manufacturer for the intended use, and shall be approved by LANL before installation.

sway bracing materialS

Sway bracing materials (e.g. rods, plates, rope, angles, etc.) shall be as specified in Section 13 4800, Sound, Vibration and Seismic Control.

Automatically-Actuated Natural Gas Shut-off Valves

Use of an automatically-actuated natural gas shut-off valve is limited to an Earthquake Sensitive Gas Shut-Off Valve (ESV) that has been certified by the California Division of the State Architect (DSA).

Concrete Formwork

*************************************************************************************************************

Edit A to match specification sections used in Division 3.

*************************************************************************************************************

Refer to Section 03 3001, Reinforced Concrete.

Concrete Reinforcement

*************************************************************************************************************

Edit A to match specification sections used in Division 3.

*************************************************************************************************************

Refer to Section 03 3001, Reinforced Concrete.

Cast-In-Place Concrete

*************************************************************************************************************

Edit A to match specification sections used in Division 3.

*************************************************************************************************************

Refer to Section 03 3001, Reinforced Concrete.

Vibration ISOLATORS

*************************************************************************************************************

Edit to match Project requirements. Mechanical equipment (e.g. fans, pumps, compressors) can generate substantial structure-borne noise that may be objectionable in noise-sensitive locations (e.g. offices, conference rooms, auditoriums, some laboratories).  Noise-generating mechanical equipment should be located as far as practicable from noise sensitive locations.  In cases where structure-born noise must be mitigated, select vibration isolators in accordance with the manufacturer’s recommendations based on equipment weight and noise spectra.  Verify seismic suitability of each vibration isolator with the design agency’s structural engineer of record.  Provide a schedule of the selected vibration isolators for each equipment item on the Drawings including indicate vibration isolator model number, rating, and loaded deflection. Indicate locations of isolators on the Drawings.

Floor mounted elastomeric vibration isolator mountings are suitable for relatively light floor-mounted mechanical equipment. Heavy floor-mounted equipment will require floor mounted spring vibration isolator mountings.  Suspended equipment will need the combination spring / rubber vibration isolator hangers.

Refer to footnote b of Table 13.6-1 in ASCE 7 for increase in seismic design force that may be required due to the use of vibration-isolated components.

Delete the article if vibration isolation is not required.

************************************************************************************************************

Furnish vibration isolators as required or as shown on the drawings.  The mechanical equipment shall be mounted on, or suspended from, vibration isolators to reduce the transmission of vibration and mechanically transmitted sound to the building structure.  Vibration isolators shall be selected in accordance with the weight distribution so as to produce reasonably uniform deflections.

All vibration isolators shall be furnished by the same manufacturer.

EXECUTION

  - GENERAL

*************************************************************************************************************

Locate each item of rigid mechanical equipment entirely on one side only of a building expansion joint.

Piping, ducts, etc., which cross an expansion joint to rigid mechanical equipment, shall have flexible joints that are capable of accommodating calculated thermal and seismic displacements.

*************************************************************************************************************

Refer to Section 13 4800, Sound, Vibration, and Seismic Control for general seismic protection installation requirements.

Install hangers, supports, and seismic control according to the project drawings, the requirements in this Section, and the requirements of Section 22 0529, Hangers and Supports for Plumbing Piping and Equipment.  Where overlap exists, the more stringent of the requirements will govern.

Conform to manufacturer's instructions and recommendations for installation of hangers, supports, and seismic control.

Do not use wire or perforated strap for permanent mechanical supports.

Attach each item of rigid mechanical equipment as shown.

Provide piping, ducts, etc., which cross an expansion joint to rigid mechanical equipment, with flexible joints as shown.

  - EXAMINATION

Examine surfaces to receive hangers, supports, and seismic control for compliance with installation tolerances and other conditions affecting performance of the system.  Do not proceed with installation until unsatisfactory conditions have been corrected.

  - Coupling and bracing.

*************************************************************************************************************

Unless otherwise determined by LANL, designs must include complete seismic calculations and the associated details showing coupling / bracing requirements.

The design is for the supports of the component/system, not the component/system itself.  As indicates previously, bracing does not guarantee that the component/system is rugged enough to survive earthquake shaking.

The following provisions apply to all piping within a 5 foot line around outside of building unless piping is buried in the ground:

- Piping grouped for support on trapeze-type hangers shall be braced at the most frequent interval as determined by applying the requirements ASCE 7 and this Section to each piping run on the common support.

- Bracing components shall be sized as required for the total load carried by the common supports.

- Where rigid attachment would interfere with thermal expansion of piping, design of bracing shall not result in such attachment to pipe flanges, or similar.

*************************************************************************************************************

Provide bracing and coupling as shown and as specified below.

  - Seismic Relative Displacements

*************************************************************************************************************

Using LANL ESM Ch. 5, and the applicable codes / standards referred to therein, the author will determine the expected seismic relative displacements and drift ratios.

Joints for vertical piping between floors of the building, where pipes pass through a building seismic or expansion joint, or where rigidly supported pipes connect to equipment with vibration isolators must be capable of accommodating the required relative displacements.

Horizontal piping across expansion joints must be capable of accommodating the resultant of the drifts of each building portion in each orthogonal direction.

Piping with manufactured ball joints must be capable of accommodating the seismic drift (i.e., deflection per unit of height above the base where the seismic separation occurs).

Insert the required flexibility (e.g., inches of relative displacement, etc.) in the blank space.

*************************************************************************************************************

Joints capable of accommodating [____] shall be provided and installed for vertical piping between floors of the building, where pipes pass through a building seismic or expansion joint, or where rigidly supported pipes connect to equipment with vibration isolators.

Piping capable of accommodating [____] shall be provided and installed for horizontal runs across expansion joints.

For threaded piping, swing joints made of the same piping material shall be provided and installed.

Piping capable of accommodating [____] shall be provided and installed for piping with manufactured ball joints; this value shall be used in place of the expansion given in the manufacturer's selection table.

  - flexible couplings or joints

Building Piping

*************************************************************************************************************

Flexible couplings or joints in building piping are required at bottom of all pipe risers as required to accommodate force and displacement provisions of LANL ESM Ch. 5.

Flexible couplings or joints shall be braced laterally without interfering with the action of the flexible coupling or joint.

Cast iron waste and vent piping need only comply with these provisions when caulked joints are used.

Flexible bell and spigot pipe joints using rubber gaskets may be used at each branch adjacent to tees and elbows for underground waste piping inside of building to satisfy these requirements

*************************************************************************************************************

Provide flexible couplings/joints in building piping as shown.

[Provide flexible bell and spigot pipe joints using rubber gaskets at each branch adjacent to tees and elbows for underground waste piping inside of building.]

Underground Piping

*************************************************************************************************************

The author will coordinate the requirements for seismic isolation of piping with the structural and civil design drawings to locate flexible connections as required.

The amount of annular space will depend on the stiffness of the foundation assembly and of the surrounding soil, and the distance between the foundation wall and the point outside the building where the pipe is considered to be restrained. The author will determine the pipe length necessary to provide fixity.  As an approximation, a value of 3 inches would be necessary for a pipe penetration in a one-story basement in soft soil.

Underground piping, including utility and service lines, requires adequate flexibility to accommodate differential movement where the piping enters the building (refer to LANL ESM Ch. 5).  Flexible couplings could be a solution, but use of them must be supported by design calculations.  For heat distribution systems, the “flexible coupling” used shall not undergo heat-related degradation over time.

Insert the required flexibility (e.g., inches of relative displacement, etc.) in the blank space.

*************************************************************************************************************

Couplings capable of accommodating [_____] shall be provided and installed where shown.

  - pipe sleeves and seals

*************************************************************************************************************

The author will determine the amount of differential movement of piping at pipe sleeves passing through non-fire-rated walls and partitions and will indicate on the drawings the amount of clearance required between the pipe and the sleeve based on deflection of the pipe between sway braces on either side of the wall.

The author should avoid pipe penetrations through fire-rated assemblies.

Edit A to match Project requirements.

*************************************************************************************************************

Provide pipe sleeves in concrete slabs and walls and all other fire-rated floors and walls for piping installations.

Sleeves through fire-rated wall or floor construction shall conform to the requirements in Section 07 8400, Firestopping.  Follow manufacturer's instructions to restore original fire rating of wall or slab.

Pipe sleeves in interior non-fire-rated walls shall be sized as indicated on the drawings to provide clearances that will permit differential movement of piping without the piping striking the pipe sleeve.

*************************************************************************************************************

Edit D to match Project requirements.

*************************************************************************************************************

Provide seals for pipe penetrations of slabs on grade and exterior walls below grade and where indicated.  Tighten sleeve seal screws until sealing grommets have expanded to form watertight seal.

At least 2 days prior to firestopping installation, notify LANL Subcontractor Technical Representative (STR) so that arrangements can be made for inspection during installation.  Do not proceed with the firestopping installation unless a LANL inspector is present.

  - Spreaders

*************************************************************************************************************

Spreaders are required between adjacent piping runs to prevent contact during seismic activity whenever the force and displacement provisions of LANL ESM Ch. 5 indicate that such contact could result in damage to the piping.

Spreaders shall be designed such that they occur at same interval as sway braces and at an equal distance between the sway braces.

If rack type hangers are used where the pipes are restrained from contact by mounting to the rack, spreaders are not required for pipes mounted in the rack.

*************************************************************************************************************

Provide spreaders between adjacent piping runs as shown.

Spreaders shall be applied to surface of bare pipe, and over insulation on insulated pipes, utilizing high-density inserts and pipe protection shields in accordance with the requirements of Section 22 0713, Plumbing and HVAC Insulation.

  - sway braces for piping

*************************************************************************************************************

Sway braces are required to prevent movement of the pipes under seismic loading.

Design of sway braces for a piping run shall be such that attachment to two dissimilar structural elements of a building that may respond differentially during an earthquake does not result, unless a flexible joint is part of the design.  Refer to paragraph 3.4, SEISMIC RELATIVE DISPLACEMENTS.

Braces are required in both the longitudinal and transverse directions, relative to the axis of the pipe.

The bracing shall not interfere with thermal expansion requirements for the pipes as described in other sections of these specifications.

*************************************************************************************************************

Transverse Sway Bracing for Piping

*************************************************************************************************************

The bracing layout must be supported by design calculations and shown on the drawings.

All runs (length of pipe between end joints) shall have a minimum of two transverse braces.

*************************************************************************************************************

Transverse sway bracing for piping shall be provided and installed as shown.

Longitudinal Sway Bracing for Piping

*************************************************************************************************************

The bracing layout must be supported by design calculations and shown on the drawings.

The design should take into account thermal expansion such that the sway braces do not interfere with expansion requirements.

All runs shall have one longitudinal brace minimum.

Branch lines, walls, or floors shall not be used as sway braces.

*************************************************************************************************************

Longitudinal sway bracing shall be provided and installed as shown.

Vertical Runs

*************************************************************************************************************

The bracing layout must be supported by design calculations and shown on the drawings, and must be  such that bracing occurs above the center of gravity of the segment being braced.

All runs shall have one longitudinal brace minimum.

Branch lines, walls, or floors shall not be used as sway braces.

*************************************************************************************************************

Run is defined as length of pipe between end joints.

Sway bracing for vertical runs of piping shall be provided and installed as shown.

Anchor Rods, Angles, and Bars

Anchor rods, angles, and bars shall be bolted to either pipe clamps or pipe flanges at one end and to cast-in-place concrete or masonry insert, or clip angles bolted to the steel structure, on the other end.

Provide bolts for attachment of anchors to pipe and structure shall be as shown.

Rods shall be solid metal or pipe.

Clamps and Hangars

Clamps or hangers on uninsulated pipes shall be applied directly to pipe.

Clamps or hangers on insulated pipes shall be applied over insulation vapor barrier with high-density inserts and metal protection shields under each clamp/hangar.

  - sway braces for ducts

*************************************************************************************************************

The bracing layout must be supported by design calculations and shown on the drawings.

Walls which ducts penetrate may be considered transverse braces.

Branch lines, walls, or floors shall not be used as sway braces.
*************************************************************************************************************

Braced Ducts

Transverse Sway Bracing

Provide transverse sway bracing at intervals not to exceed those shown.

Longitudinal Sway Bracing

Provide longitudinal sway bracing at intervals not to exceed those shown.

Unbraced Ducts

Hangers for unbraced ducts shall be attached to the duct within 2 inches of the top of the duct [with a minimum of two #10 sheet metal screws] [          ].

Unbraced ducts shall be installed with a 6-inch minimum clearance to vertical ceiling hanger wires.

Angles and Bars

Provide bracing angles and bars for ducts as shown.

  - CONCRETE BASES

*************************************************************************************************************

Edit the following article to match project conditions; delete if concrete bases are not required.

*************************************************************************************************************

Install a reinforced concrete base, not less than 6 inches high, for each piece of floor- mounted mechanical equipment.

*************************************************************************************************************

Edit the following article to match project conditions; delete if not required.  Use concrete bases with a permanent steel perimeter for heavy equipment.

*************************************************************************************************************

Support each [     ] on a concrete equipment base with a permanent steel perimeter frame.

Form base using ASTM A 36 steel channels.

Construct concrete base not less than 4 inches larger in both directions than supported equipment. Miter and weld corners and provide cross bracing.  Anchor or key to floor slab.

Install reinforcing bars tied to frame, and place anchor bolts, floor sills and sleeves using manufacturer's installation template.  Refer to Section 03 3001, Reinforced Concrete.

Place concrete and provide a steel trowel finish on top.  Refer to Section    03 3001, Reinforced Concrete.

Clean exposed steel frames and apply 2 coats of rust-preventative metal primer and 2 coats of exterior, gloss, alkyd enamel in color selected by the Architect.

*************************************************************************************************************

Edit the following article to match project conditions; delete if not required.  Use concrete bases without a permanent steel perimeter for relatively light floor–mounted equipment.

*************************************************************************************************************

Support each [     ] on a formed concrete equipment base.

Form concrete equipment bases using framing lumber with form release compounds. Refer to Section 03 3001, Reinforced Concrete.

Construct concrete base not less than 4 inches larger in both directions than supported unit.

Install reinforcing bars, and place anchor bolts, floor sills and sleeves using manufacturer's installation template. Refer to Section 03 3001, Reinforced Concrete.

Place concrete and provide a steel trowel finish on top; chamfer top edges and corners. Refer to Section 03 3001, Reinforced Concrete.

Cure concrete not less than seven days before installing equipment.

  - Anchor Bolts

Refer to Sections 03 [1512] [1534] and 1550 on post-installed concrete anchors.

  - FASTENING

Refer to Section 13 4800, Sound, Vibration and Seismic Control.

Vibration Isolation

    - Install and adjust vibration isolators as indicated on the Drawings in accordance with the manufacturer’s installation instructions.

    - Installation of vibration isolators shall not cause any change of position of equipment, piping or ductwork resulting in stresses or misalignment.

    - Make flexible mechanical connections to equipment supported by vibration isolators.

END OF SECTION

**************************************************************

Do not delete the following reference information.

**************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 22 0548 Rev. 2, dated September 14, 2009.