SECTION 22 0813

TESTING PIPING SYSTEMS

*************************************************************************************************************

LANL MASTER SPECIFICATION

Word file at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifiers notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual (ESM) Mechanical POC for interior, Civil POC for exterior.  Please contact applicable POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Ch 1 Section Z10 Specifications and Quality sections.

*************************************************************************************************************

GENERAL

SECTION INCLUDES

Pressure [and holiday] testing of the following systems:

Fire protection piping

Plumbing piping (sewer lines, water lines, rainwater lines)

Natural gas piping

Compressed air piping

Instrument air piping

Hydronic piping

Steam and condensate service piping

Steam and condensate distribution piping system

Refrigerant piping

Vacuum piping

Hazardous waste and vent double wall containment piping

Laboratory gas piping

Other Process Piping (B31.3)

Holiday testing (buried coated steel piping)

SUBCONTRACTOR REQUIREMENTS

Notify LANL Subcontract Technical Representative (STR) at least 24 hours (1 working day) in advance to arrange for witnessing of the piping test.

For discharge requirements of water used for pressure testing comply with Section 01 3545, Water Discharge Requirements.

Notify LANL STR immediately in the event of any accidental discharge.

SUBMITTALS

Submit the following in accordance with Project submittal procedures:

Test plan for approval that includes:

Material of construction

Design pressure

Test pressure and duration of test

Test medium and method of achieving the test pressure

Certification on calibration of pressure gauges

Method to exclude personnel from the area containing the system to be tested.

Overpressurization protection/prevention: Device make/model number, certification, pressure relief set point, point of installation in system.

Test Reports:  Submit test results within 10 working days of successful test.

PRODUCTS

  - MATERIALS

Furnish instruments, equipment, material and labor necessary to conduct tests.

Calibrate testing equipment at reasonable intervals with devices of accuracy traceable to National Institute of Standards and Technology (NIST).

Test gauges used in conducting test shall be in accordance with IAPMO UPC.

EXECUTION

  - FIELD QUALITY CONTROL

Piping being tested shall remain exposed until LANL has approved the piping test results.

Trenches may be backfilled between joints before testing to prevent movement of pipe during testing.  Ensure that thrust blocks are sufficiently hardened before testing.

Piping being tested shall not leak nor show any loss in test pressure for duration specified unless otherwise noted.

Where portion of piping system is to be concealed before completion, the portion shall be tested separately as specified for the entire system.

Ensure piping supports are in place.

Isolate system gages, sensors, etc., from pressure tests so instruments and devices are not damaged.  Test pressure shall not exceed the maximum allowable test pressure for any vessel, pump, valves, or other component in the system.

Hydrostatic (Water) Testing:

Use potable water as test medium.  Do not fill system until the LANL STR has approved the source of water supply.

Provide vents at high points to release trapped air while filling system.

Provide drains at low points for complete removal of test liquid.

Drain system if there is a potential for freezing, i.e., no heat in building, coil in outside air stream, or other similar situations.

Pneumatic (Air) Testing:

Use clean dry air (Excluded from use with natural gas pipe testing) or inert gas as the test medium.

Barricade the area around the system to be tested.

Prior to application of full air test pressure, apply a preliminary test of not more than 10 psig to reveal possible major leaks.

After preliminary test, raise pressure in stages not more than 25 percent up to full test pressure, allowing at least 10 minutes for equalization of strain and detection of major leaks at each intermediate stage.  Hold final test pressure for time specified.

Examine piping for leakage using soap bubble solution, or by test gage monitoring.

If leaks are found, they shall be eliminated by tightening, repair, or replacement, as appropriate and test repeated until no leakage is found.

Where repairs or additions are made to piping system following the pressure test, the affected piping shall be tested.  Minor repairs and additions are not required to be pressure tested, provided that the work is inspected and connections are tested with a noncorrosive leak-detecting fluid or other leak-detecting methods approved by the authority having jurisdiction. Testing will not be required in cases where it does not include addition to, replacement, alteration or relocation of, any piping, or in any cases where piping is set up temporarily for exhibition purposes.

PRESSURE TESTING

Fire Protection Piping:

Below Grade: Test with water in accordance with NFPA 24 at a minimum of 200 psig, or at 50 psig in excess of the system working pressure, whichever is greater for 2 hours. Piping shall maintain test pressure +/- 5 psi for the duration of the test and there shall be no visible signs of leakage.

Above Grade: Test with water in accordance with NFPA 13 at a minimum of 200 psig, or 50 psig in excess of the system working pressure, whichever is greater, for 2 hours and shall maintain that pressure without loss.

Plumbing Piping:

Sanitary Waste and Vent Piping Within Building to Building Wall, including condensate drain line from cooling coils:

Test with water in accordance with the IAPMO UPC to a minimum of 10 foot head of water.  Keep water in system for at least 1 hour before inspection starts.

Acceptable Alternate: Test with air at 5 psig and hold pressure for at least 15 minutes.

Note: This alternative method may not be used for plastic piping.

For modifications to existing plug the outlet of the drain piping, and fill pipe with water to the point of overflow. After 15 minutes, check piping for leaks. No loss of water from the piping for the duration of the test indicates that the system meets the requirements of the project.

Sanitary Sewer Piping Beyond Building Wall (other than Force Main): Completely fill system with water and let stand for at least 1 hour before inspection starts, then visually inspect to ensure that all joints are tight.

For partial system tests, test with water in accordance with the IAPMO UPC to a minimum of 10 foot head of water.  Keep water in system for at least 1 hour before inspection starts.

Acceptable Alternate: Test with air at 5 psig and hold pressure for at least 15 minutes.

Note: This alternative testing method may not be used for plastic piping.

Sanitary Sewer Force Main: Test with water at [    ] psig for 2 hours.

*************************************************************************************************************

Test force main piping to 1.5 times operating pressure, 25 psig minimum.

*************************************************************************************************************

Potable Water Inside Building: Test with water at [    ] psig for 30 minutes.

Potable Water Site Main to Building Backflow Preventer:  Test with water at [    ] psig for 2 hours.

*************************************************************************************************************

Test potable water piping to 1.5 times operating pressure, 100 psig minimum.

*************************************************************************************************************

Nonpotable Water:  Test with water in accordance with the IAPMO UPC at [   ] psig for 30 minutes.

*************************************************************************************************************

Test nonpotable water piping to 1.5 times operating pressure, 100 psig minimum.

*************************************************************************************************************

Rainwater Piping:

Rainwater Piping Inside Building to 5 Feet Outside Building: Test with water in accordance with the IAPMO UPC.  Fill the entire system with water to the point of overflowing.  Keep water in system for at least 1 hour before inspection starts.  If the system is tested in sections, no piping (except the uppermost 10 foot of the system) shall have been submitted to a test of less than 10 foot head of water.

Acceptable Alternate:  Test with air at 5 psig and hold pressure for at least 15 minutes.

Note: pneumatic testing may not be used for plastic piping.

Rainwater Piping Beyond 5 feet of Building: Completely fill system with water and let stand for at least 1 hour before inspection starts, then visually inspect to ensure that all joints are tight.

Natural Gas Piping

Operating Pressure up to 5 psig: Test with air or inert gas at 60 psig for 8 hours

      - Operating Pressure Greater than 5 psig to 100 psig: Test with inert gas at 160 psig for 24 hour.  Bring pressure to 160 psig and equalize to ambient temperature before starting pressure test; re-pressure as necessary to attain 160 psig.  Record test with a continuous (24 hour) calibrated pressure recording chart, calibrated and certified per LANL requirements prior to each pressure test.  Recorded pressure line shall be continuous, even and virtually “straight” without abrupt glitches, jogs or changes.  Pressure line shall return to its starting position pressure at end of 24 hour period.

Compressed Air

Test with air at [    ] psig in accordance with ASME B31.9, paragraph 937.4 for 30 minutes.

If using soap bubble solution for detecting leaks, hold pressure for a minimum of 10 minutes prior to applying soap bubble solution.

*************************************************************************************************************

Test compressed air piping to 1.25 times design pressure.  (Note: ASME B31.9 paragraph 937.4.5 only requires the test pressure to be maintained at a minimum of 10 minutes).

*************************************************************************************************************

Instrument Air

Test with air at [    ] psig in accordance with ASME B31.9, paragraph 937.4.for 30 minutes.

If using soap bubble solution for detecting leaks, hold pressure for a minimum of 10 minutes prior to applying soap bubble solution.

*************************************************************************************************************

Test instrument air to 1.25 times design pressure.  (Note: ASME B31.9 paragraph 937.4.5 only requires the test pressure to be maintained at a minimum of 10 minutes).

*************************************************************************************************************

Hydronic Piping (heating hot water, chilled water, tower water, condenser water, make-up water and equipment drains)

Test with water in accordance with the Uniform Mechanical Code (IAPMO UMC) at [   ] psig for at least 30 minutes.

*************************************************************************************************************

Test hydronic piping to 1.5 times operating pressure, 100 psig minimum.

*************************************************************************************************************

For modifications to existing piping bring system up to operating pressure gradually. Visually examine the piping for leaks at one-half the system operating pressure. Perform a final examination at the system operating pressure. No leaking from the piping indicates that the system meets the requirement of the project. (Per ASME 31.9, paragraph 937.5.2)

Steam and Condensate Service Piping: Test with water at [    ] psig.  Test pressure shall be maintained for 30 minutes.

*************************************************************************************************************

Test steam and condensate service piping to 1.5 times design pressure, 100 psig minimum.  If the design pressure is other than 150 psig, the test pressure should be adjusted from 180 psig.

*************************************************************************************************************

Steam and Condensate Distribution Piping Systems:

Distribution Piping: Test with air or inert gas at 180 psig minimum for 1 hour.

Pre-insulated Conduit Systems: Outer steel casing, test with air at 15 psig for 1 hour or as otherwise specified in manufacture’s written instructions.

Refrigerant Piping:

Test in accordance with the Uniform Mechanical Code (IAPMO UMC).

Pressure test with dry nitrogen mixed with a trace of halocarbon (HCFC-22) gas for 24 hours.  Test the high and low side of each system at not less than the lower of the pressure noted in the IAPMO UMC for field leak test pressure or the setting of the pressure relief valve.  Record test with a pressure-recording chart and check system with an electronic halogen leak detector or ultrasonic leak detector.

Do not use oxygen, acetylene, or other flammable/combustible gases or gas mixtures for leak testing.

40 CFR 82.156 (b)(I)(B) prohibits use of refrigerants for leak testing.  It does allow the use of trace quantities of HCFC-22 as a tracer gas.

After successful completion of nitrogen test, remove pressurization gas and evacuate system to 1 mm Hg (1 Torr or 1000 microns) or less to remove moisture and non-condensables.  After 30 minutes, if the vacuum level has not risen higher than 2.5 mm Hg (2.5 Torr or 2500 microns), the leak rate is acceptable.  Check system with an electronic manometer or thermocouple gauge.

After successful completion of vacuum test, charge piping with system refrigerant.  If start up is not within 24 hour, temporarily pressurize to 5 psig with system refrigerant.

Provide a dated test report to the LANL STR for systems containing 50 pounds or more of refrigerant.  Include in report the name and number designation of refrigerant used and the field pressure test applied to the high and low side of the system.  The installer shall sign the test report.

Vacuum Piping: Evacuate to 1mm Hg (1 Torr or 1000 microns) measured with an electronic manometer or thermocouple gauge.  After 2 hours, if vacuum level has risen to no higher than 2.5 mm Hg (2.5 Torr or 2500 microns), the leak test is acceptable.

Hazardous Waste and Vent Double Wall Containment Piping:

Inner Pipe and Vent: Test with air at 5 psig for 30 minutes or as otherwise specified in manufacturer’s written instructions.

Outer Pipe: Test with air at 5 psig for 30 minutes or as otherwise specified in manufacturer’s written instructions.

*************************************************************************************************************

Note: ASME B31.3 paragraph 345.2.2 or ASME B31.9 paragraph 937.4.5 only requires the test pressure to be maintained at a minimum of 10 minutes.

*************************************************************************************************************

Laboratory Gas Piping:

Test [           ] piping with cylinder nitrogen at [    ] psig for 30 minutes.

************************************************************************************************************

Test laboratory gas piping to 1.25 times design pressure.  (Note: ASME B31.3 paragraph 345.2.2 or ASME B31.9 paragraph 937.4.5 only requires the test pressure to be maintained at a minimum of 10 minutes).

*************************************************************************************************************

After test has been satisfactorily completed, temporarily reduce pressure to 5 psig with system nitrogen.

Other Process Piping (B31.3):

************************************************************************************************************

Test pressure and duration may be specified here for the fluids which Section does not specify elsewhere.

************************************************************************************************************

      - Perform hydrostatic and/or pneumatic testing, when approved by the owner, using the test pressures and durations listed below. Hydrostatic testing shall not be performed on piping designed to carry gases.  Testing shall be performed in accordance with the requirements in ASME B31.3, Section 345.

  - Hydrostatic testing (150% of design pressure) at ____psig for ___  minutes [10 is minimum].

**********OR*****

  - Pneumatic testing (110% of design pressure) at ____ psig for ___  minutes [10 is minimum].

      - PVC and CPVC piping shall not be pneumatically tested.

      - Piping subject to external pressure shall be tested at 1.5 times the external differential pressure, but not less than 15 psig.

      - For double wall (containment) piping:

  - Inner piping: at________psig for ___  minutes [10 is minimum].

  - Outer piping: at________psig for ___  minutes [10 is minimum].

      - Unless noted otherwise, water and air shall be used for hydrostatic test and pneumatic test respectively.

      - Other leak tests such as pressure/vacuum decay may be performed, but shall not be used as a substitute for sensitive leak tests required for Category M fluid service.

      - For new construction attachment to existing systems, the final weld connecting piping systems or components which have been successfully tested need not be leak tested, but shall be examined in-progress and 100% radiographic or 100% ultrasonic examined.

Testing for Holidays:

Test the following buried coated steel piping systems for holidays:

Natural gas.

[List other piping systems].

Perform holiday test in accordance with the following procedure:

After pipe has been welded, joints wrapped, and pipe is ready for lowering into trench, test coating for flaws (holidays). Test coated piping system throughout its length for flaws in coating system by means of a high-potential flaw detector that can impress a maximum of 8,000 volts across coating.  One electrode of tester shall maintain complete circumferential contact with coating while transversing entire length of coating system and other electrode shall be the underlying metal pipe.  An electrical discharge through coating detected visually or by instrument, shall constitute failure of this test.

Actual working voltage of detector on pipe will depend upon thickness of coating and size of pipe.  A thin coating on a large pipe will offer a capacitive load to the detector that will drop the working voltage several thousand volts below the "no-load" voltage.  Detector output may also have to be increased to overcome conditions such as extremely dry rock, or sandy soil.

Important!  Do not cut ground cable to a shorter length.  The length supplied is important to proper operation of the detector.  Keep as much of the cable as possible in contact with the earth.  Straighten out kinks where possible and do not let it ride up over skids.  In dry areas it will help to drag the cable in the ditch where there is more moisture.  The pipe should be grounded.

Mark holidays as they are found and repair prior to lowering pipe into trench.  Repair holidays in factory coating by removing initial coating and undercoating for a minimum of 4 inches on each side of holiday.  Remove coating around holiday and feather edge to pipe wall for sufficient distance to make a satisfactory repair.  Apply primer (Polyken 1027) to the holiday to form a bond over the entire surface of the holiday and then spirally wrap pipe with a double layer of half-lapped 35 mil polyethylene tape (Polyken 934) for a minimum of 2 inches on each side of the holiday.

Repair holidays in joint wrappings by removing field applied coating in area of holiday and rewrapping.  LANL STR or designated representative will approve all areas of joint coating.

RETESTING

If piping does not pass test, locate and repair leaks and repeat testing procedure until satisfactory results are obtained.

Make repairs to piping with new materials.  Caulking on screwed joints, cracks, or holes is not acceptable.

END OF SECTION

************************************************************

Do not delete the following reference information:

************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 22 0813 Rev. 5, dated July 24, 2012.