SECTION 22 0813

TESTING PIPING SYSTEMS

*************************************************************************************************************

LANL MASTER SPECIFICATION

Word file at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  The specifications must also be edited to delete specification items for processes, items, or designs that are not included in the project -- and specifiers notes such as these.  This specification template is written to meet requirements contained in the LANL Engineering Standards Manual (ESM).

To seek a variance from requirements of the ESM that are applicable, contact the ESM Mechanical POC for interior piping systems, Civil POC for exterior piping systems.  Please contact applicable POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Ch 1 Section Z10 Specifications and Quality sections.

*************************************************************************************************************

GENERAL

SECTION INCLUDES

Pressure testing of the following systems:

Fire protection piping

Plumbing piping (sewer lines, water lines, rainwater lines)

Natural gas piping

Compressed air piping

Instrument air piping

Hydronic piping

Steam and condensate service piping

Steam and condensate distribution piping system

Refrigerant piping

Vacuum piping

Hazardous waste and vent double wall containment piping

Laboratory gas piping

Other Process Piping (B31.3)

Holiday testing (buried coated steel piping)

RELATED SECTIONS

Section 01 3545, Water Discharge Requirements.

Section 01 4000, Quality Requirements.

Section 01 4216, Definitions

Section 23 2500, HVAC Water Treatment.

DEFINITIONS

Refer to Section 01 4216, Definitions.

*************************************************************************************************************

Designer note:

In the listing below, designer must eliminate standards that are not applicable to the project, add standards that are applicable, and update code and standard edition years to match project code of record—or eliminate years and state that all shall be taken as latest.

This template was developed to meet the requirements for ASME 31 code editions listed.  Application of this template to different editions of the ASME code(s) will require a detailed review of the code and ESM Chapter 17.

*************************************************************************************************************

REFERENCES

    - ASME B31.1- 2016, Power Piping

    - ASME B31.3 - 2016, Process Piping

    - ASME B31.5 - 2016, Refrigerant Piping and Heat Transfer Components

    - ASME B31.8 - 2016, Gas Transmission and Distribution Piping Systems

    - ASME B31.9 - 2014, Building Services Piping

    - ASTM E515-11, Standard Practice for Leaks Using Bubble Emission Techniques

    - ASTM E1003-13, Standard Practice for Hydrostatic Leak Testing

    - IAPMO UPC 2012

    - NFPA 13 - 2017, Standard for the Installation of Sprinkler Systems

    - NFPA 24- 2016, Standard for the Installation of Private Fire Service Mains and Their Appurtenances

    - NFPA 54 - 2015, National Fuel Gas Code

    - UL-404, Standard for Gauges, Indicating Pressure, for Compressed Gas Service

    - 40 CFR 82, Protection of Stratospheric Ozone

    - 49 CFR 192, Transportation of Natural and Other Gas by Pipeline: Minimum Federal Safety Standards

SUBCONTRACTOR REQUIREMENTS

Notify LANL Subcontract Technical Representative (STR) at least 24 hours (1 working day) in advance to arrange for onsite witnessing by LANL inspector of the piping test (a hold/witness point).

For discharge requirements of water used for pressure testing comply with Section 01 3545, Water Discharge Requirements.

Notify LANL STR immediately in the event of any accidental discharge.

SUBMITTALS

Action Submittals

Test plan for approval that includes:

Material of construction

Design pressures

Test pressures and duration of tests

Test medium and method of achieving the test pressure

Certification on calibration of pressure gauges

Method to exclude personnel from the area containing the system to be tested.

Over-pressurization protection/prevention: Device make/model number, certification, pressure relief set point, point of installation in system.

Informational Submittals

Test Reports:  Submit within 10 working days of successful test.

PRODUCTS

  - MATERIALS

Furnish instruments, equipment, material and labor necessary to conduct tests.

Calibrate testing equipment at reasonable intervals with devices of accuracy traceable to National Institute of Standards and Technology (NIST). Test pressure shall be within the calibration range.

Test gauges used shall be in accordance with IAPMO UPC-2012, Section 318.

Pressure gauges meeting Underwriters Laboratories (UL) in accordance with UL-404, “Standard for Gauges, Indicating Pressure, for Compressed Gas Service” Standard for Safety.

Gauges shall be protected by tempered safety glass or plastic face or shield and blowout back or plug.

*************************************************************************************************************

Designer Notes:

Digital gauges are allowed provided they provide at least the same accuracy and calibration as analog (mechanical) gauges.

Vacuum testing digital gauges shall bound by a decade—e.g., if the level of vacuum required for the testing is 999 to 100 micron, a digital gauge shall be accurate to 10 micron.  Vacuum test digital gauges also require test gauge calibration (for LANL performed, to P330-2).

*************************************************************************************************************

EXECUTION

  - FIELD QUALITY CONTROL

Perform piping pressure test before water treatment, cleaning, or flushing to avoid possible discharge of chemicals due to pipe or joint failure during a pressure test. Refer to Section 23 2500, HVAC Water Treatment.

All examination records and pressure test plans must be complete and submitted prior to testing.

Piping being tested shall remain exposed until LANL has approved the test results.

Trenches may be backfilled between joints before testing to prevent movement of pipe during testing.  Ensure that thrust blocks are sufficiently hardened before testing.

Piping being tested shall not leak nor show any change in test pressure for duration specified unless otherwise noted.

Where portion of piping system is to be concealed before completion, the portion shall be tested separately as specified for the entire system.

Ensure piping supports are in place.

Isolate system gages, sensors, etc., from pressure tests so instruments and devices are not damaged.  Test pressure shall not exceed the maximum allowable test pressure for any vessel, pump, valves, or other component in the system.

Hydrostatic (Water) Testing:

Use potable water as test medium.  Do not fill system until the LANL STR has approved the source of water supply.

Provide vents at high points to release trapped air while filling system.

Provide drains at low points for complete removal of test liquid.

Follow ASTM E1003–Standard Practice for Hydrostatic Leak Testing for detecting leaks [and] [or ] [use other enhanced detection methods like pressure decay or vacuum decay techniques.]

After the test duration [reduce pressure to design pressure and] visually examine the system for leaks.

Drain system if there is a potential for freezing, e.g., no heat in building, coil in outside air stream, or other similar situations.

Pneumatic (Air) Testing– B31.3 345.1(c) pneumatic testing is only allowed by owner approval and is currently set at a maximum of 2 cubic feet (ft3).

*************************************************************************************************************

Designer Notes:

Request ES-DO approval for larger than 2 cubic feet of test volume

*************************************************************************************************************

Use clean dry air (Excluded from use with natural gas pipe testing) or inert gas as the test medium.

Barricade the area around the system to be tested.

Prior to application of full air test pressure, apply a preliminary test of not more than 10 psig to reveal possible major leaks.

After preliminary test, raise pressure in stages not more than 25 percent up to full test pressure, allowing at least 10 minutes for equalization of strain and detection of major leaks at each intermediate stage.  Hold final test pressure for time specified.

If test pressure is 25 psig or less, pressure can be raised in a single increment.

      - Use ASTM E515 Standard Practice for Leaks Using Bubble Emission Techniques, for detecting leaks [and] [or ] [use other enhanced detection methods like pressure decay or vacuum decay techniques.]

      - After the test duration [reduce pressure to design pressure and] visually examine the system for leaks.

If leaks are found, eliminate them by tightening, repair, or replacement, as appropriate and test repeated until no leakage is found.

Where repairs or additions are made to piping system following the pressure test, test the affected piping.  Testing is not required in cases where it does not include addition to, replacement, alteration or relocation of, any piping, or in any cases where piping is set up temporarily for exhibition purposes.

  - PRESSURE TESTING

*************************************************************************************************************

Designer Note:

Piping joints for B31.1, B31.3, B31.5, and B31.9 pressure systems connecting to existing piping shall be leak tested in accordance with the Engineering Standards Manual STD-342-100 Chapter 17, Pressure Safety, Section EXIST - Legacy System Requirements, 3.0 Modification or Maintenance of an Existing System.

Qualified examiners are not required for code leak tests except when specified by the code, for example B31.3 Category M Fluid Service.

The design has the discretion to require qualified examiners and examination procedures.

************************************************************************************************************

Fire Protection Piping:

Below Grade: Test with water in accordance with NFPA 24 at a minimum of 200 psig, or at 50 psig in excess of the system working pressure, whichever is greater for 2 hours. Piping shall maintain test pressure +/- 5 psi for the duration of the test and there shall be no visible signs of leakage.

Above Grade: Test with water in accordance with NFPA 13 at a minimum of 200 psig, or 50 psig in excess of the system working pressure, whichever is greater, for 2 hours and shall maintain that pressure without loss.

For modifications to existing piping bring system up to operating pressure gradually. Visually examine the piping for leaks at one-half the system operating pressure. Perform a final examination at the system operating pressure. No leaking from the piping indicates that the system meets the requirement of the project.

Plumbing Piping:

      - Pumped Drain Piping (UPC Code of Record)

        - Pumped Drain: Test with water at 50 psig for 3 hours per ASME B31.9.

Sanitary Waste and Vent Piping Within Building to Building Wall, including condensate drain line from cooling coils:

Test with water in accordance with the IAPMO UPC to a minimum of 10 foot head of water.  Keep water in system for at least 1 hour before inspection starts.

Acceptable Alternate: Test with air at 5 psig and hold pressure for at least 15 minutes.

Note: This alternative method may not be used for plastic piping.

For modifications to existing plug the outlet of the drain piping, and fill pipe with water to the point of overflow. After 15 minutes, check piping for leaks. No loss of water from the piping for the duration of the test indicates that the system meets the requirements of the project. [If it is not possible to isolate the modifications from the remainder of the system, a visual inspection is acceptable.]

Sanitary Sewer Piping Beyond Building Wall (other than Force Main): Completely fill system with water and let stand for at least 1 hour before inspection starts, then visually inspect to ensure that all joints are tight.

For partial system tests, test with water in accordance with the IAPMO UPC to a minimum of 10 foot head of water.  Keep water in system for at least 1 hour before inspection starts.

Acceptable Alternate: Test with air at 5 psig and hold pressure for at least 15 minutes.

Note: This alternative testing method may not be used for plastic piping.

Sanitary Sewer Force Main: Test with water at [    ] psig for 2 hours.

*************************************************************************************************************

Test force main piping to 1.5 times operating pressure, 25 psig minimum.

*************************************************************************************************************

Potable Water Inside Building: Test with water at [    ] psig for 30 minutes.

Potable Water Site Main to Building Backflow Preventer:  Test with water at [    ] psig for 2 hours.

*************************************************************************************************************

Test potable water piping to 1.5 times operating pressure, 100 psig minimum.

*************************************************************************************************************

Nonpotable Water:  Test with water in accordance with the IAPMO UPC at [   ] psig for 30 minutes.

*************************************************************************************************************

Test nonpotable water piping to 1.5 times operating pressure, 100 psig minimum.

*************************************************************************************************************

Rainwater Piping:

Rainwater Piping Inside Building to 5 Feet Outside Building: Test with water in accordance with the IAPMO UPC.  Fill the entire system with water to the point of overflowing.  Keep water in system for at least 1 hour before inspection starts.  If the system is tested in segments, no piping (except the uppermost 10 feet of the system) shall have been submitted to a test of less than 10 foot head of water.

Acceptable Alternate:  Test with air at 5 psig and hold pressure for at least 15 minutes.

Note: pneumatic testing may not be used for plastic piping.

Rainwater Piping Beyond 5 feet of Building: Completely fill system with water and let stand for at least 1 hour before inspection starts, then visually inspect to ensure that all joints are tight.

Natural Gas Piping

Operating Pressure up to 14 inches w.c.: Test with air or inert gas at 10 psig for [15] minutes.

Operating pressure higher that 14 inches w.g.: The test pressure shall be not less than 60 psig for [30] minutes.

Distribution piping

        - Test with inert gas at 160 psig for not less than 1/2 hour for each 500 ft3 (14m3) of pipe volume or fraction thereof. Minimum duration of pressure test shall be 1/2 hour. The duration of the test shall not exceed 8 hours.  Bring pressure to 160 psig and equalize to ambient temperature before starting pressure test; re-pressure as necessary to attain 160 psig prior to beginning test.  Record test with a continuous, 24-hour, calibrated pressure recording chart, calibrated and certified per LANL requirements prior to each pressure test.  Recorded pressure line shall be continuous, even, and virtually “straight” without abrupt glitches, jogs or changes.  The chart pressure line shall return to within five (5) percent of the starting position pressure at end of testing period.

Compressed Air (Less than 150 psig design pressure)

Test with air at [    ] psig in accordance with ASME B31.9, paragraph 937.4 for 30 minutes.

*************************************************************************************************************

Test compressed air piping to 1.25 times design pressure.  (Note: ASME B31.9 paragraph 937.4.5 only requires the test pressure to be maintained at a minimum of 10 minutes).

*************************************************************************************************************

Instrument Air (Less than 150 psig design pressure)

Test with air at [    ] psig in accordance with ASME B31.9, paragraph 937.4.for 30 minutes.

*************************************************************************************************************

Test instrument air to 1.25 times design pressure, but not more than 150 psig, see ASME B31.9 937.3.  (Note: ASME B31.9 paragraph 937.4.5 only requires the test pressure to be maintained at a minimum of 10 minutes).

*************************************************************************************************************

Hydronic Piping (heating hot water, chilled water, tower water, condenser water, make-up water and equipment drains)

Test with water in accordance with ASME B31.9 [year] at [   ] psig for at least [10] minutes.

*************************************************************************************************************

Test hydronic piping to 1.5 times operating pressure.

*************************************************************************************************************

For modifications to existing piping test the connection between new and existing at normal operating pressure. Bring system up to operating pressure gradually. Visually examine the piping for leaks at one-half the system operating pressure. Perform a final examination at the system operating pressure. No leaking from the piping indicates that the system meets the requirement of the project.

Steam and Condensate Service Piping: (B31.9)

Test with water at [    ] psig.  Test pressure shall be maintained for 30 minutes.

*************************************************************************************************************

Test steam and condensate service piping to 1.5 times design pressure, 100 psig minimum 150 psig maximum per 900.1.2 (d).  Note: ASME B31.9 Paragraph 937.4.5 only requires the test pressure to be maintained for a minimum of 10 minutes.

*************************************************************************************************************

Steam and Condensate Distribution Piping Systems:  (B31.9)

Distribution Piping: Test with air or inert gas at 100 psig minimum and 150 psig maximum for 1 hour.

Pre-insulated Conduit Systems: Outer steel casing, test with air at 15 psig for 1 hour or as otherwise specified in manufacture’s written instructions. .

*************************************************************************************************************

Test steam and condensate distribution piping to 1.5 times design pressure, 100 psig minimum, 150 psig maximum per B31.9 937.4.

(Note: ASME B31.9 paragraph 937.4.5 only requires the test pressure to be maintained at a minimum of 10 minutes).

*************************************************************************************************************

Refrigerant Piping:

Test in accordance with ASME B31.5 [year]

Pressure test and leak test the refrigerant piping at the following pressures:

| Refrigerant | Design Pressure | Pressure Test | Leak Test |
| --- | --- | --- | --- |
| R-410A | High Side 430 Low Side 250 | High Side 475 PSIG Low Side 260 PSIG | High Side 450 PSIG Low Side 250 PSIG |
| R-407C | High Side 307 Low Side 166 | High Side 340 PSIG Low Side 185 PSIG | High Side 325 PSIG Low Side 175PSIG |
| R-134A | High Side 177 Low Side 87 | High Side 200 PSIG Low Side 100 PSIG | High Side 180 PSIG Low Side 90 PSIG |
| R-404A | High Side 320 Low Side 235 | High Side 355 PSIG Low Side 260 PSIG | High Side 330 PSIG Low Side 240 PSIG |

Pressure test with dry nitrogen mixed with a trace of halocarbon (HCFC-22) gas for [10] minutes.  Test the high and low side of each system at not less than the pressure noted above for test pressure.  Record test with a calibrated pressure gauge and check system with an electronic halogen leak detector or ultrasonic leak detector.

Do not use oxygen, acetylene, or other flammable/combustible gases or gas mixtures for leak testing.

40 CFR 82.156 (b)(I)(B) prohibits use of refrigerants for leak testing.  It does allow the use of trace quantities of HCFC-22 as a tracer gas.

After the pressure test is complete, perform a system leak test at the pressures listed in the table above, per ASME B31.5, para. 538.4.3.

After successful completion of nitrogen tests, remove pressurization gas and evacuate system to remove moisture and non-condensables.  See Specification 23 2300, Refrigerant Piping.

After successful completion of vacuum test, charge piping with system refrigerant per Section 23 2300, Refrigerant Piping.  If start up is not within 24 hours, temporarily pressurize to 5 psig with system refrigerant.

Perform leak and pressure tests in accordance with ASME B31.5, Refrigerant Piping and Heat Transfer Components, paragraphs 538.4.2 and 538.4.3.

Vacuum Piping: Evacuate to 1mm Hg (1 Torr or 1000 microns) measured with an electronic manometer or thermocouple gauge.  After 2 hours, if vacuum level has risen to no higher than 2.5 mm Hg (2.5 Torr or 2500 microns), the leak test is acceptable.

Piping subject to external pressure shall be tested at 1.5 times the external differential pressure, but not less than 15 psig.

Hazardous Waste and Vent Double Wall Containment Piping Including Fire:

Inner Pipe and Vent: Test with water at 5 psig for [10] minutes or for sensitive leak testing including requirements specified in manufacturer’s written instructions.

Outer Pipe: Test with air at [5] psig for [30] minutes including requirements specified in manufacturer’s written instructions.

*************************************************************************************************************

Note: ASME B31.3 paragraph 345.2.2 only requires the test pressure to be maintained at a minimum of 10 minutes. Sensitive leak test is required to meet ASME Case 180.  ASTM E1003 Section 10 Pressure Drop method must be held for 100 minutes minimum (recommend 200 minutes) for this method.

RLW is required to be ASME B31.3 Fluid Category Normal.

*************************************************************************************************************

Laboratory Gas Piping:

      - Test piping with oil-free, dry cylinder nitrogen up to 1.25 times the design; pressure of 100 psig, not to exceed 150 psig, in accordance with ASME B31.9, paragraph 937.4 for 30 minutes.

*************************************************************************************************************

Test laboratory gas piping to 1.25 times design pressure.  (Note: ASME B31.9 paragraph 937.4.5 only requires the test pressure to be maintained at a minimum of 10 minutes).

*************************************************************************************************************

After test has been satisfactorily completed, temporarily reduce pressure to 5 psig with system nitrogen.

    - RO Water Piping:

      - RO piping shall be leak tested with deionized water at 1.5 times system design pressure and shall show no drop in pressure in a two-hour period. ASME Section V requires the use of a qualified examiner and a qualified procedure.  Calibrated gauges are also required.

      - Upon completion of the leak testing, all piping installed shall be cleaned with chlorinated water (sodium hypochlorite, 500 ppm) for a four-hour period.

    - Process Piping (B31.3):

      - Process piping shall be pneumatically leak tested at [120] psig, not to exceed [133] psig in accordance with ASME B31.3, 345.5 “Normal” Fluid Service after owner’s approval per paragraph 345.5. A leak test shall be maintained for at least 10 minutes, and all joints and connections shall be examined for leaks as required in paragraph 345.2.2 (a)

      - Category D piping shall be tested in accordance with ASME B31.3, 345.7.

    - Category M Fluid Service Piping (B31.3):

      - Category M Fluid Service Piping shall be leak tested and sensitive leak tested in accordance with ASME B31.3, Paragraphs M345 and 345.8.

      - A qualified examiner with a procedure that is compliant with ASME Section V and which must be written by the engineer is required.

    - Non-Metallic Pipe (B31.3):

      - Non-Metallic (plastic) pipe shall be tested in accordance with ASME B31.3.

Other Process Piping (B31.3):

************************************************************************************************************

Test pressure and duration may be specified here for the fluids which are not addressed in this Section.

************************************************************************************************************

      - Perform hydrostatic and/or pneumatic testing, when approved by the owner, using the test pressures and durations listed below. Hydrostatic testing shall not be performed on piping designed to carry gases.  Testing shall be performed in accordance with the requirements in ASME B31.3, Section 345.

  - Hydrostatic testing (150% of design pressure) at ____psig for ___ minutes [10 is minimum].

**********OR*****

  - Pneumatic testing (110% of design pressure) at ____ psig for ___ minutes [10 is minimum].

      - PVC and CPVC piping shall not be pneumatically tested.

      - Piping subject to external pressure shall be tested at 1.5 times the external differential pressure, but not less than 15 psig.

      - For double wall (containment) piping:

  - Inner piping: at ________psig for ___ minutes [10 is minimum].

  - Outer piping: at ________psig for ___ minutes [10 is minimum].

      - Unless noted otherwise, water and air shall be used for hydrostatic test and pneumatic test respectively.

      - Other evaluations such as pressure/vacuum decay may be performed, but shall not be used as a substitute for the code leak test or sensitive leak test required for Category M fluid service.

      - All examinations must be in accordance with ASME B&PVC Section V.

      - For new construction attachment to existing systems, the final weld connecting piping systems or components which have been successfully tested need not be leak tested, but shall be examined in-progress and 100% radiographic or 100% ultrasonic examined as a closure, see 345.2.3(c).

RETESTING

    - If piping does not pass test, locate leak, safely vent pressure repair leaks and repeat testing procedure until satisfactory results are obtained.

    - Make repairs to piping with new materials.  Caulking on screwed joints, cracks, or holes is not acceptable.

    - Notify LANL STR at least 24 hours (1 working day) in advance to arrange for onsite witnessing by LANL inspector of the piping retesting (a hold/witness point).

END OF SECTION

************************************************************

Do not delete the following reference information:

************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project spec section is based on LANL Master Specification Section 22 0813 Rev. 8, dated September 21, 2017.