SECTION 22 1500

COMPRESSED-AIR SYSTEMS

*************************************************************************************************************

LANL MASTER SPECIFICATION

The designer is encouraged to review the DOE Handbook 1132, Design Considerations and ESM Chapters 6, 13, and 17.

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  This section must also be edited to delete requirements for processes, items, or designs that are not included in the project—and specifier’s notes such as these.

Please contact Mechanical Standards POC with suggestions for improvements.
When assembling a specification package, include applicable sections from all Divisions, especially Division 1, General requirements.

Section developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

This section is primary written for piping inside a building.  Large, outside systems should normally be covered in the site utilities series (Div 33).  The utility sections may reference this section.

NOTE:  When compressed air system exceeds 150 psig, verify all material specified meets the design pressure/temperature requirements.  Systems with pressures greater than 150 psig must be constructed to ASME B31.3, Process Piping; see Section 40 0504.

Refer to LANL Standard Drawings ST-D2090-1 for compressed air component details.

Seismic: In order to edit this section for Project-specific seismic requirements, refer to author notes that say/begin with “Seismic” and the “Seismic Specification Guide for Nonstructural Components: ASME B31 Piping” posted with the templates for guidance on properly editing this section.

*************************************************************************************************************

GENERAL

Section Includes

General requirements for tube, pipe, piping components, materials, fittings, valves, flanges, and installation of process piping systems applicable to ASME B31.9, Building Services Piping, [2017][YEAR].

SUMMARY

Section Includes

Pipe fittings, valves, and accessories

Filters

Automatic drain valves

Torpedo Oil/Water separators

Air dryers

Pressure regulating valves

Air receivers

Safety valves

Air compressors

  - RELATED SECTIONS

    - Section 01 2500, Substitution Procedures

    - Section 01 3300, Submittal Procedures

    - Section 01 4000, Quality Requirements

    - Section 01 4115, Pressure Safety Submittals

    - Section 01 4200, References

    - Section 01 4444, Offsite Welding and Joining Requirements

    - Section 01 4455, Onsite Welding and Joining Requirements

********************************************************************************************

Seismic:  Edit “H” per Guide

********************************************************************************************

    - Section 01 8734, Seismic Qualification of Nonstructural Components (IBC), for requirements pertaining to [manufacturer’s certification] [and] [special certification].

    - Section 22 0529, Hangers and Supports for Plumbing Piping and Equipment

********************************************************************************************

Seismic:  Edit “J” per Guide

********************************************************************************************

    - Section 22 0548.23, Vibration and Seismic Controls for Mechanical Systems for [seismic-design criteria,] submittal requirements, devices for seismic restraint, and installation requirements for these devices.

    - Section 22 0554, Identification for Plumbing, HVAC, and Fire Protection and   Equipment

    - Section 22 0713, Plumbing and HVAC Insulation

    - Section 22 0813, Testing Piping Systems

References

ASME B31.9-[2017][YEAR]

****************************************************************************************************
In the listing below, designer shall eliminate standards that are not applicable to the project and add other standards that are. Then, designer must either (1) specify each B31.9-listed materials’ national standard edition for each remaining standard listed or (2) determine latest is equivalent.  Then modify 1.4 to either (1) choose the first option—and also list the edition year after each standard number (e.g., ASTM F493-04) or (2) choose the second option (and remove the years listed for ASTMs, etc.).

****************************************************************************************************

[[All national standards invoked herein shall be taken to be the edition in effect for the code of record listed above in 1.4.A and shown below, unless noted otherwise]  [All national standards invoked below and herein shall be taken to be the latest edition].

### astm International

    - ASTM A53, Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless

ASTM A197, Standard Specification for Cupola Malleable Iron

ASTM A234, Standard Specification for Piping Fittings of Wrought Carbon Steel and Alloy Steel for Moderate and High Temperature Service

ASTM B32, Standard Specification for Solder Metal

ASTM B68, Standard Specification for Seamless Copper Tube, Bright Annealed

ASTM B75, Standard Specification for Seamless Copper Tube

ASTM B88, Standard Specification for Seamless Copper Water Tube

ASTM B280, Standard Specification for Seamless Copper Tube for Air Conditioning and Refrigeration Field Service

### ASME (American Society of Mechanical Engineers)

    - ASME PCC-1, Guidelines for Pressure Boundary Bolted Flange Joint Assembly

    - B40.100, Pressure Gauges and Gauge Attachments

ASME B1 Series

    - ASME B1.20.1, Pipe Threads, General Purpose (Inch)

ASME B16 Series

    - ASME B16.3, Malleable Iron Threaded Fittings Classes 150 and 300

    - ASME B16.9, Factory Made Wrought Steel Buttwelding Fittings

    - ASME B16.18, Cast Copper Alloy Solder Joint Pressure Fittings

    - ASME B16.22, Wrought Copper and Copper Alloy Solder-Joint  Pressure Fittings

    - ASME B16.39, Malleable Iron Threaded Pipe Unions Classes 150, 250, and 300

ASME Boiler and Pressure Vessel Code

    - ASME BPVC Section VIII, Division 1, Rules for Construction of Pressure Vessels

    - ASME BPVC Section IX, Welding, Brazing, and Fusing Qualifications

American Welding Society (AWS)

    - AWS A 5.8, Specification for Filler Metals for Brazing and Braze Welding

    - AWS D 2.4, Standard Symbols for Welding, Brazing, and Nondestructive Examination

Manufacturers Standardization Society of the Valve and Fittings Industry (MSS)

    - MSS SP-25, Standard Marking System for Valves, Fittings, Flanges, and Unions

MSS SP-70, Gray Iron Gate Valves, Flanged and Threaded Ends

MSS SP-72, Ball Valves with Flanged or Butt-Welding Ends for General Service

MSS SP-80, Bronze Gate, Globe, Angle, and Check Valves

MSS SP-85, Gray Iron Globe & Angle Valves, Flanged and Threaded Ends

MSS SP-110, Ball Valves Threaded, Socket-Welding, Solder Joint, Grooved and Flared Ends

MSS SP-125, Gray Iron and Ductile Iron In-Line, Spring-Loaded, Center-Guided Check Valves

UL (Underwriters Laboratory)

    - UL 207, Standard for Safety Refrigerant-Containing Components and Accessories, Nonelectrical

    - UL 404, Gauges, Indicating Pressure, for Compressed Gas Service

ACTION SUBMITTALS

Submit the following in accordance with submittal procedures:

Air compressor performance data for LANL elevation (7,500ft).

Manufacturer’s catalog data

Certification of welders and qualified welding procedure per Section [01 4444] [and] [01 4455].

Manufacturer’s installation instructions

Materials/Parts list

Warranties

Examination processes and forms and examiner qualifications for LANL review prior to commencing work.

informational submittals

Welding Inspection Reports, as applicable.

Manufacturer’s data report form for ASME pressure vessels.

closeout submittals

Operational and Maintenance data.

Follow Section 01 4115 Pressure Safety Submittals regarding required documentation.  In addition, provide:

Installation examination evidence documentation required by Article 3.1 of this Section.

maintenance material submittals

Air compressor inlet air filters, two for each compressor

Belts: [One] [Two] for each belt-driven compressor

QUALITY ASSURANCE

Manufacturer Qualifications: Company specializing in manufacturing products specified in this section with minimum 5 years’ experience.

Material and Installation: Conform to ASME B31.9-[2014] [2017, after June 29, 2018], Building Services Piping for systems operating at pressure of 150 psig or less and at temperature of 200°F or less.  For systems beyond above pressure and temperature limitations, conform to ASME B31.1-[2016], Power Piping unless supplying process air; then use ASME B31.3-[2016].  The design codes and pressure(s) for this installation are as follows: B31.[   ]; [   ] psig.

Performance of rotary air compressor shall be tested and rated in accordance with CAGI (Compressed Air and Gas Institute) rotary compressor performance verification program (ISO 1217:[2009] Displacement Compressors-Acceptance Tests).

Air quality classification shall be Class [0], [1],[2],[3],[4] according to ISO 8573-1:  [2010] Compressed air -- Part 1: Contaminants and purity classes.

Welders Certification and Qualified Procedure Standards shall be in accordance with Section IX of ASME Boiler and Pressure Vessel Code. Welding per Sections [01 4444 and/or 01 4455].

Valve Identification:  Each valve shall bear markings in accordance with MSS SP-25, including manufacturer’s name or trademark, the material of construction, and symbols to indicate the service conditions for which the manufacturer rates the valve.

Component identification shall follow ESM Chapter 1, 200, Equipment and Numbering & Labeling.  At existing facilities, component labeling conventions are to be continued to be used to avoid confusion.

WARRANTIES

Provide a minimum of 1-year manufacturer’s warranty, parts and labor, for air compressor system.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTION

Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

*************************************************************************************************************NOTES FOR DESIGNER

On Brazing:  When specifying brazed joints, consider that brazing reduces the tube rating to the fully annealed condition.

On welding:  Welding design shall meet ESM Chapter 17 ADMIN-2 (AA. Welding Systems)

On flanges:  Flange joint design must comply with ASME PCC-1.  Use 01 4731 Flange Assembly for B31 Systems, when issued (project-created equivalent until then).

Copper tubing thickness callouts throughout are below based on LANL Alternate Method VAR-2015-011

*************************************************************************************************************

COPPER TUBING AND FITTINGS (up to 2 inches)

Copper tubing alloy [102, 122] per ASME B31.9 Table I-1. Temper [drawn H and/or annealed O].  Thickness per UL 207, ASTM B88, B75, B68, or B280.

Braze Joints

Fittings: ASME B16.22, wrought copper and copper alloy, solder-joint pressure fittings [and/or] ASME B16.18 cast-copper-alloy solder-joint pressure-fittings

[Manufacturers and model numbers]

AWS A5.8 TB-BCuP-5 silver braze.

Comply with [01 4444, 01 4455].

Solder joint

Application is restricted to tubing less than 4.125 inch OD.

Fittings: ASME B16.22, wrought copper and copper alloy, solder-joint pressure fittings [and/or] ASME B16.18 cast-copper-alloy solder-joint pressure-fittings.

[Manufacturers and model numbers]

Solder in accordance with ASTM B32, Alloy Grade [Sb5, Sn50, other] or UNS [L13950, L55031, other].

Flux [manufacturer, material]

STEEL PIPE AND FITTINGS UP TO 2 INCHES

Pipe:  black steel ASTM A53, Type [E, F, S] grade [A or B], wall thickness [standard wall]. Threaded joints per ASME B1.20.1 for pipe sizes 2 inches and under.

Threaded Joints:

Fittings: Black steel, ASTM A234, butt welding type, ASME B16.9, [and/or], ASTM A197, ASME B16.3 malleable threaded type ASME B1.20.1.

[Manufacturer and model numbers]

STEEL PIPE AND FITTINGS over 2 inches

Pipe: Black steel, ASTM A53, Type [E, F, S], Schedule 40 grade [A or B], standard wall.

Fittings: Steel, ASTM A234, Grade WPB, Schedule 40, butt-welding type, ASME B16.9.

Fittings: ASME B16.28, Wrought Steel Butt-welding Short Radius Elbows and Returns.

Welded Joints: As shown in Drawings.

VALVES

Gates Valves up to 2 inches.

Manufacturer: Nibco, Series 111.

MSS SP-80 Class [125, 150 for threaded, or solder] ends, valve type [1A, 1B, 2, 3, or 4] bronze body, bronze trim.

Gate Valves over 2 to 12 inches.

Manufacturer: Nibco, Series F-617-0

MSS SP-70, Class [125, 250], valve type [I, II, III, IV], construction [NF: non-rising stem, OF: outside screw and yolk], iron body, bronze trim flanged ends.

Globe Valves up to 2 inches.

Manufacturer: Nibco, Series 211.

MSS SP-80, Class [125, 250 for threaded, or solder] ends, valve type [1, 2, or 3] bronze body, bronze trim, rising stem, hand wheel, inside screw.

Globe Valves over 2 inches

Manufacturer: Nibco F-718-B.

MSS SP-85, Class 150 flanged ends, iron body, bronze trim, hand wheel, type [1, 2, or 3] removable bronze disc.

Ball Valves up to 2 inches.

Manufacturer: Nibco, Series 585-70.

MSS SP 110, 150 psi non-shock cold working pressure (CWP) minimum pressure rating.

Bronze, two-piece body, chrome-plated brass ball, full port, Teflon seats and stuffing box ring, blowout proof stem, lever handle, solder or threaded ends.

Ball Valves over 2 inches.

Manufacturer: Nibco, Series F-510-CS-R-66-FS.

MSS SP-72, one piece body, full port ball, flange class 150, 150 psig non-shock cold working pressure (CWP) minimum.

Swing Check Valves up to 2 inches.

Manufacturer: Nibco 413 Series.

MSS SP-80, Type [1, 2] bronze, horizontal swing, Y-pattern, renewable seat and disc, non-shock cold working pressure (CWP) minimum pressure rating. Solder or threaded ends.

Spring Check Valves over 2 inches.

Manufacturer: Nibco F-910-B.

MSS-SP-125, Class 125, cast iron body, fluid to 200 degrees F, renewable seats and disc, spring actuated, flanged.

STRAINER

Tee-type filter, ½ inch NPT, threaded type ASME B1.20.1, [440, 120, 90, 60, 40] micron pore size,

Manufacturer: Swagelok

Model number: SS-8TF2-[440, 120, 90, 60, 40]

UNIONS AND FLANGES

Unions

Ferrous Pipe: ASME B16.39, Class 150, malleable iron, threaded unions.

Copper Tube and Pipe: ASME B16.22, Class 150, bronze unions with soldered joints.

Flanges (N/A to copper)

Forged carbon steel, ASTM A105, Class 150

FLEXIBLE CONNECTOR

Manufacturer:  Universal Metal Hose

Model: Anaconda

Industrial Metal Hose, Refrigeration Products, Armored and Specialty Flexible Hose Components Anaconda Vibration Eliminators, Bronze or Stainless Steel Vibration Eliminators, copper conforms to UL SA 2528, ends per ASME B16.18 and B16.22;

Diameter [   ] inch

Length [   ] inch

Part Number [   ]

*************************************************************************************************************

If individual components listed below are furnished by the compressor manufacturer as part of a packaged system, those components should be listed as compressor accessories under compressor in this Section. The manufacturer (not the vendor) is to provide any line sets required to link the compressor system items.

*************************************************************************************************************

PREFILTER, HIGH-EFFICIENCY COALESCING

*************************************************************************************************************

When selecting filter, assume maximum flow conditions at the minimum operating pressure.  Match inlet and outlet connections to system pipe size.

*************************************************************************************************************

Manufacturers:

Van Air, Housing Series F200, Filter Grade C

Pneumatics Products, Housing Series P2001, Filter Grade SU

High-efficiency coalescing filter efficiency 99.99 percent at 0.6 microns, maximum oil carryover 0.008 ppm by weight, maximum inlet temperature 125 degrees F, maximum clean dry pressure drop 1.50 psid.  Housing maximum working pressure 250 psig at 225 degrees F, furnish with optional two-sided color-coded pressure differential indicator, and without internal float drain.

In/Out Connection: [        ] inches NPT

Flow Capacity: [         ] scfm at 100 psig

AFTERFILTER, HIGH-EFFICIENCY PARTICULATE

*************************************************************************************************************

When selecting filter, assume maximum flow conditions at the minimum operating pressure.  Match inlet and outlet connections to system pipe size.

*************************************************************************************************************

Manufacturers:

Van Air, Housing Series F200, Filter Grade RC

Pneumatics Products, Housing Series P2001, Filter Grade AF

High-efficiency particulate filter efficiency 99.99 percent at 0.9 microns, maximum inlet temperature 150 degrees F, maximum clean dry pressure drop 1.50 psid. Housing maximum working pressure 250 psig at 225 degrees F, furnish with optional two-sided color-coded pressure differential indicator, and without internal float drain.

In/Out Connection: [           ] inches NPT

Flow Capacity: [          ] scfm at 100 psig

AUTOMATIC DRAIN VALVE

Manufacturer: Van Air, Model EDV-2002

Solenoid valve, brass body, NEMA 4 enclosure, rated at 300 psig, open time 1 to 60 seconds cycle time 1-60 minutes, 6 foot power cord with plug, electrical [115V/ 1 PH/60 Hz] [230V/ 1 PH/ 60 Hz], maximum fluid temperature 210 degrees F, ambient temperature range 32-150 degrees F.

Valve In/Out Port Size:  [1/4] [1/2] inch NPT

****** [OR] ******

Automatic drain valve (zero air loss)

Manufacturer: Zeks, Model NCC1701-D.

Zero air loss drain valve, 1/2 inch NPT connections, pressure range 0-230 psi, temperature range 36 - 120 degree F, electrical connection [115] [230] VAC, NEMA 4 enclosure, and Y-strainer.  Operation, 50 volume checks/second.

TORPEDO OIL/WATER SEPARATOR

*************************************************************************************************************

Consult with FOD facility engineer for type of oil/water separator (torpedo or commercially available) to be specified. Specify 2-inch-diameter torpedo for compressors less than or equal to 5hp; 4-inch-diameter torpedo for compressors greater than 5hp.  Alternative is to specify a commercially available oil/water separator such as Van Air Model ES Series.  Consult with manufacturers’ representative for application and sizing information.  If a commercially available oil/water separator is specified, edit Standard Detail ST-D2090-1 accordingly.

*************************************************************************************************************

Manufacturer: Eggelhof Inc., Albuquerque, [4 inch, Model No. 4 - 20 ABS] [2 inch, Model 2 - 20 ABS].

4-inch-diameter oil/water torpedo separator, ABS construction, 20 inch long.

2-inch-diameter oil/water torpedo separator, ABS construction, 20 inch long.

Furnish above with safety cable and 20 x 20 inch polypropylene absorbent pad.

REGENERATIVE AIR DRYER

Manufacturers:

Van Air, Model HLS-[           ], HL-[           ].

Pneumatic Products, DHA Series, Model [          ].

Heatless, regenerative dryer, minus 40 degrees F pressure dew point, solid state controller, twin towers, with adsorbent desiccant, purge exhaust valve and muffler, drain connection and cycle saver control option that adjusts dryer purge to actual moisture load condition and includes failure to switch (FTS) alarm.

Capacity: [          ] scfm at [         ]psig

Power Voltage: [         ] V, [         ] phase, 60 Hz.

REFRIGERATED AIR DRYER (Air-Cooled)

Manufacturers:

Van Air, [Model RD           ].

Hankison, [Model HPR             ].

Refrigerated air dryer, air cooled condenser, 35-38 degrees F pressure dew point, indoor installation (ambient temperature 40-100 degrees F), automatic drain valve, and charged with R134a.

Capacity: [          ] scfm at [      ] degrees F inlet temperature and [           ] psig inlet pressure.

Power Voltage: [        ] V, [      ] phase, 60 Hz.

PRESSURE GAUGE

*************************************************************************************************************

Refer to manufacturer’s recommendations for pressure ranges.  Generally, a range of twice the expected normal pressure is recommended, with a maximum working pressure not exceeding 75 percent of the range.

*************************************************************************************************************

Manufacturer: Ashcroft, Type 1009.

ASME B40.100, Grade 1A, minimum 2 1/2 inch dial, 1/4 inch NPT brass bottom connection, maximum plus or minus 1 percent full scale accuracy, stainless steel case, phosphor bronze bourdon tube, and isolation valve.

Range: [            psi ] [per Drawings].

Cock Valve: 1/4 inch brass plug, 250 psi working pressure valve.  
Manufacturer: Anderson Metals, PAC-56NB, Part No. 138-00110.

Overpressure relief protection must be provided on Bourdon-tube, dial-indicating pressure gauges that operate at pressures greater than 15 psig by one of the following means:

Pressure gauges approved by Underwriters Laboratories (UL) in accordance with UL-404, “Standard for Gauges, Indicating Pressure, for Compressed Gas Service” Standard for Safety.

Tempered safety glass or plastic face or shield and a blowout back or plug for pressure relief.

Pressure gauges that serve primarily a pressure indication for over pressure protection (i.e., not used for process data collection) must have a range of at least 1.25 times, but no more than twice the set pressure of the relief device as recommended in ASME Section VIII, Div. 1, Appendix M, Para. M-14.

PRESSURE REGULATING VALVE

Manufacturer: Norgren

Model: 11-002-031 (100 MAWP)

DEW POINT TEST FITTING

Manufacturer: Swagelok.

Model: QC Series, rated 250 PSIG uncoupled.

Size: Brass quick-disconnect fitting, 1/4 inch FPT x QD with protector.

Part number:  B-QC4-BP-4PF

MOISTURE INDICATOR

*************************************************************************************************************

Provide visible moisture indicator when not provided with regenerative dryer.  Do not install on system with refrigerated dryer.

*************************************************************************************************************

Manufacturers:

Puregas Model [51364 1/8” NPT] [51356, 1/4” NPT]

Van Air, No. 46-2300.

Pneumatic Products, Aquadex.

Visible moisture indicator assembly, with indicating silica gel that changes from blue to pink at dew point of 0 - 10 degrees F, and back to blue when dew point is lower than minus 10 degree F.

*************************************************************************************************************

Designer note:  the relief valve is required to have a calculation meeting the rigor of AP-341-605 to show that it can accommodate the fail-open regulator fault condition and meet the design parameters of ASME B31.9 paragraphs 901.2.3, and 922.1.Pressure Reducing Systems.  The regulator and relief device shown below are examples only and the section must be tailored to the design requirements.  The designer is cautioned that the design must accommodate flow demand requirements of the system as well as relief valve sizing.

The safety relief device(s) on the compressed air receiver shall be meet the requirements of ASME Boiler and Pressure Vessel Section VIII Division 1, UG-125 through UG-138.  In accordance with the ASME B&PVC Section VIII Division 1, UG-125 (a) (3) the designer shall act as the owner’s agent to ensure the required overpressure protection is properly sized for and selected.  There shall be at least one reclosing relief device for normal operation not to exceed 110% of MAWP.  There shall also be relief device(s) to ensure the vessel does not exceed 121% of MAWP during a fire.

*************************************************************************************************************

GAS REGULATORS

Manufacturer/Model:  Swagelok K Series, Part Number: [KPR-AGJA415C2000]

Design Description:  Maximum [500] psig inlet, 0- maximum [45] psig outlet

Fluid Service: Normal,

System Application(s):  Compressed Air

Inlet Size: [¼ in]

Outlet Size: [¼ in]

Cv: [0.20]

Inlet Pressure:  [500 psig]

Outlet Control Range:  [0 to 250] psig

Location:  Above grade

Assembly Methods: ASME B1.20.1 threads

Failure flow in application:  [61.61] SCFM as air with [500] psig maximum inlet pressure

COMPRESSED AIR RELIEF VALVES

Manufacturer/Model:  Kingston Valves, M/N 118, Part Number: [118CSS-2-045]

Description:  stainless steel ASME Section VIII, Div. 1 stamped relief device, set pressure [45 psig]

Fluid Service: Category D

System Application(s):  Compressed Air

Inlet Size: ¼ inch

Set Pressure:  [45 psig (+/- 2  psig)]

Location:  Above grade

Assembly Methods: ASME B1.20.1 threads

Manufacturers rating:  [69] SCFM air

AIR RECEIVER

Manufacturer: [Hanson Tank] [Compressor Manufacturer]

Carbon steel tank built and tested to ASME Section VIII, Division 1 Pressure Vessel Code, “U” stamped. NBIC numbered and registered.

Configuration: [Vertical] [Horizontal] tank with ring base and standard, screw or flange inlet and outlet connections with factory exterior prime coat.

Size: [         ] gallons, rated at [        ] psi, [         ] diameter x [        ] long.

Seismic Design Category [D]

AIR COMPRESSOR or PACKaged system (1/4 through 30 HP)

*************************************************************************************************************

Consult with manufacturer’s representative, commercial guide specs, and the LANL Engineering Manual Mechanical chapter when editing this Article.  Verify compressor capacity (discharge pressure and flow rate) can meet the pressure and flow demands at LANL elevation.  Furnish compressors with an after cooler, mechanical separator and an intake air filter silencer.  If sound control is a factor, an intake filter silencer, muffler or sound enclosure may be required. Furnish duplex compressors with hour meters. For air compressors of greater than 30HP, a separate Section for air compressors may be used.    
*************************************************************************************************************

    - Manufacturer:

Atlas Copco

Sullair

Ingersoll Rand

Quincy

[other]

Compressor: Discharge pressure must be rated for LANL elevation (7,500ft).

Types:

[Reciprocating single or two stage], [rocking piston type], [diaphragm type], [lubricated, non-lubricated or oil less].

[Rotary vane type- oil lubricated],[rotary screw type- oil lubricated or oil less],[rotary scroll type-oil lubricated or oil less].

Controls: [Constant speed- start stop controls], [variable speed controls].

Drives: [Electric motor-V belt drive or gear drive or direct drive], [diesel engine- V belt drive or direct drive] or [  ]

Mounting: [Base mounted],[tank mounted],[portable].

HP: [      ] HP, [ V/phase].

Discharge pressure: [            ] psig rated for 7,500 ft elevation.

Delivery capacity: [              ] scfm (14.5 psia, 68F and 0% relative humidity).

Others: [Diagnostic control devices-high air temperature shutdown, low oil level shutdown], [belt guard], [intake filter], [after cooler], [motor starter].

Compressor accessories (components furnished by the compressor manufacturer):

[     ]

EXECUTION

  - INSTALLATION

Follow the manufacturer’s installation requirements.

Install compressor unit on concrete housekeeping pad. Provide thermometer and pressure gage on discharge piping from each air compressor and on each receiver tank.

Install compressor unit on vibration isolators. Level and bolt in place. See [Section 05 0520] [drawings] for anchors.

Install air piping with a slope of at least 1 inch per 100ft or less downward in direction of flow.

Install branch take-offs to outlets from top of main, with shutoff valve after take-off.  Slope take-off piping to outlets.

Provide drip legs and drain traps at end of each main and branch and at low points of piping system.

Route condensate drains to nearest floor drain.

Install compressed air couplings, female quick connectors, and pressure gages [where branch outlets are indicated] [as indicated on Drawings].

Label piping system in accordance with Section 22 0554, Identification for Plumbing, HVAC and Fire Piping and Equipment.

Pressure test piping system in accordance with Section 22 0813, Testing Piping Systems.

Install piping hangers and supports per Section 22 0529, Hangers and Supports for Plumbing Piping and Equipment.

Cap or seal ends of piping when not connected to mechanical equipment to ensure contamination by foreign material does not occur.

END OF SECTION

*********************************************************

Do not delete the following reference information:

*********************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification section is based on LANL Master Specification Section 22 1500 Rev. 4, dated March 8, 2018.