Section 23 2300 
Refrigerant Piping

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 7 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Pressure Safety/Mechanical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements might be necessary if increased confidence in procurement or execution is desired, and independent review is necessary.  See LANL ESM Chapter 1 - General, Section Z10 specifications and quality sections.

      - ==========================================================

      - This template was developed to meet the requirements for ASME B31.5-2022.  Use with a different edition requires a detailed review of the code and LANL ESM Chapter 17 - Pressure Safety.

      - This specification does not address buried piping. It is strongly discouraged to bury refrigerant piping. It is the responsibility of the Designer to include provisions for corrosion control of buried piping if necessary. Consult other Sections such as Section << 23 2113 - Hydronic Piping>>for template information on buried piping.

      - Seismic:  In order to edit this section for job-specific seismic requirements, refer to author notes that begin with “Seismic.”  Also, see the flowchart and Seismic Specification Guide for Mechanical (posted on LANL specs webpage) for guidance on properly editing this section.

  - *************************************************************************************************************

part 1 - GENERAL

SECTION INCLUDES

      - ***************************************************************************************

      - The following paragraphs are designer choices based on project-specific requirements.

      - ***************************************************************************************

Refrigerant Piping

Piping Fittings

Refrigeration Piping Components

      - ***************************************************************************************

      - The following Sections are not referenced in the body of this Section. Including them are a designer choice.

      - << 01 4000 - Quality Requirements - Non-Nuclear>>

      - << 01 8113.13 - Sustainable Design>>

      - << 22 0548.23 - Vibration and Seismic Controls for Mechanical Systems>>

      - ***************************************************************************************

RELATED requirements

Section << 01 2500 - Substitution Procedures>>

Section << 01 3300 - Submittal Procedures>>

Section << 01 4000 - Quality Requirements - Non-Nuclear>>

Section << 01 4115 - Pressure Safety Submittals>>

Section << 01 4444 - Offsite Welding, Brazing and Joining Requirements>>

Section << 01 4455 - Onsite Welding, Brazing and Joining Requirements>>

Section << 01 4525 - Non-Destructive Examination (NDE) Requirements>>

Section << 01 4631 - Welding, Brazing, and Soldering of Pressure Systems>>

Section << 01 8113.13 - Sustainable Design>>

Section << 07 8400 - Firestopping>>

Section << 22 0529 - Hangers and Supports for Plumbing Piping and Equipment>>

Section << 22 0548.23 - Vibration and Seismic Controls for Mechanical Systems>>

Section << 22 0554 - Identification for Plumbing,  HVAC, and Fire Piping and Equipment>>

Section << 22 0713 - Plumbing and HVAC Insulation>>

Section << 22 0813 - Testing Piping Systems>>

      - ***************************************************************************************

      - The referenced standards editions are based on the code of record ASME B31.5-2022 and ASME BPVC-2023. If the Code of Record for the project refers to a different version of ASME B31.5 & ASME BPVC, the designer is responsible to update the years/editions for the invoked standards. If the invoked standards editions do not comply with those referenced by the Code of Record, EOR needs to evaluate and verify those for equal or better. For the standards without an edition/year, the latest edition is to be used. In addition, the designer must ensure the code and standards editions align between sections in the project specification package and the project design drawings.

      - Note: ASCE 7 edition is based on Code of Record IBC 2021.

      - ***************************************************************************************

REFERENCE Standards

ASCE 7 - Minimum Design Loads and Associated Criteria for Buildings and Other Structures.

ASHRAE 15 - Safety Standard for Refrigeration Systems and Designation and Safety Classification of Refrigerants.

ASME B1.1 - Unified Inch Screw Threads (UN, UNR, and UNJ Thread Forms).

ASME B1.20.1 - Pipe Threads, General Purpose, Inch.

ASME B16.18 - Cast Copper Alloy Solder Joint Pressure Fittings.

ASME B16.22 - Wrought Copper and Copper Alloy Solder-Joint Pressure Fittings.

ASME B16.50 - Wrought Copper and Copper Alloy Braze-Joint Pressure Fittings.

ASME B31.5 - Refrigeration Piping and Heat Transfer Components.

ASME BPVC-IX - Boiler and Pressure Vessel Code, Section IX - Qualification Standard for Welding, Brazing, and Fusing Procedures; Welders; Brazers; and Welding, Brazing, and Fusing Operators.

ASTM B280 - Standard Specification for Seamless Copper Tube for Air Conditioning and Refrigeration Field Service - 2008 (ASME B31.3), 2018 (ASME B31.5), 2016 (ASME B31.9).

NMAC - New Mexico Administrative Code.

SAE J513 - Refrigeration Tube Fittings - General Specifications - 1999 (ASME B31.5), 1999(R2019) (ASME B31.3).

SUBMITTALS

Submit the following in accordance with Section << 01 3300 - Submittal Procedures>>.

Action Submittals:

Catalog data on pipe materials, fittings, valves, and accessories.  Include the manufacturer’s name, model number, parts list, and brief description of equipment and its basic operational features, i.e. data sheet, spec sheet, etc.

        - ******************************************************************************

        - The subparagraph below shall be included when welded, brazed, or soldered joints are specified by the Designer.

        - For high-risk applications such as ML-1 or ML-2, add submittals for “Weld Filler Material Control Procedures” and “Filler Material Certified Material Test Reports CMTRs)” when required. Add “Post-Weld Heat Treatment Procedures” when required.

        - ******************************************************************************

Per the requirements of Section(s) << 01 4444 - Offsite Welding, Brazing and Joining Requirements; and  01 4455 - Onsite Welding, Brazing and Joining Requirements>>, submit:

          - *******Note: Only required as a submittal for Onsite welding, when subcontractor not using LANL WPS/PQR*******

Welding Procedure Specification (WPS) and supporting Procedure Qualification Record (PQR).

          - ********Note: Only required as a submittal for Onsite welding, when subcontractor not tested at LANL*******

Welder Performance Qualification Records (WPQR) including continuity.

Per the requirements of Section << 01 4525 - Non-Destructive Examination (NDE) Requirements>>​, submit:

Written Practice or Procedure for Qualification and Certification of NDE personnel.

NDE Personnel Qualification Records

NDE Procedures

NDE Procedure Qualification Records

NDE Report(s)

NTIP submitted under Section << 01 4525 - Non-Destructive Examination (NDE) Requirements>>.

Before fabrication, submit:

Proof of journeyman certificate of competence in accordance with <<NMAC>> 14.6.6.11

Leak Test plan submitted under Section << 22 0813 - Testing Piping Systems>>.

Cleaning procedures for joint assembly preparation.

After fabrication, submit examination records per <<ASME B31.5>> para. 536.2(d).

Informational Submittals:

Spare Parts and Maintenance Materials list

Installation, Operation, & Maintenance Manual

Warranties

        - ******************************************************************************

        - EPC-CP-QP-0312 Attachment 1 is available at the link below. Those without LANL Internal website access may contact the LANL STR for a copy.

        - https://int.lanl.gov/environment/air/guidance/refrigerants.shtml (LANL Internal only).

        - ******************************************************************************

Provide completed “LANL Refrigerant Service Record Form,” EPC-CP-QP-0312 Attachment 1. Additionally, send completed form to refrigerants@lanl.gov.

QUALITY ASSURANCE

NDE/Inspection and Testing

Subcontractor shall perform inspection and testing to verify the conformance to the requirements in PART 2 of this Section.

Subcontractor shall provide an Inspection and Test Plan indicating all testing and inspection functions to be performed, including hold points during fabrication and assembly, as well as during the Factory Acceptance Testing (FAT).  Hold points are required during the fabrication process to allow inspection, verification, or approval by LANL before the Subcontractor does further work. LANL has the right to waive Hold Points at their discretion.

NDE/Inspection and testing functions shall be performed by qualified personnel using documented procedures and per specified requirements.

NDE/Inspection Records: Subcontractor shall appropriately record, submit, and maintain records documenting the inspection and/or test then submit the completed Inspection Record as part of the QA Document Package. The status of all planned and executed inspection and testing activities shall be logged and traceable to ensure that the required inspection and testing have been performed, and any items that have failed inspection or testing are not inadvertently installed or implemented.

Qualifications

Installer Qualifications

Certify that all personnel have passed relevant qualification tests for joining processes involved and that certification is current.

Metallic Pipe:  Welders and brazers shall be qualified per <<ASME BPVC-IX>> and per Section(s) << 01 4444 - Offsite Welding, Brazing and Joining Requirements; and  01 4455 - Onsite Welding, Brazing and Joining Requirements>>.

Certification of Examination Personnel shall be as given in Section ​<< 01 4525 - Non-Destructive Examination (NDE) Requirements>>​ and shall be maintained for Inspector's review.

LANL Owner’s Inspector will be qualified per <<ASME B31.5>>​ Section 537.4. LANL will act for DOE to designate Owner’s Inspectors or Designee.

Extent and Retention of Records

The following shall be maintained by the fabricator for a minimum of 3 years:

Procedure specification, procedure qualification, and performance qualification records

Results of weld examinations other than visual

Records of the testing of each piping system, which shall include the following information:

date

identification of piping system tested

testing medium

test pressure

signature of examiner and inspector.

PART 2 - PRODUCTS

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted per Section << 01 2500 - Substitution Procedures>> and << 01 4115 - Pressure Safety Submittals>>.

Proposal of unlisted components as substituted components is strongly discouraged and shall be evaluated per Section << 01 2500 - Substitution Procedures>>. Substitutions will be allowed only if the Subcontractor can demonstrate that the product can meet the same code requirements of the item specified in the design. Costs associated with evaluation of substituted unlisted components shall be the responsibility of the Subcontractor.

SEISMIC PERFORMANCE REQUIREMENTS

      - ***************************************************************************************

      - The seismic exemptions noted below are based on ASCE 7-16. If the Code of Record for the project refers to a different version of ASCE 7, the Designer is responsible to check the seismic design requirements per that applicable edition.

      - ***************************************************************************************

Piping systems with trapeze assemblies/rod hangers that meet the requirements per <<ASCE 7>>, Section 13.6.7.3 are seismically exempt.

For piping systems not meeting the above exemptions, Structural EOR shall design seismic supports per LANL ESM Chapter 5 - Structural, Section II; <<ASCE 7>>, Chapter 13; and <<ASME B31.5>>.

      - ***************************************************************************************

      - Where more than one piping system material is specified, provide compatible system components and joints.

      - Provide unions or couplings at locations requiring servicing. Do not use direct-welded or threaded connections to equipment or major valves.

      - Provide flexible connectors at or near equipment where piping configuration does not absorb vibration.

      - Install flexible connectors at right angles to axial movement of compressor, parallel to crankshaft.

      - Provide external equalizer piping on expansion valves with refrigerant distributor connected to evaporator.

      - Comply with ASHRAE 15 procedures for charging and purging of systems and for disposal of refrigerant.

      - The following items should be considered during the design.

        - Install moisture/liquid indicators in liquid line at the inlet of the thermostatic expansion valve or at the inlet of the evaporator coil capillary tube.

        - Install refrigerant service valves in suction and discharge lines of compressor.

        - Install a check valve at the compressor discharge and a liquid accumulator at the compressor suction connection.

        - Install refrigerant charging valve in liquid line between receiver shut-off valve and expansion valve.

        - Install solenoid valves upstream from each expansion valve.  Install solenoid valves in horizontal lines with coil at top and provide electrical connection to solenoid valves.

        - Install thermostatic expansion valves as close as possible to distributors on evaporators and locate expansion valve sensing bulb immediately downstream of evaporator on suction line.

        - Install filter dryers in liquid line between compressor and thermostatic expansion valve or in the suction line of the compressor. Additional filter dryer is not needed if one is provided with the condensing unit.

        - In process examination per ASME B31.5 paragraph 536.6.2 may be substituted for all or part of the substituted for all or part of radiographic examination on a weld-for-weld basis if specified in the engineering design and specifically approved by the Inspector.

      - Brazing reduces the tube pressure rating to the fully annealed condition. Solder joints shall not be used.

      - The following PART 2 Articles are designer choices based on project-specific conditions. Within each Article, paragraphs related to pipe material types, fitting types, component size ranges, etc. are designer choices based on project-specific requirements.

      - ***************************************************************************************

REFRIGERANT PIPING

Copper Tubing: <<ASTM B280>>, Type ACR, Alloy C12200, temper shall be soft annealed O60 or drawn general purpose H58.

Manufacturer: Mueller/Streamline

Model Number:  Nitrogenized ®ACR Tube (Refrigeration Service Tube)

Design Temperature Range: 80 degrees F to 122 degrees F (low side to high side temp per <<ASME B31.5>>)

Pressure Rating: 430 psig minimum

Size (OD): 1/8 inch through 1 3/8 inch OD shall use ACR Type L or Type K,  above 1 3/8 up to 2 5/8 inches OD shall use Type K.

Location:  Above grade

Copper-iron Tubing: <<ASTM B280>>, Alloy C19400

Manufacturer: Mueller/Streamline XHP

Maximum Operating Temperature: 250 degrees F.

Pressure Rating: 1885 psig

Size (OD): For piping 1-1/2 inch OD and greater

Location: Used on the high pressure side of ​​​<< R-410A;  R-454B;  R-32; or  _______>>​​​ systems.

PIPING FITTINGS

      - ***************************************************************************************

      - Flame-Free Press Fittings shall only be used with hard drawn copper tube. Soft annealed coil tube is not permitted.

      - ***************************************************************************************

Flame-Free Press Fittings

Manufacturer: Parker-Sporlan

Model Number: ZoomLock MAX

Temperature Range: -40 degrees to +250 degrees F

Pressure Rating: 600 psig

Size: 1/4 inch through 1-3/8 inch

Only the following fittings are permitted: Couplings, Slip Couplings, Caps, SAE Flares (Only 1/4 inch through 3/4 inch permitted), 90 Elbows (1-3/8 inch not permitted), 45 Elbows (1/4 inch 45 Elbows not available)

Copper Flare Fittings

Fittings conforming to <<SAE J513>>

Description:  A 45-degree flare flared body and nut for use with annealed copper tubing. Materials are SAE CA360 (half-hard), CA345, CA350 or CA377 (forged) brass with CA377 nuts.  Fittings may have a combination of <<ASME B1.1>> UNF (5/16 to 7/8 inch) or UNS 1 1/16 inch and <<ASME B1.20.1>> NPT tapered threads (1/8 through 3/4 inch). Fittings are available based on outside tube diameter.

Location: ​<< Above grade; or  Below grade>>​

Size: 3/16 though 3/4 inch tube outside diameter, to match pipe size

Temperature Range: -65 degrees to +250 degrees F

Pressure Rating: 550 psig

Manufacturer: << Parker; or  _______>>

Copper Braze Fittings (up to 430 psi design pressure)

Fittings conforming to <<ASME B16.50>>, <<ASME B16.18>>, or <<ASME B16.22>>.

Location:  << Above grade; or  Below grade>>

Manufacturer: Muller/Streamline ACR

Copper Braze Fittings (above 430 psi design pressure)

Fittings conforming to <<ASME B16.50>>, <<ASME B16.18>>, or <<ASME B16.22>>.

Location: ​​<< Above grade; or  Below grade>>​​

Manufacturer:  Muller/Streamline XHP

      - ***************************************************************************************

      - Specify required refrigeration specialty components such as filter-dryers, solenoid valves, expansion valves, moisture and liquid indicators, strainers, pressure regulators, etc., to suit project.  Items must meet the ASME B31.5 requirements for components.

      - All components in Article Refrigeration Piping Components are either standard piping components (listed items) per ASME B31.5 para. 526 or have previously LANL-approved unlisted component evaluations in accordance with ASME B31.5 para. 504.7.

      - The types of components shown may be a non-exhaustive list. Any substitutions or additions shall be ASME B31.5 compliant. All previously LANL approved ASME B31.5 components are available in LANL ESM Chapter 17 - Pressure Safety.

      - ***************************************************************************************

REFRIGERATION PIPING COMPONENTS

Solenoid Valve

Description: Brass valve, Pilot operator, MKC-2 coil kit, synthetic to metal main port, stainless steel pin to synthetic seal pilot port, stainless steel stem and plunger assembly, piston disc.

Manufacturer: Sporlan

Model Number: E series HP

End Connections: Braze ends

Pressure rating: 700 psig

Size: 3/8 inch through 1-1/8 inch

Ball Valve

Description: Forged Brass Body; Polished Brass or Carbon Steel Ball

Manufacturer: Superior Refrigeration Products

Model Number: << WA;  WAS;  WBS; or  MST>>

End Connections: Braze ends

Temperature Range: -40 degrees to 325 degrees F

Pressure Rating: 800 psig

Size: 1/4 inch through 4-1/8 inch

Moisture and Liquid Indicator, Sight Glass

Manufacturer: Parker-Sporlan

Model Number: See-All

Temperature Range: -50 degrees to 149 degrees F

Pressure Rating: 650 psig

Size: 1/4 inch through 2-1/8 inch

Thermostatic Expansion Valve

Description: Machined brass bar body, brass port machined into body, stainless steel pin and pushrod, maximum external leakage – 0.10 oz/yr at 300 psig.

Manufacturer: Parker-Sporlan

Model/End Connections: Type << R, SAE J513 ends;  ER, braze ends; or  SR, braze ends>>.

Pressure Rating: 450 psig

Size: << ______ inlet, _______ outlet>>​

Metal Hose - Vibration Elimination, by size and material; Bronze hose and braids, female copper tube ends.

Manufacturer: << Universal Hose & Braid; or  Parker>>

Model Number: << _______>>

End Connections: Inside conforms to <<ASME B16.18>> and <<ASME B16.22>>.

Pressure Rating: 450 psig minimum

Size: 1/8 inch through 1-1/4 inch.

PART 3 - EXECUTION

PREPARATION

Square, ream pipe and tube ends. Remove burrs.

      - ***************************************************************************************

      - Consult manufacturer’s recommendation for the use of acids and cleaning agents to prevent damage.

      - Ensure safeguards are taken to protect personnel from hazards of cleaning, which may include but not be limited to flying particulates, corrosive chemicals, and harmful vapors.

      - A suitable chemical and/or mechanical cleaning method shall be used, if necessary, to clean all surfaces to be fabricated.

      - ***************************************************************************************

Cleaning:

Remove scale and dirt on inside and outside before assembly.

Cleaning will consist of removing all non-adhering material such as loose scale, sand, weld spatter particles, rust, cutting chips, grinding residue, etc. from the inside of the piping assembly by suitable means. This level of cleaning will allow the presence of mill scale and surface rust.

        - ******************************************************************************

        - Specify any special cleaning requirement below.

        - ******************************************************************************

​<< ______>>​​

Prepare piping connections to equipment with unions.

Fastener materials shall be free of nicks, burrs, chips, dirt, and damage (inspect threads, shank, and nuts). All damaged fasteners must be replaced.

INSTALLATION

General

Install piping in conformance with <<ASME B31.5>>.

No pipe or tube bends are allowed.  Fittings are to be used instead of bends.

Piping systems include all piping components (including pressure retaining portions of instruments), pipe fixtures, clamps, and supports, instrument mounting plates and their attachment to structural framework.

Unless noted otherwise on the isometric drawing, field fit-up welds shall include 6 inches of pipe beyond the length required.

Label piping system in accordance with Section ​<< 22 0554 - Identification for Plumbing,  HVAC, and Fire Piping and Equipment>>​.

Insulate piping system in accordance with Section << 22 0713 - Plumbing and HVAC Insulation>>. Provide clearance for installation of insulation and access to valves and fittings.

Support piping system in accordance with Section << 22 0529 - Hangers and Supports for Plumbing Piping and Equipment>>​.  Do not anchor the pipe.  Allow piping to slide and expand or contract with temperature.

        - ******************************************************************************

        - The following subparagraph is a designer choice based on project-specific conditions.

        - ******************************************************************************

Sleeve and caulk pipes penetrating exterior walls or interior bearing walls. Provide waterproof installation for exterior walls.  Provide UL/FM approved through-penetration firestop system when penetrating fire rated barriers (e.g., walls, floors, etc.). See Section << 07 8400 - Firestopping>>.

Route piping in orderly manner and maintain gradient. Route parallel and perpendicular to walls.

For multiple openings in piping mains, the distance between their centers shall be at least the sum of their inside diameters.

Branch connections shall utilize fittings (tee, lateral, or cross) in accordance with listed codes.

Install piping to maintain headroom and neither interfere with use of space nor take more space than necessary.

Group piping whenever practical at common elevations.

Install piping to allow for expansion and contraction without stressing pipe, joints, or connected equipment.

All valves shall be installed in accordance with the manufacturer's instructions and with sufficient clearance and access for ease of operation and maintenance. Install valves with stems upright or horizontal, not inverted.

Arrange refrigerant piping to return oil to compressor. Provide traps and loops in piping, and provide double risers as required. Slope horizontal piping 1/2 inch per 10 feet, and in direction of flow.

Install pressure gauges vertically.

Keep open ends of pipe free from scale and dirt. Whenever work is suspended during construction, protect open ends with temporary plugs, caps, or residue-free tape.

Install flexible connections where shown on drawings.

      - ***************************************************************************************

      - The following paragraphs are designer choices based on project-specific conditions.

      - ***************************************************************************************

Welding, brazed, or soldered joints

Welded, brazed, or soldered joining of piping/tubing and components shall be per Section << 01 4631 - Welding, Brazing, and Soldering of Pressure Systems>>​.

When brazing/welding or soldering piping/tubing to a valve, follow manufacturer’s instructions to prevent heat damage to valve internals.

45 Degree Flare (<<SAE J513>>) joints

Cut tubing squarely and clean tube end thoroughly to remove burrs.

Place nut onto tube. Place threaded end of nut toward end of tube.

Flare tube end with flaring tool to provide 45 degree flare.

No scratches, breaks, or other mars at sealing surface of flare shall be permitted.

Clamp tube flare between nut and nose of fitting body by screwing nut on finger-tight.  Tighten with a wrench an additional 1/4 turn for a metal-to-metal seal.

Flame-Free Press Fitting joints

Assemble per manufacturer’s installation instructions. www.parker.com, Catalog K-3 or successor document.

EXAMINATION, INSPECTION AND TESTING

      - ***************************************************************************************

      - Retain the following two paragraphs when welded, brazed, or soldered joints are specified by the Designer.

      - ***************************************************************************************

All welding, brazing and soldering: Inspected, examined, and tested in accordance with Section ​​<< 01 4631 - Welding, Brazing, and Soldering of Pressure Systems>>​​​​<< and Section 01 4525 - Non-Destructive Examination (NDE) Requirements; or  None - N/A>>​​.

Externally the pressure system will be free of weld slag, flux, and weld spatter.

Examination activities to verify the quality of the work must be performed by personnel other than those who performed the activity being examined. Such persons must not report directly to the immediate supervisors responsible for work being examined.

The fabrication documentation must have evidence of the examination, the evidence must be maintained in the pressure system documentation package submitted to the pressure safety officer.

Contact LANL Owner’s Inspector to determine the initial inspection points (minimum hold points).

LANL Owner’s Inspector shall have access to any and all design, fabrication, manufacture, heat treatment, assembly, erection, examination, testing, records, documentation and other project information or activities to verify that all required examinations and testing have been completed and to inspect the piping to the extent necessary to be satisfied that it conforms to all applicable examination requirements of the Code and of the engineering design and to perform the role defined in <<ASME B31.5>>.

LANL Owner’s Inspector is the final authority on acceptance of the project examination or test.

Pressure test and leak test piping per Section ​<< 22 0813 - Testing Piping Systems>>​​.

Prior to the pressure test, a preliminary test up to 25 psig using dry nitrogen gas may be applied as a means of locating major leaks per <<ASME B31.5>> para. 538.4.2(b).

        - ******************************************************************************

        - Standardized ASME B31.5 Minimum Design Pressures, Pressure Test Pressures, and Leak Test Pressures for the six most common refrigerants used at LANL provided in the subparagraph below. Designer shall retain the table row(s) applicable to the project.

        - NOTE: It is acceptable to test the low side of the refrigeration system at the high side test pressure if all low side components are rated for the high side design pressure.

        - ******************************************************************************

Pressure test and leak test the refrigerant piping at the following pressures:

If testing of the low side and the high side are done at different pressures, provide positive isolation of the two sides using factory installed isolation valves and/or service valves that are provided as part of the equipment.

| Refrigerant | Minimum Design Pressure (psig) | Pressure Test (psig) | Leak Test (psig) |
| --- | --- | --- | --- |

Hidden Paragraph

| R-410A | High Side 430 Low Side 235 | High Side 475 Low Side 260 | High Side 450 Low Side 250 |
| --- | --- | --- | --- |

Hidden Paragraph

| R-407C | High Side 307 Low Side 166 | High Side 340 Low Side 185 | High Side 325 Low Side 175 |
| --- | --- | --- | --- |

Hidden Paragraph

| R-134A | High Side 177 Low Side 87 | High Side 200 Low Side 100 | High Side 180 Low Side 90 |
| --- | --- | --- | --- |

Hidden Paragraph

| R-404A | High Side 320 Low Side 235 | High Side 355 Low Side 260 | High Side 330 Low Side 240 |
| --- | --- | --- | --- |

Hidden Paragraph

| R-454B | High Side 405 Low Side 220 | High Side 450 Low Side 250 | High Side 420 Low Side 240 |
| --- | --- | --- | --- |

Hidden Paragraph

| R-32 | High Side 435 Low Side 250 | High Side 480 Low Side 280 | High Side 450 Low Side 260 |
| --- | --- | --- | --- |

Hidden Paragraph

| ​<< _______>>​ | High Side ​<< _______>>​ Low Side ​<< _______>>​ | High Side ​<< _______>>​ Low Side ​<< _______>>​ | High Side ​<< _______>>​ Low Side ​<< _______>>​ |
| --- | --- | --- | --- |

Pressure test per <<ASME B31.5>> para. 538.4.2 with dry nitrogen gas for a minimum of ​<< 10;  _______; or  None - N/A>>​ minutes. Test the high and low side of each system at not less than the pressures noted below. Record test with a calibrated pressure gauge. Do not exceed 117% of the test pressures listed above.

Do not use oxygen, acetylene, or other flammable/combustible gases or gas mixtures for leak testing.

After the pressure test is complete, perform a system leak test at the pressures listed above, per <<ASME B31.5>>, para. 538.4.3 Leak Test, with personnel qualifications as defined by <<ASME B31.5>>, para. 536.3 Examination Personnel Qualification and Certification.

        - ******************************************************************************

        - The application of the ASHRAE 15-2022 paragraph 9.13.6.1 Leak Testing Protocol provides the same or greater level of leak detection as the ASME B31.5 paragraph 538.4.3 Leak Test. Any of the three methods shown below for leak testing may be used to satisfy the leak testing requirement.

        - ******************************************************************************

Bubble leak testing per <<ASME B31.5>>, para. 538.4.3

Pressure testing per <<ASHRAE 15>>, para. 9.13.6.1

Vacuum testing per <<ASHRAE 15>>, para. 9.13.6.1

After successful completion of pressure and leak tests, remove pressurization gas and evacuate system to ​<< value req'd by manf.; or  500>>​ microns to remove moisture and non-condensables. After this level is reached, isolate from the vacuum pump and verify that there is no appreciable rise (rise above 1000 microns) after 30 minutes.

Fully charge completed system with refrigerant after testing. If startup is not within 24 hours, temporarily pressurize to 5 psig with system refrigerant.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 23 2300, REV. 7, DATED APRIL 15, 2026.