Section 23 3225 
Bag-In Bag-Out Housings

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 4 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Mechanical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable Sections from all Divisions, especially Division 1, General Requirements.

      - This Section serves as a template. The Section was prepared by an organization operating under a quality assurance program that meets the requirements of DOE O 414.1E, and 10 CFR 830 (suitable for ML-1 through ML-4 projects).

      - Implementation of this Section requires modification to the Section to meet project-specific requirements. Responsibility for application of this Section to meet project-specific requirements lies with the organization modifying or implementing the Section. The organization modifying the Section shall apply a graded approach to quality assurance based on the management level designation of the project. When this Section is used with nuclear facilities subject to 10 CFR 830, modification to this Section must be performed by an individual or organization operating under a quality assurance program that meets the requirements of that CFR.

  - *************************************************************************************************************

PART 1 - GENERAL

Section Includes

      - ***************************************************************************************

      - The following paragraphs are designer choices based on project-specific requirements.

      - ***************************************************************************************

Fire Screen.

Prefilter.

Moisture Separator.

HEPA Filter.

Chemical Adsorber.

Filter Train.

Applicability

This Section applies to filter trains to be installed in confinement ventilation systems for containing radioactive and other hazardous particles.

Related requirements

Section << 01 4216 - Definitions>>.

Section ​<< 23 4133.13 - HEPA Filters – ASME AG-1, Section FC>>​.

Section << 23 4133.16 - HEPA Filters - ASME AG-1, Section FK, Special>>.

REFERENCE Standards

10 CFR 830.122 - Nuclear Safety Management, Quality Assurance Criteria.

ASHRAE Std 52.2 - Method of Testing General Ventilation Air-Cleaning Devices for Removal Efficiency by Particle Size.

ASME AG-1 - Code on Nuclear Air and Gas Treatment.

ASME N511 - In-Service Testing of Nuclear Air-Treatment, Heating, Ventilating, and Air-Conditioning Systems.

ASME NQA-1 - Quality Assurance Requirements for Nuclear Facility Applications.

ASTM D1056 - Standard Specification for Flexible Cellular Materials—Sponge or Expanded Rubber.

DOE Order 414.1E - Quality Assurance.

DOE-HDBK-1169 - Nuclear Air Cleaning Handbook.

IEST-RP-CC008.2 - High-Efficiency Gas Phase Adsorber Cells.

UL 900 - Standard for Air Filter Units.

DEFINITIONS

For definitions and acronyms, refer to COE Glossary of Terms.

ACFM: Actual Cubic Feet per Minute.

Access Door:  Part of a filter housing from which the filter is serviced.

ASHRAE:  American Society of Heating Refrigerating and Air-Conditioning Engineers.

ANSI:  American National Standards Institute.

ASME: American Society of Mechanical Engineers.

ASTM:  American Society for Testing and Materials.

AWS: American Welding Society.

C of C or COC: Certificate of Conformance:  A document from a Supplier and/or Manufacturer that identifies the Subcontract or purchase order number and states that the item or service described thereon conforms in all respects with Subcontract/manufacturer requirements, which may include any applicable specifications, drawings, marking requirements, part/model/serial number identification, or codes/standards to which the item is certified.  Where applicable, the COC shall identify the material by part/control number consistent with part number information in Subcontract documents and/or Specifications.  Each COC shall further identify any approved changes, waivers, or deviations to the item requirements and identify any requirements that have not been met, with a corresponding means/recommendation for resolving the nonconformance.  Each COC shall be signed or otherwise authenticated by an authorized person responsible for this function as described in the Supplier’s quality assurance program.

CMTR:  Certified Material Test Report.  A document issued by the original manufacturer of the material that identifies the actual chemical and/or physical properties and any test(s) performed to the applicable nationally recognized standards or as specified by the Subcontract. The CMTR shall be traceable to the material supplied through heat number, batch number, manufacturer's lot numbers, or other method as allowable by manufacturer’s quality assurance program or national recognized standard.  The CMTR shall be signed by the manufacturer's authorized representative as defined by the manufacturer’s quality assurance program or as otherwise authorized.

HEPA: High Efficiency Particulate Air.

LANL: Los Alamos National Laboratory.

NFPA: National Fire Protection Association.

QA: Quality Assurance.

SCFM: Standard Cubic Feet per Minute.

LANL-PERFORMED WORK

LANL is responsible for having installed HEPA filers and chemical adsorbers in-place tested.

action SUBMITTALS

      - ***************************************************************************************

      - The submittals as listed are required for ML-1, ML-2, and ML-3 filter trains.  For ML-4 filter trains, the submittals listed may be edited to include fewer requirements.

      - ***************************************************************************************

Fire Screen

Catalog data indicating materials of construction and mesh size.

Prefilters

Catalog data indicating the filter efficiency and pressure drop at rated capacity.

        - ******************************************************************************

        - As of the date of the last revision of this Section, there are no known prefilters that meet all of the requirements of ASME AG-1, Section FB. Therefore, until this changes, require that the C of C list which parts of ASME AG-1, Section FB are met.

        - ******************************************************************************

Certificate of Conformance (C of C) that the prefilter conforms to <<ASME AG-1>>, Section FB ​​<< (if not completely, note which parts of AG-1 it does meet) ; or  None - N/A>>​​and to the purchase specifications.

Moisture Separator

Drawings giving outline and interface dimensions of the moisture separator.

Installation and maintenance instructions.

Storage and handling instructions.

        - ******************************************************************************

        - As of the date of the last revision of this Section, there are no known moisture separators that meet all of the requirements of ASME AG-1, Section FA. Therefore, until this changes, require that the C of C list which parts of ASME AG-1, Section FA are met.

        - ******************************************************************************

Certificate of Conformance (C of C that the moisture separator conforms to <<ASME AG-1>>, Section FA << (if not completely, note which parts of AG-1 it does meet) ; or  None - N/A>>​and to the purchase specifications.

Chemical Adsorbers

Table or drawing giving outline dimensions of the cell.

Certified Material Test Reports (CMTRs) of materials used in construction (or Certificate of Conformance (C of C) with requester and QA approval if CMTR(s) are not available).

Adsorbent type with applicable test reports.

Welding procedures and procedure qualifications.

All qualification reports (seismic and filling method).

Certification of performance (resistance and leak test).

Residence time.

Certification of the appropriate flow rate.

Filter Train

Do not fabricate products or begin work that requires approval of submittal documents before such submittals are approved.

        - ******************************************************************************

        - Submittal of QA plan is not necessary if filter housing manufacturer is on the current LANL Institutional Evaluated Suppliers List (IESL) (internal IQPA web site).

        - ******************************************************************************

Copy of the filter train manufacturer’s QA plan identifying procurement, fabrication, test & inspection, material traceability and non-conformity control for approval.

Product Data.

Catalog or manufacturer’s data for filter trains.  Include design features, configurations, total ACFM flow capacity, component dimensions, weight, furnished accessories, standard materials, construction details, and service requirements.

Materials/parts list

        - ******************************************************************************

        - Include the ASME AG-1 Section DA requirements if filter train includes isolation dampers.

        - ******************************************************************************

Certification of Conformance (C of C) that unit meets the applicable <<ASME AG-1>>, Section HA << and DA; or  None - N/A>> requirements. The C of C shall also state that the filter train as designed and delivered by the manufacturer meets the intent of <<DOE-HDBK-1169>> guidance and specifically meets the applicable requirements for in-service testing as specified in <<ASME N511>>.

Manufacturer’s Instructions.

Manufacturer’s installation and assembly instructions showing the field installation of parts and components.

Written instructions providing details on proper operation and maintenance.

Shop drawings

Shop drawings indicating component dimensions, ends, cross sections, clearances for maintenance, construction details and material used.

Test report of pressure decay leak test for the entire housing and each sub assembly, per this Section.

Test report of structural capability test per this Section.

Test report for the airflow distribution qualification test per this Section..

Test report for the air-aerosol mixing uniformity test per this Section.

Test report for sampling manifold qualification test per this Section.

Warranty.

Provide copy of manufacturers warranty documentation.

QUALITY ASSURANCE

Manufacture, inspect, test, and ship filter trains under a quality assurance program, which has been evaluated and approved by LANL and meets the applicable requirements of <<10 CFR 830.122>>, <<DOE Order 414.1E>>, and <<ASME NQA-1>>-2008 with 2009 addenda.

Subcontractors and suppliers providing filter trains shall

Have manufactured at least (50) bag-in bag-out housings of similar type and size specified.

Have five years or more experience in the manufacture of bag-in bag-out housings.

Have records of manufacturing facility, testing facility, assembly, and quality control procedures available for LANL inspection.

Implement and maintain a QA program meeting <<ASME NQA-1>>.

Provide filter trains with performance conforming to related <<ASME AG-1>> and requirements of this Section.

PACKAGING AND SHIPPING

      - ***************************************************************************************

      - Retain the following paragraphs based on product selected for project.

      - ***************************************************************************************

Package and ship filter trains in accordance with <<ASME AG-1>>​, Article HA-7000

Package and ship chemical adsorbers in accordance with <<ASME AG-1>>, Article FH-7000.

Package and ship prefilters and fire screens in accordance with <<ASME AG-1>>, Article FB-7000.

Package and ship moisture separators in accordance with <<ASME AG-1>>, Article FA-7000.

WARRANTY

The manufacturer warrants all products sold to be free from defects in material and workmanship for a period of one year minimum, or as negotiated within the contract, (beginning with the date of acceptance). LANL will provide notification to the manufacturer’s representative of any defective product and provide the manufacturer with a reasonable opportunity to inspect the goods. LANL and its Subcontractors shall not return defective products without written shipping instructions and authorization from the manufacturer.

PART 2 - PRODUCTS

DESIGN AND PERFORMANCE REQUIREMENTS

Filter trains function as enclosures to house filters and adsorbers.  They shall provide a means to bag-in new and bag-out used filters and adsorbers.

      - ***************************************************************************************

      - The following PART 2 Articles are designer choices based on project-specific requirements.

      - ***************************************************************************************

Fire Screen

Metal meshes from 8 to 16 openings per inch.

Frame size nominal 24 in. x 24 in. x 2 in., no gasket, all metal filter with stainless steel frame and screen media, initial pressure drop not to exceed 0.06 in. w.c. at 1000 scfm.

Manufacturer:  Camfil, Type S4S4.  Filter shall not be oiled.

Prefilter

      - ***************************************************************************************

      - As of the date of this Master Spec there are no known prefilters that meet all of the requirements of ASME AG-1, Section FB. Until there are, it is suggested to retain the "Provide prefilters with glass fiber media..." paragraph below.

      - ***************************************************************************************

Provide prefilters in accordance with <<ASME AG-1>>, Section FB.

Provide prefilters with glass fiber media with a bonded backing to support the media. Media shall be continuously sealed to frame with an adhesive to prevent bypass and ensure integrity up to a differential pressure of 10 in. w.c. Frame shall be of corrosion-resistant galvanized steel.

Frame size nominal 24 in. x 24 in. x 6 in., no gasket, <<UL 900>> listed, MERV 11 per <<ASHRAE Std 52.2>>, initial pressure drop not to exceed 0.20 in. w.c. at 1000 scfm.

Manufacturer: Camfil, RIGA-FLO M11.

Moisture Separator

      - ***************************************************************************************

      - As of the date of this Master Spec there are no known moisture separators that meet all of the requirements of ASME AG-1, Section FA. Until there are, it is suggested to retain the “Provide moisture separators specifically designed...” paragraph below.

      - ***************************************************************************************

Provide moisture separators in accordance with <<ASME AG-1>>, Section FA.

Provide moisture separators specifically designed for the removal of airborne moisture droplets. The moisture separator shall be constructed of layers of flat and serpentine metal screen media housed in a 16 gauge (min.) metal frame. The frame shall have a minimum of three 0.375 in. holes on the bottom for liquid drainage. When installed vertically, the moisture separator shall be 98% efficient on 20 micron size droplets when operating at a velocity of 500 fpm face velocity. Resistance to airflow shall not exceed 0.25 in. w.c. at 500 fpm.

Frame size Nominal 24 in. x 24 in. x 4 in.

Manufacturer:  Camfil, ECO Moisture Separator, Stainless Steel construction.

HEPA Filter

      - ***************************************************************************************

      - The following paragraphs are designer choices.

      - ***************************************************************************************

See Section ​<< 23 4133.13 - HEPA Filters – ASME AG-1, Section FC>>​.

See Section << 23 4133.16 - HEPA Filters - ASME AG-1, Section FK, Special>>.

Chemical Adsorber

      - ***************************************************************************************

      - The following is a sample specification of a chemical adsorber to adsorb organic radioiodides.  Several types of adsorbent material are available.  The “N” in the model numbers below is for nuclear grade Carbon which would normally be used.  Consult with OSH-ISH and the user for specific criteria.  Note that the adsorbers manufactured by Camfil use a 16 gage frame and therefore do not meet ASME AG-1, Section FH requirements.  However, these adsorbers would be acceptable for an ML-4 application.

      - ***************************************************************************************

Provide chemical adsorber in accordance with <<ASME AG-1>>​, Section FH.

Type IV (V-Bed) adsorber with 2 in. thick bed of 8 x 16 mesh activated carbon made from Coconut shell. Minimum residence time of 0.125 seconds at a flow of 1250 acfm. Construct adsorber frame of 14 gage Type 304 stainless steel with 26 gage Type 304 stainless steel perforated screens. Provide adsorber frame with 1/4 in. thick x 3/4 in. wide closed cell neoprene gasket on the upstream flange. Adsorber shall have a minimum mechanical efficiency of 99.9% when tested in accordance with <<IEST-RP-CC008.2>> . Adsorber nominal dimensions are 24 in. x 24 in. x 18 in.

Manufacturers:

AAF | Flanders, Model No. AG-GG18-62-NS (gasket seal).

AAF | Flanders, Model No. AF-GG18-62-NS (gel fluid seal).

Camfil, Model No. CF-G-242418-62-NS (gasket seal) (Can only be used for ML-4 applications)

FILTER TRAIN

Manufacturers

        - ******************************************************************************

        - The following subparagraphs are designer choices.

        - ******************************************************************************

AAF | Flanders ​<< BG;  BF;  G; or  GRF>>​ Series Containment Housings.

Camfil ​<< GB;  FB; or  FB-R>>​ Containment Housings.

AAF International Bag In/Bag Out Housing.

Filter Train Assembly Arrangement

        - ******************************************************************************

        - The maximum height of a housing is 3 tiers high and the maximum width is 3 filters wide per access door.

        - Specify doors on both sides when there are more than 3 filters wide in a bank.

        - Use the subparagraph below for straight-through airflow rectangular filter housings containing one or more filters per stage. Consult LANL Fire Marshal's office for fire protection requirements.

        - ******************************************************************************

Provide a << _______>> high x << _______>> wide filter train assembly with side access doors on << the left side;  the right side; or  both sides>> looking in direction of air flow, transitions on both ends, and with housings assembled in direction of air flow as follows; << bubble tight isolation damper;  section for 2 in. fire screen;  section for 6 in. prefilter;  automatic water deluge fire spray head section with moisture separator downstream of spray heads;  test section;  manual water deluge fire spray head section;  section for 12 in. HEPA filter;  test section;  section for 18 in. chemical adsorber;  test section;  section for 18 in. chemical adsorber;  test section;  section for 12 in. HEPA filter;  test section; and  bubble tight isolation damper>>. The filter train assembly shall be built up of factory leak tested subsection housings that are no larger than 1 high x 3 wide. Join housing sections together << vertically;  in parallel; or  in series>> to make up a filter train. Weld joints airtight and conform to standard welding procedures.

        - ******************************************************************************

        - Edit the subparagraph below to suit job requirements. Use the subparagraph below for a single HEPA filter or chemical adsorber in a round filter housing. Will need to include a drawing showing the arrangement described and any additional details.

        - ******************************************************************************

Arrangement: Provide << _______>> in. diameter inlet and outlet on the circumference of the housing. The inlet centerline shall be located on the << back; or  side>> of the housing at << _______>> in. up from the bottom of the housing. The outlet centerline shall be << _______>> degrees clockwise (as viewed from the top of the housing) from the inlet and be << _______>> in. up from the bottom of the housing. The face of the inlet and outlet << flanges; or  _______>> shall be at << _______>>​ in. from the centerline of the housing. The access door shall be located on the top of the housing. A mounting ring shall be located on the bottom of the housing. See Attachment A for additional details.

Filter train for ​<< fire screens;  prefilters;  moisture separators;  HEPA filters; and  adsorbers>>​.

        - ******************************************************************************

        - Specify Type 316/316L stainless steel for highly corrosive air streams.

        - Consult with the manufacturer if a higher system pressure (greater than ± 10 in. w.g.) is required since additional bracing may be necessary.

        - Edit operation pressure to suit.  The plenum must be tested at the maximum pressure it could possibly see during service.  A housing that is normally under a negative pressure but could see a positive pressure during an upset condition, e.g., fan failure, must be tested for both a positive and a negative pressure of the expected magnitude.  As a minimum, use a test pressure of ±10 in. w.g.

        - ******************************************************************************

Construction: Construct housing from << Type 304/304L; or  Type 316/316L>> stainless steel with a 2B mill finish. Provide housing with 100 percent seam-welds in accordance with <<ASME AG-1>>, Article HA-6140 on joints across the pressure boundaries and reinforce to withstand up to << 10 in.; or  _______>> w.g. << positive; and  negative>> operation pressure. Wire brush and clean welds to remove discoloration and weld splatter. Joints and seams which are part of the filter sealing surface << and knife edge; or  None - N/A>>, flange connections and bag-out rings shall be ground smooth and free of burrs and sharp edges. Factory weld housing sections, transitions, << base; or  mounting ring>>, lifting lugs, and weather cap to form one unit. Provide Type 300 series stainless steel miscellaneous mechanical components. Manufacture housings in accordance with <<ASME AG-1>>, Section HA.

Access Doors: Provide removable, separate, access doors for each tier of filters specified in the paragraph heading above. Use silicone or neoprene gaskets that seal the door to the housing wall while maintaining clearance between the bag-out flange and the inside door surface. Door gasket shall be a molded gasket fitted to the door. Use door gasket material of  grade SCE-45 or 30-40 Shore-A durometer. Provide stainless steel door latches that pivot away after release and remain attached to the housing or door. Use Type 300-Series stainless steel bolts with captive hand knobs made from aluminum. Metal pockets for instruction manuals are optional.

Smooth Inlet Design: Provide a smooth inlet design around the upstream perimeter of each filter position to limit the buildup of contaminants in crevices or filter frames. Inlet transitions provided as part of the filter train shall be designed to direct the airflow into the filter medium.

        - ******************************************************************************

        - Gasket sealed filter housings should be used for most applications. Fluid sealed filter housings are normally only specified for outdoor installations where the housing will experience varying solar loading which can cause the housing to warp slightly. The fluid seal seems to provide a better seal for these conditions. Fluid seal type filter housings are also not recommended for housings more than one filter wide due to the fluid sometimes sticking to the knife edge and being difficult to remove while working through a bag. Round filter housings can only use fluid seal type filters due to their design constraints.

        - Sealing force is based on eighty-percent compression, which requires a loading of approximately 20 pounds per square inch of gasket area.

        - ******************************************************************************

Gasket Seal Filter Housing: The filter housing shall have a flat sealing surface that mates with the gasket face of each HEPA filter << and chemical adsorber; or  None - N/A>>. Prior to leaving the factory, each sealing surface shall be checked with a flatness gage to insure proper mating with the filter. Each tier of filters shall be provided with a removable filter clamping mechanism on the downstream side of the HEPA filter << and chemical adsorber; or  None - N/A>>​​​ that is operated from outside the housing. The filter clamping mechanism shall include independent pressure bars for each filter. Each pressure bar shall have pre-loaded springs that exert a minimum sealing force of 1400 lbs. per 24 in. by 24 in. filter (per guidance in <<DOE-HDBK-1169>>, Section 4.4.6) applied as an even, uniform load along at least 80% of the top and bottom of each filter frame. The ends of each pressure bar shall be chamfered to prevent holdup of filters being installed or removed. All mechanical components of the filter clamping mechanism shall be Type 300-Series stainless steel except for the pivot blocks which can be made from brass. (This type of sealing mechanism is not suitable for round filter housings.)

Fluid Seal Filter Housing: The filter housing shall have a knife edge that mates into the fluid seal channel of the face of each HEPA filter ​<< and chemical adsorber; or  None - N/A>>​. Prior to leaving the factory, each knife edge shall be checked with an alignment gage to insure proper alignment with each filter. Each tier of filters shall be provided with a removable filter locking mechanism on the downstream side of the HEPA filter ​<< and chemical adsorber; or  None - N/A>>​ that is operated through the change-out bag by a locking handle. The filter locking mechanism shall be designed such that the access door cannot be installed unless the filters are correctly seated in the housing. The mechanism shall exert equal force at the top and bottom edge of the filter when engaging or disengaging the filter from the knife edge and provide a total clamping load sufficient to resist displacement of the filter under normal operating filter resistance and the pressure produced by shock loadings in the system (per guidance in <<DOE-HDBK-1169>>, Section 4.4.6). All mechanical components of the filter locking mechanism shall be Type 300-Series stainless steel.

Filter Rails: Provide filter rails in the fire screen, prefilter, and moisture separator housings, 2 1/8 in. wide for the fire screen, 6 in. wide for the prefilter, and 4 in. wide for the moisture separator.

Filter Removal Rod: Provide housings with two or more filters per access door with a replaceable removal rod to draw the filters to the change-out position.  The removal rods shall be operated from inside the change-out bag.

        - ******************************************************************************

        - One bag per access door is the minimum number of bags needed to put the housing into service.

        - ******************************************************************************

Bag In/Out: Provide each filter access door with a bag-out port inside the access door which is hemmed on its outer edges to prevent tearing of the bag. Provide two continuous ribs on the outside of the port to hold the bag’s elastic shock cord and the safety strap during the bag-out operation. The turned edge on the port is not considered a rib. Provide each housing with << one;  two; or  _______>>, 8 mil, transparent PVC change-out bags for each bag-out port. Three glove sleeves shall be built into the bag to facilitate handling of the filter during change-out. Provide bag with stock number rolled into the hem for easy identification when reordering. Provide bag with a smooth finish to prevent from sticking to itself. The elastic shock cord shall be hemmed into the mouth of the bag so that it fits securely when stretched around the bagging ring. Provide a nylon safety strap with each bag-out port to prevent the bag from slipping off during the bag-out procedure. Provide a cinching strap with each bag-out port to tie off the slack in the bag while the exhaust system is operating. Provide a banding kit to facilitate in the secure clamping off of the bag between the housing and the spent filter.

Filter Removal Tray: Provide one filter removal tray for each size of HEPA filter << and chemical adsorber; or  None - N/A>> to aid in the change-out operation.

Test Sections

Construct test section in such a manner that adjoining test chambers are isolated from each other to permit individual testing of each HEPA filter << and chemical adsorber; or  None - N/A>>​.

Provide test section with separate aerosol mixing devices, sample ports, and injection ports to allow individual in-place testing of the HEPA filters << and chemical adsorber; or  None - N/A>> per <<ASME N511>>. Test sections shall be designed and qualified to the applicable parts of <<ASME AG-1>>, Sections HA and TA. Upstream sampling sections, and downstream sampling sections that require the use of external power, e.g., compressed air, are not acceptable. The pressure drop through each test section during testing and normal operation is not to exceed 0.5 in. w.g. at 1000 scfm per filter. Identify each test section with a model number and label all test equipment such as operational handles, injection and sample ports.

Airflow distribution qualification tests shall be performed in the shop prior to shipment in accordance with <<ASME AG-1>>, Article TA-4600 to provide assurance that manufacturer’s design provides uniform air distribution. Shop tests shall simulate actual field entrance and exit duct connections as closely as possible. Acceptance criteria shall be in accordance with TA-4600. Filter trains which are duplicates in design, layout, and fabrication to other units which have been successfully tested and documented, need not be shop tested for airflow distribution. Results of airflow distribution tests shall be documented and submitted to the owner.

Air-aerosol mixing uniformity tests shall be performed in the shop for each manifold which is provided by the manufacturer to be mounted within the filter housing in accordance with <<ASME AG-1>>, Article TA-4600. Acceptance criteria shall be in accordance with TA-4600. Sampling manifolds shall be qualified in accordance with <<ASME AG-1>>​, Article HA-5800 including Nonmandatory Appendix HA-D. Filter trains and test manifolds which are duplicates in design, layout, and fabrication to other air-cleaning units which have been successfully tested and documented need not be shop tested for air-aerosol mixing uniformity. Results of the tests shall be documented and submitted to the owner.

Structural Capability Test

        - ******************************************************************************

        - Edit design pressure below to suit.  The plenum must be tested at the maximum pressure it could possibly see during service.  A housing that is normally under a negative pressure but could see a positive pressure during an upset condition, e.g., fan failure, must be tested for both a positive and a negative pressure of the expected magnitude.  As a minimum, use a test pressure of ±10 in. w.g.

        - ******************************************************************************

Perform factory Structural Capability Test per <<ASME AG-1>>, Article HA-5500 at a static pressure of << plus 10 in. w.g.;  minus 10 in. w.g.;  plus and minus 10 in. w.g.; or  _______>>. This test can be combined with the Pressure Decay Leak Test if both tests are to be performed at the same static pressure.

Pressure Decay Leak Test

        - ******************************************************************************

        - Edit design pressure below to suit.  The plenum must be tested at the maximum pressure it could possibly see during service.  A housing that is normally under a negative pressure but could see a positive pressure during an upset condition, e.g., fan failure, must be tested for both a positive and a negative pressure of the expected magnitude.  As a minimum, use a test pressure of ±10 in. w.g.

        - The 0.2 percent of housing volume per hour requirement is a very low leakage requirement that had been listed as guidance in ERDA 76-21, Table 4.5 for an all-welded man-entry steel housing.  This requirement is not included as guidance in DOE-HDBK-1169-2003, Chapter 4.  Consult with Rad Engineering group on what value to use on a case-by-case basis.

        - ******************************************************************************

Factory leak test each subsection housing and the completed filter train assembly by the pressure decay method to << plus 10 in. w.g.;  minus 10 in. w.g.;  plus and minus 10 in. w.g.; or  ______>> in accordance with <<ASME AG-1>>, Mandatory Appendix TA-III. Leak test to acceptance criteria of a maximum of << 0.2 percent of housing volume per hour; or  0.0005 scfm per cubic foot of housing volume>> at << design pressure; or  ______>> (. Rectify and retest any deficiency and work affected by such deficiency. Submit certifications of leak test.

Miscellaneous

        - ******************************************************************************

        - Do not include "with a cap" if differential pressure gages are included.

        - ******************************************************************************

Static Pressure Ports: Locate static-pressure ports on the front or top of the housing upstream and downstream of each filter bank. Provide each tier of a filter bank with a port. Provide 1/4 in. NPT type 304 stainless steel ports​​​<< with a cap; or  None - N/A>>​​​.

        - ******************************************************************************

        - Specify gage ranges per LANL Mechanical Standard Detail ST-D3040-5.  Minimum resolution for all gages is 0.1 in. w.g.  These gages have a plastic face which is damaged by prolonged exposure to UV light.

        - ******************************************************************************

Differential Pressure Gages: Provide Magnehelic® analog differential pressure gages connected to the static pressure ports using 300 series stainless steel fittings and tubing that allow each gage to be zeroed and to be connected to a handheld calibrated gage (see LANL Mechanical Standard Detail ST-D3040-5). Provide valves to allow the differential pressure of each tier of a filter bank to be monitored separately and combined. Mount gages on the housing so that they are easily readable from the working side of the housing. Label each gage indicating which filter bank it is connected to. For outdoor installations, mount gages in a metal cabinet that has a latching hinged cover.

        - ******************************************************************************

        - 6 inches is the minimum base height.  Higher bases can be specified.  Consult with the design team structural engineer for the specific project requirements for the base channel.

        - Designer shall select only one of the two mounting options below.

        - ******************************************************************************

Base: Provide a << 6 in.; or  _______>>-high stainless steel channel base on four sides welded to the unit and with predrilled mounting holes. (Use for straight through airflow rectangular filter housings.)

Housing Mounting Ring: Provide a 3/16 in. thick mounting ring welded to the bottom of the housing. See Attachment A for additional details on dimensions and bolt hole locations. (Use for round filter housings. Alternate mounting types are also acceptable.)

        - ******************************************************************************

        - The following subparagraph is a designer choice.

        - ******************************************************************************

Drains: Provide drains on the bottom of housings where the build-up of water in the housing is a possibility. Drain size and location is to be determined on a case-by-case basis.  Fire protection water discharge into plenums will usually be the driver for drain sizing.  Need to provide sufficient information so that the housing manufacturer understands the specific requirements for the project.  In general the drains need to be sized to keep water from rising more than 10 in. in height.  The drains and discharge piping must be located such that they do not interfere with in-place testing and filter change-out activities.

Lifting Lugs: Provide lifting lugs made from the same type of stainless steel as the housing, with a 2 in. diameter lifting eye.  Design lugs and attachment point to prevent pull out or distortion of both the lug and the securing member.

Custom-Engraved Plates: Include plates with the housing model number, and the original order number with minimum 1/8 in. letter height.  Fabricate custom-engraved plates from polished stainless steel and be permanently welded to the operating side of the housing at or near eye level.

        - ******************************************************************************

        - Consult with the design team structural engineer for the specific project requirements that will govern the seismic criteria to be used.

        - ******************************************************************************

Seismic Qualification: << _______>>.

Provide a 1/8” NPT vent port with a replaceable plug for each void space located between tiers to allow the air pressure in the void space to equalize with ambient air pressure during shipping. (Los Alamos is at an elevation of 7500 Ft with an average air pressure of 11.1 PSIA. Failure to vent the void spaces in the past has caused deformation of filter housing sheet metal in filter trains fabricated at lower elevations.)

        - ******************************************************************************

        - The subparagraph below is not applicable for round filter housings.

        - ******************************************************************************

Weather/Housekeeping Cap: Provide a continuously welded weather cap to the top of each filter housing that is sloped to prevent accumulation of liquids.

        - ******************************************************************************

        - Specify 36 in. (min.) long transitions for 3 high x 3 wide assemblies and 24 in. (min.) long transition for assemblies less than 3 high x 3 wide.

        - Edit I.D. to suit when upstream or downstream duct sizes are different or if rectangular duct is used.

        - Consult with the manufacturer if a higher system pressure (greater than ± 10 in. w.g.) is required since additional bracing may be necessary.

        - ******************************************************************************

Transition to Ductwork: Provide << 24 inch;  36 inch; or  _______>>​​ long inlet and outlet transitions welded or bolted to the housing with a minimum 1 1/2 in. x 1 1/2 in. x 3/16 in.  x << _______>> I.D. angle ring flange with predrilled mounting holes and shipped with gaskets. If the transition is bolted, the spacing shall be the manufacturer’s standard bolt-hole pattern, not to exceed 4 in. between bolt holes on center. Transition to be capable of withstanding up to << plus 10 in. w.g.;  minus 10 in. w.g.;  plus and minus 10 in. w.g.; or  ______>> pressure. Provide gasket materials of closed cell neoprene, 1/4 in. thick, <<ASTM D1056>>  Grades 2C3 or 2C4, or 30-40 Shore-A durometer. (Use for straight through air flow rectangular filter housings.)

        - ******************************************************************************

        - Describe inlet and outlet connects for round filter housings below. The connections must meet the applicable requirements of ASME AG-1, Sections HA and/or SA.

        - ******************************************************************************

Inlet and Outlet Connections: << _______>>.

PART 3 - EXECUTION

EXAMINATION

Field Conditions: Examine areas and conditions under which air filters and filter housings will be installed.  Do not proceed with work until unsatisfactory conditions have been corrected in manner acceptable to Installer.

INSTALLATION

Filter Train: Install per manufacturer’s instructions and structural design requirements.

Install 1/8 inch NPT plug in vent port located on void space between tiers on filter trains more than one tier high.

Cleaning: Vacuum clean inside of filter train. Wipe down exterior of filter train to remove construction grit.

Filters: Install in accordance with manufacturer’s instructions and recognized industry practices.

Fan Operation: Do not operate fan system until filters are in place.  Replace temporary filters used during construction.

END OF << MAIN; or  None - N/A>> SECTION<< ; ATTACHMENT FOLLOWS; or  None - N/A>>

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 23 3225, REV. 4, DATED APRIL 15, 2026.

    - **********************************************************************************************

      - Provide a drawing as needed to show the specific configuration of the round housing to clarify inlet and outlet locations and any other port locations.

    - **********************************************************************************************

    - Attachment A – Round Filter Housing Reference Drawings