Section 23 3300 
Air Duct Accessories

  - ************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 4 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Mechanical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects and commercial applications. For industrial and confinement ventilation applications, SMACNA-Round and Rectangular Industrial Duct Construction Standards should be used to edit this specification. For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

  - ************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

      - ***************************************************************************************

      - The following paragraphs are designer choices based on project-specific requirements.

      - ***************************************************************************************

Backdraft​​​​<< and barometric relief; or  None - N/A>>​​​​​ dampers.

Thermally insulated dampers for outside air applications.

Manual volume (balancing) dampers.

Control dampers.

Industrial control dampers.

Fire dampers.

Smoke dampers.

Combination fire/smoke dampers.

Ceiling radiation dampers.

Duct-mounted access doors.

Elbow turning vanes.

Duct test holes.

RELATED REQUIREMENTS

Section << 01 4444 - Offsite Welding, Brazing and Joining Requirements>>.

Section << 01 4455 - Onsite Welding, Brazing and Joining Requirements>>.

Section << 01 8113.13 - Sustainable Design>>.

Section ​<< 22 0554 - Identification for Plumbing,  HVAC, and Fire Piping and Equipment>>​.

    - **********************************************************************************************

      - The codes/standards listed below are provided for reference only and are not listed within the body of this section. It is a user-choice to include these codes/standards.

      - <<NFPA 101>>

    - **********************************************************************************************

REFERENCE STANDARDS

AMCA 500-D - Laboratory Methods of Testing Dampers for Rating.

AMCA 511 - Certified Ratings Program Product Rating Manual for Air Control Devices.

ASHRAE 62.1 - Ventilation and Acceptable Indoor Air Quality.

ASTM A480/A480M - Standard Specification for General Requirements for Flat-Rolled Stainless and Heat-Resisting Steel Plate, Sheet, and Strip.

ASTM A653/A653M - Standard Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process.

ASTM B209/B209M - Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate.

ASTM B221 - Standard Specification for Aluminum and Aluminum-Alloy Extruded Bars, Rods, Wire, Profiles, and Tubes.

AWS D9.1/D9.1M - Sheet Metal Welding Code.

NFPA 90A - Standard for the Installation of Air-Conditioning and Ventilating Systems.

NFPA 90B - Standard for the Installation of Warm Air Heating and Air-Conditioning Systems.

NFPA 92 - Standard for Smoke Control Systems.

NFPA 96 - Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations.

NFPA 101 - Life Safety Code.

SMACNA (DCS) - HVAC Duct Construction Standards Metal and Flexible.

SMACNA (RECTANGULAR) - Rectangular Industrial Duct Construction Standards.

SMACNA (ROUND) - Round Industrial Duct Construction Standards.

UL 33 - Safety Heat Responsive Links for Fire-Protection Service.

UL 555 - Standard for Fire Dampers.

UL 555C - Standard for Safety Ceiling Dampers.

UL 555S - Standard for Smoke Dampers.

ACTION SUBMITTALS

Product data including materials, dimensions, weights, loads, and required clearances; and method of field assembly into duct systems and applicable electrical characteristics and wiring diagrams. Submit the following as applicable:

Leakage, pressure drop, maximum operating << pressure; or  velocity>>, and maximum back pressure data.

UL ratings, dynamic ratings, and fire/smoke rating data.

Damper pressure drop ratings based on tests and procedures performed in accordance with <<AMCA 500-D>>.

Shop drawings for shop fabricated assemblies of << dampers;  duct access doors; and  duct test holes>>:  Include dimensions, weights, loads, and required clearances; fire and smoke damper installation including sleeves, and method of field assembly into duct systems and other construction.

Damper Schedule:  Include<< as applicable; or  None - N/A>> damper identification number, damper type, damper size, damper orientation, airflow, pressure rating, leakage rating, fire rating, smoke rating, actuator type, manufacturer, and model number.

      - ***************************************************************************************

      - The following is a designer choice.

      - ***************************************************************************************

Certification showing conformance with the applicable standards for duct accessories materials, brazing materials, mill-rolled reinforcing and supporting materials, welding procedures, shop test procedures and reports.

Per the requirements of Section(s) << 01 4444 - Offsite Welding, Brazing and Joining Requirements; and  01 4455 - Onsite Welding, Brazing and Joining Requirements>>, submit:

          - **********************************************************************

          - When offsite only, do not select submittals below regarding onsite welding. For high-risk applications such as ML-1 or ML-2, add submittals for “Weld Filler Material Control Procedures” and “Filler Material Certified Material Test Reports (CMTRs)” when required. Add “Post-Weld Heat Treatment Procedures” when required.

          - **********************************************************************

Welding Procedure Specification (WPS) and supporting Procedure Qualification Record (PQR). (NOTE: For onsite welding use of LANL WPS/PQR is the default; coordinate usage with the LANL CWI; no submittal required)

Welder Performance Qualification Records (WPQR) including continuity [NOTE: For onsite, welders are tested by LANL who will produce WPQR and track continuity; this includes brazing, bonding and fusing; no submittal required)

Inspector qualification records

Inspection procedures

Weld inspection report(s) and weld map(s)

      - ***************************************************************************************

      - Some submittals only apply to projects subject to LANL ESM Chapter 14 - Sustainable Design (e.g., total estimated cost greater than or equal to $50 million), LEED, and other projects having sustainability goals. Retain the paragraph below and make the choices specified as applicable.

      - ***************************************************************************************

Sustainable Design (SD) Submittal: Per Section << 01 8113.13 - Sustainable Design>>, (1) Guiding Principles: Requirements for energy efficiency;<< (2) when LEED:  Product Data for Prerequisite EQ 1:  Documentation indicating that units comply with ASHRAE 62.1 , Section 5 - "Systems and Equipment."; or  None - N/A>> .

informational submittals

Manufacturer's Installation Instructions:  Submit for fire and combination smoke and fire dampers.

At Closeout: Operations and Maintenance Data:

For air duct accessories (to include in operations and maintenance manuals).

DELIVERY, STORAGE, AND HANDLING

Delivery:  Deliver materials to site in manufacturer's original, unopened containers and packaging, with labels clearly indicating manufacturer and material.

Storage:  Store materials in a dry area indoor, protected from damage.

Handling:  Handle and lift dampers in accordance with manufacturer's instructions. Protect materials and finishes during handling and installation to prevent damage.

Protect dampers from damage to operating linkages and blades.

QUALITY ASSURANCE

Construct duct accessories in accordance with <<SMACNA (DCS)>>, <<UL 555>>, <<UL 555S>>, <<NFPA 90A>>, <<NFPA 90B>>, and <<NFPA 92>>.

      - ***************************************************************************************

      - Retain the paragraph below only if specifying for air with contamination or chemicals (e.g. laboratory exhaust).

      - ***************************************************************************************

Construct duct accessories in accordance with ​​<< SMACNA (RECTANGULAR); and  SMACNA (ROUND)>>​​, <<NFPA 90A>>, <<NFPA 90B>>, and <<NFPA 92>>.

Qualify welding processes and welding operators in accordance with <<AWS D9.1/D9.1M>>.

Dampers tested, rated and labeled in accordance with the latest UL requirements, and pressure drop ratings based on tests and procedures performed in accordance with <<AMCA 500-D>>

PART 2 - PRODUCTS

MATERIALS

Comply with <<SMACNA (DCS)>> for acceptable materials, material thicknesses, and duct construction methods unless otherwise indicated. Sheet metal materials shall be free of pitting, seam marks, roller marks, stains, discolorations, and other imperfections.

Galvanized Sheet Steel: Comply with <<ASTM A653/A653M>>.

Galvanized Coating Designation: G90 Zinc coating.

Exposed-Surface Finish:  Mill phosphatized.

Aluminum Sheets: Comply with <<ASTM B209/B209M>>, alloy 3003, temper H14; with mill finish for concealed ducts and standard 1-side bright finish for exposed ducts.

Extruded Aluminum: Comply with <<ASTM B221>>, alloy 6063, temper << T5; or  T6>>.

Stainless-Steel Sheets: Comply with <<ASTM A480/A480M>>, Type 304, and having a No. 2D finish.

Reinforcement Shapes and Plates: Galvanized-steel reinforcement where installed on galvanized sheet metal ducts; compatible materials for aluminum and stainless-steel ducts.

Tie Rods: Galvanized steel, 1/4-inch minimum diameter for lengths 36 inches or less; 3/8-inch minimum diameter for lengths longer than 36 inches.

      - ***************************************************************************************

      - The following PART 2 Articles are designer choices based on project-specific requirements.

      - ***************************************************************************************

Backdraft​​​​​<< and barometric relief; or  None - N/A>>​​​​​ DAMPERS

Damper Frame: Channel frame with welded corners and mounting flanges, minimum 16 gage << galvanized steel; or  extruded aluminum>>.

Blades and Blade Seals: Parallel blades, minimum 18 gage << galvanized steel; or  extruded aluminum>>, maximum 6 inch width gravity-balanced parallel multi-blades, << center pivoted, ; or  None - N/A>>with felt or flexible vinyl seals mechanically attached to blade edge. Blades linked together in rattle-free manner with 90-degree stop, steel ball bearings, and plated steel pivot pin.

Blade Axle: Long-life, corrosion-resistant, synthetic, locked to blade and formed as single-piece with bearings.

Bearings: Long-life, corrosion-resistant bearings, steel ball or synthetic pivot bushing, and formed as single piece with axles.

Counterbalance: Adjustable zinc-plated steel weights mechanically attached to blade enabling damper to operate over wide range of differential static pressure.

Mounting: << Vertical;  Horizontal, air flow up; or  Horizontal, air flow down>>.

Duct Connection: << Round; or  Rectangular>>.

THERMALLY INSULATED DAMPER for outside air applications

Damper Frame: Extruded aluminum (6063-T5) not be less than 0.080” (2.03 mm) in thickness. Damper frame shall be 4” (101.6 mm) deep x 1" (25.4 mm), with duct mounting flanges on both sides of frame. Frame to be assembled using zinc-plated steel mounting fasteners. Welded frames are not acceptable.

Dampers shall be Flanged-to-Duct install type only.

Entire frame shall be thermally broken by means of polyurethane resin pockets complete with thermal cuts.

Frame seals shall be extruded silicone, secured in an integral slot within the aluminum frame extrusions and shall be mechanically fastened to prevent shrinkage and movement over the life of the damper. Metallic compression type jamb seals are not acceptable.

Damper Blades: Maximum 6" (152.4 mm) deep extruded aluminum (6063-T5) air-foil profiles with a minimum wall thickness of 0.06” (1.52mm). Blades shall be internally insulated with expanded polyurethane foam and shall be thermally broken. Complete blade shall have an insulating factor of R-2.29. All blades shall be symmetrically pivoted.

Dampers shall be opposed blade action or parallel blade action, as indicated on the plans.

Blade seals shall be extruded silicone, secured in an integral slot within the aluminum blade extrusions and shall be mechanically fastened to prevent shrinkage and movement over the life of the damper. Adhesive or clip-on type blade seals are not acceptable.

Bearings: Dual bearing system composed of a Celcon inner bearing (fixed around a 7/16" (11.11 mm) aluminum hexagon blade pivot pin), rotating within a polycarbonate outer bearing inserted in the frame. Single axle bearing, rotating in an extruded or punched hole are not acceptable. Bearings are to be maintenance-free, requiring no lubrication.

Control Shaft: Hexagonal shaft shall be 7/16" (11.11 mm). It shall have an adjustable length and shall be an integral part of the blade axle. A field-applied control shaft shall not be acceptable. All parts shall be zinc-plated steel.

Linkage: Linkage hardware shall be aluminum and corrosion-resistant zinc-plated steel, installed in the frame side, out of the airstream, and accessible after installation. Linkage hardware shall be complete with cup-point trunnion screws to prevent linkage slippage and a Celcon bearing between moving parts to reduce wear and increase longevity. Linkage that consists of metal rubbing metal is not acceptable.

Dampers shall be designed for operation in temperatures ranging from -40°F (-40°C) to 212°F (100°C).

Certifications: Dampers shall be AMCA rated for Leakage Class 1A at 1-inch w.g. (0.25 kPa) static pressure differential. Standard air leakage data to be certified under <<AMCA 511>>.

Dampers shall be custom made to required size, with blade stops not exceeding 1-1/4” (31.7 mm) in height. The blade stop shall be a continuous and integral part of the head/sill. Welded and caulked blade stops shall not be acceptable.

Manufacturer: TAMCO Series 9000 BF Thermally Insulated Damper with Thermally Broken Frame.

manual Volume (balancing) dampers

Manufacturer: Ruskin Model << CD60; or  CDR25>>.

Damper Frame: Minimum 16 gage << galvanized; or  stainless>> steel with flanges for attaching to walls and flangeless frames for installing in ducts.

Blades: << Round, Single; or  Multiple, Opposed>> blade design. Minimum 16 gage << galvanized; or  stainless>> steel, maximum 8 inch width for multi-blade dampers. If required, stiffen damper blades for stability.

Blade Axle:  Minimum 1/2-inch plated steel rod mechanically attached to blade.

Bearings

​​​<< Molded synthetic;  Oil-impregnated bronze;  Oil-impregnated Nylon;  Teflon; or  Self-lubricating stainless steel sleeve>>​​​.

Dampers in ducts with pressure classes of 3-inch wg or less shall have axles full length of damper blades and bearings at both ends of operating shaft.

Actuators: Provide locking, indicating quadrant regulators on single and multi-blade dampers. On insulated ducts mount quadrant regulators on standoff mounting brackets, bases, or adapters.

Mounting: << Vertical;  Horizontal, air flow up; or  Horizontal, air flow down>>.

Duct Connection: << Round; or  Rectangular>>.

Control dampers

      - ***************************************************************************************

      - Refer to Section << 25 5000 - Integrated Automated Facility Controls>> for additional information on Automatic (Control) Dampers and Damper Actuators.

      - ***************************************************************************************

Manufacturer: Ruskin Model << CD60; or  CDR25>>.

Damper Frame: Minimum 16 gage << galvanized; or  stainless>> steel channels with mitered and welded corners

Blades: Minimum 16 gage << galvanized; or  stainless>> steel, << round, single;  multiple;  parallel; or  opposed>> blade design, maximum 8-inch width for multi-blade dampers with the linkages located out of the air stream.

Blade Seals: Closed-cell neoprene edging.

Blade Axles: Minimum 1/2-inch diameter; << galvanized steel; or  stainless steel>>, blade-linkage hardware of zinc-plated steel and brass; ends sealed against blade bearings.

Bearings

​​<< Molded synthetic;  Oil-impregnated nylon;  Oil-impregnated sintered bronze; or  Self-lubricating stainless steel sleeve>>​​.

Dampers in ducts with pressure classes of 3-inch w.g. or less shall have axles full length of damper blades with bearings at both ends of operating shaft and thrust bearings at each end of every blade.

Operator: ​<< Electric ; or  ___>>​​<< two-position; or  modulating action>>​. Coordinate with Controls Contractor.

Mounting: << Vertical;  Horizontal, air flow up; or  Horizontal, air flow down>>.

Duct Connection: << Round; or  Rectangular>>.

Multiple section assemblies shall be coupled together with a jackshaft.

Leakage Class 1A, per ANSI/<<AMCA 500-D>>.

      - ***************************************************************************************

      - The following is a designer choice.

      - ***************************************************************************************

End of shaft marking on drive shaft to indicate damper position.

Industrial Control dampers

      - ***************************************************************************************

      - Refer to Section << 25 5000 - Integrated Automated Facility Controls>> for additional information on Automatic (Control) Dampers and Damper Actuators.

      - ***************************************************************************************

Manufacturer: Ruskin Model << CD80AF1; or  CDR82>>.

Damper Frame: Minimum << 14; or  10>> gage << galvanized; or  stainless>> steel channels with mitered and welded corners

Blades: Minimum << 16; or  10>> gage << galvanized; or  stainless>> steel, << multiple;  round, single;  double skin airfoil;  parallel; or  opposed>> blade design, maximum 8-inch width for multi-blade dampers with the linkages located out of the air stream.

Blade Seals: << EPDM;  Silicone;  Stainless Steel;  Stainless Steel jamb seals;  Ultra-low leakage; or  Closed-cell neoprene edging>>. Adhesive type seals are not acceptable. Wind stops or sponge seals are not acceptable.

Blade Axles: Minimum 1/2-inch diameter; << galvanized steel; or  stainless steel>>​, blade-linkage hardware of zinc-plated steel and stainless steel; ends sealed against blade bearings. << Axle shall be continuous, extending through entire diameter of damper and beyond damper bearing a minimum of 6 inches.; or  None - N/A>>

Bearings

​<< Stainless steel sleeve pressed into frame;  Stainless steel sleeve in cast HSG bolted to frame;  Bearings bolted to frame with shaft seal; and  Outboard bearings with shaft seal>>​.

Oil impregnated bronze or synthetic bearings are not acceptable.

Operator: ​<< Locking hand quadrant; or  Crank lever for motor operation>>​. Coordinate with Controls Contractor.

Mounting: << Vertical;  Horizontal, air flow up; or  Horizontal, air flow down>>​.<< Damper to be installed with horizontal blade orientation.; or  None - N/A>>

Duct Connection: << Rectangular; or  Round>>.

Damper leakage shall not exceed ​<< 35; or  _______>>​ total CFM with blade seals or ​<< 175; or  _______>>​ total CFM with full circumference blade stop based on 48" diameter unit at 1" W.G.

      - ***************************************************************************************

      - The following is a designer choice.

      - ***************************************************************************************

End of shaft marking on drive shaft to indicate damper position.

Fire dampers

Damper Type: << Static; or  Dynamic>> Curtain Type

Fire Rating: <<UL 555>> classified and labeled as a ​<< 1-1/2-hour; and  3-hour>>​ fire damper

      - ***************************************************************************************

      - The following is a designer choice.

      - ***************************************************************************************

Dynamic Closure Rating: Dampers classified for dynamic closure to 4-inch w.g. static pressure and minimum 2000-fpm velocity.

Air-Flow Rating: UL-approved for dual-directional air flow.

Fire Damper Configuration: << Rectangular connection, B style - blades out of air stream; and  round connection, LR style - blades out of air stream>>.

Blades: 20 gage galvanized steel curtain type interlocking blades, << in; or  out of>>​ airstream. Gravity closure upon fusible link release for vertical mount. Spring closure upon fusible link release for horizontal mount.

Frame: Blade frame fabricated with roll-formed, 20 gage galvanized steel; with mitered and interlocking corners.

Fusible Link Release:  Heat responsive links in accordance with <<UL 33>>, replaceable << 165°F; or  ___ °F>> rated fusible link, or resettable << 165°F; or  ___ °F>> electro-thermal link, 24-volt power.

Mounting Sleeve:  Factory or field installed, minimum 14 gage galvanized sheet steel, and of length to suit application.

Blade Orientation (Mounting):  Horizontal or vertical<< as indicated on Drawings; or  None - N/A>>.

Smoke dampers

      - ***************************************************************************************

      - International Building Code requires minimum smoke damper leakage rating of Class II and elevated temperature rating of not less than 250°F.

      - ***************************************************************************************

Smoke Rating: Leakage Class I or Class II smoke damper in accordance with <<UL 555S>>.

Damper Temperature Rating:  << 250°F; or  350°F>>.

Frame: Minimum 16 gage galvanized steel roll-formed, galvanized steel hat-shaped channel, reinforced at corners.

Blades: 16 gage galvanized steel multiple blade type, airfoil-shaped, single piece, double skin, maximum 6 inch width.

Blade Seals: Inflatable silicone material to maintain smoke leakage rating to a minimum of 450°F mechanically attached to blade edge.

Jamb Seals: Stainless steel, flexible metal compression type.

Linkage: Concealed in frame.

Axles: Minimum 1/2-inch diameter plated steel, hex-shaped, mechanically attached to blade.

Bearings: Self-lubricating stainless steel sleeve, turning in extruded hole in frame.

Sleeve: Factory installed 18 gage galvanized steel sleeve, minimum 12 inches long, or length to suit wall or floor application.

Actuator

Type: << Electric; or  Pneumatic>>, << two-position; or  modulating>> action.

Mounting:  << External; or  Internal>>.

combination fire/Smoke dampers

      - ***************************************************************************************

      - International Building Code requires minimum fire/smoke damper leakage rating of Class II and elevated temperature rating of not less than 250°F.

      - ***************************************************************************************

The fire/smoke dampers shall be of the addressable type and be compatible with the building fire alarm system.<<  Coordinate with Building Fire Alarm Systems Subcontractor.; or  None - N/A>>

Fire Resistance Rating: << 1½-hour; and  3-hour>> fire damper in accordance with <<UL 555>>.

Smoke Rating: Leakage Class I or Class II smoke damper in accordance with <<UL 555S>>.

Damper Temperature Rating: << 250°F; or  350°F>>.

Dynamic Closure Rating: Dampers classified for dynamic closure to 4-inch wg static pressure and minimum 2000-fpm velocity.

Frame: Roll-formed, minimum 16 gage galvanized steel hat-shaped channel, reinforced at corners or U-channel type frame.

Blades: Multiple blade, minimum 16 gage galvanized steel, airfoil-shaped, single piece, double skin, maximum 6 inch blade width. Linkage concealed in frame.

Seals: Material to maintain smoke leakage rating to a minimum of 450°F mechanically attached to blade edge.

Blade Edge: Blade seals shall be extruded silicone rubber permanently bonded to the appropriate blade edges.

Jamb Seals: Flexible stainless steel compression type.

Axles: Minimum 1/2-inch diameter plated steel, hex-shaped, mechanically attached to blade.

Axle Bearings: Self-lubricating stainless steel sleeve, turning in extruded hole in frame.

Fusible Link Release Temperature: ​<< Replaceable 165°F rated fusible link; or  Resettable 165°F electro-thermal link, 24 volt power>>​​.

Mounting Sleeve: Factory or field installed, minimum 14 gage galvanized sheet steel, and of length to suit application.

Release Device: << Close in controlled manner and lock damper through actuator closure spring; or  Close in controlled manner and allow damper to be automatically reset>>.

Actuator

Type: ​<< Electric 120 volt, 60 hertz, two-position;  Electric ______ volt, 60 hertz, two-position; or  Pneumatic, minimum 20 psi control pressure, two-position>>​.

Mounting: ​<< External; or  Internal>>​.

        - ******************************************************************************

        - The following is a designer choice.

        - ******************************************************************************

End switch indications for remote position indication, manual override, and test panel.

CEILING RADIATION DAMPERS

Label in accordance with <<UL 555C>> by a Nationally Recognized Testing Laboratory.

Comply with construction details for tested floor- and roof-ceiling assemblies as indicated in UL's "Fire Resistance Directory". See design drawings for detail.

Frame: Galvanized sheet steel, round or rectangular, style to suit ceiling construction; gage in accordance with UL listing.

Blades: Galvanized sheet steel with refractory insulation; gage in accordance with UL listing.

Heat-Responsive Device: Replaceable, << 165 deg F;  212 deg F; or  _______>> rated, fusible links.

Fire Rating: << 1; or  _______>> hour(s).

Duct-mounted access doors

Fabricate in accordance with <<SMACNA (DCS)>>, Figure 7-2, "Duct Access Doors and Panels" and Figure 7-3, "Access Doors - Round Duct” << and as indicated on drawings; or  None - N/A>>. Fabricate doors airtight and suitable for duct pressure class.

Frame:  Minimum 22 gage galvanized sheet steel, with bend-over installation tabs and foam gaskets.

Door:  Double wall, galvanized sheet steel and thickness as indicated for duct pressure class, with sealing gaskets and quick fastening locking devices.

Hinges and Latches: 1” x 1” butt or continuous piano hinge and cam latches.

Insulation: For insulated ductwork, furnish with minimum 1 inch thick fiberglass insulation.

Number of Hinges and Locks

Less than 12 inches Square: Secure with sash locks.

Up to 18 inches Square: Furnish two hinges and two sash locks.

Up to 24 x 48 inches: Three hinges and two compression latches << with outside and inside handles; or  None - N/A>>.

Larger Sizes: Four hinges and two compression latches with outside and inside handles.

Access panels with sheet metal screw fasteners are not acceptable.

Elbow Turning vanes

Fabricate in accordance with <<SMACNA (DCS)>>, Figure 4-3, "Vanes and Vane Runners" and Figure 4-4, "Vane Support in Elbows”.

Vane Construction: << Single; or  Double>> wall.

Manufactured Turning Vanes: Curved blades of galvanized sheet steel; support with bars perpendicular to blades set; set into vane runners suitable for duct mounting.

Acoustic Turning Vanes: Fabricate airfoil-shaped aluminum extrusions with perforated faces and fibrous-glass fill.

Duct test holes

Permanent Test Holes: Factory fabricated, airtight flanged fittings to suit duct material with screw cap and gasket. Size to allow insertion of pitot tube and other testing instruments and of length to suit duct-insulation thickness, if provided.

PART 3 - EXECUTION

EXAMINATION

Verify ducts and equipment installations are ready for accessories.

Verify rated walls are ready for fire damper installation.

Verify duct access door location prior to fabrication.

INSTALLATION

Install duct accessories in accordance with <<NFPA 90A>> and <<NFPA 92>>, and in accordance with manufacturer’s installation instructions at the locations shown on the drawings.

        - ******************************************************************************

        - The following two subparagraphs are designer choices.

        - ******************************************************************************

Follow <<SMACNA (DCS)>> for duct construction and pressure class.

Follow <<SMACNA (RECTANGULAR)>>​ or <<SMACNA (ROUND)>>, as applicable, for laboratory duct construction and pressure class.

Install duct accessories of materials suited to duct materials or as described in Part 2 of this Section

Use galvanized-steel accessories in galvanized-steel and fibrous-glass ducts.

Stainless-steel accessories in stainless-steel ducts.

Aluminum accessories in aluminum ducts.

      - ***************************************************************************************

      - LEED-NC Prerequisite EA 2 requires compliance with ASHRAE 90.1-2019, in which Section 6.4.3.4.2- "Shutoff Damper Controls" restricts the use of backdraft dampers and requires control dampers for certain applications. If applying for LEED certification, select the "control" choice in paragraph below, required by ASHRAE 90.1.

      - ***************************************************************************************

Install ​<< backdraft; or  control>>​ dampers at inlet of exhaust fans or exhaust ducts as close as possible to exhaust fan​<< and where indicated on Drawings; or  None - N/A>>​.

Install volume (balancing) dampers with indicating type locking quadrant where noted on Drawings. Inspect and ensure that the construction of balancing dampers, including the hand quadrant, is of good quality prior to installation.

Dampers are not required upstream or downstream of VAV boxes serving only one diffuser.

Do not use splitter dampers.

Locate balancing dampers as far as possible (recommend no closer than 5 feet) from air terminals to avoid excessive noise.

Set dampers to fully open position before testing, adjusting, and balancing.

Install ​<< fire dampers;  smoke dampers;  ceiling radiation dampers; and  combination fire and smoke dampers>>​ at locations as indicated on Drawings. Install with required perimeter mounting angles, sleeves, breakaway duct connections, corrosion resistant springs, bearings, bushings and hinges.

Install smoke dampers and combination fire/smoke dampers in accordance with <<NFPA 90A>> and <<NFPA 92>>.

Install dampers square and free from racking with blades running horizontally.

Do not compress or stretch damper frame into duct or opening.

Handle damper using sleeve or frame. Do not lift damper using blades, actuator, or jack shaft.

Install bracing for multiple section assemblies to support assembly weight and to hold against system pressure. Install bracing as needed.

      - ***************************************************************************************

      - Refer to NFPA 90A, Annex A, Section A.4.3.4.1 and SMACNA Fire, Smoke and Radiation Dampers Installation guide for HVAC System for fire damper access door sizes, locations, etc.

      - ***************************************************************************************

Install duct access doors for inspection and cleaning upstream of filters, coils, dampers, rectangular elbows with turning vanes, and equipment as indicated on drawings. Access doors shall be accessibly located. Provide minimum 8 X 8 inch size for hand access, 18 X 18 inch size or 18 inch x the duct height/width less 2 inches for shoulder access. Install duct access door at the following locations

Adjacent to and close enough to fire or smoke dampers, to reset or reinstall fusible links. Access doors for access to fire or smoke dampers having fusible links shall be barometric relief access doors and shall be outward operation for access doors installed upstream from dampers and inward operation for access doors installed downstream from dampers.

Upstream of each duct mounted coil.

Upstream of each duct mounted filter.

Upstream of each duct mounted fan.

Upstream of control damper.

Upstream or downstream of duct silencers.

        - ******************************************************************************

        - The following 3 subparagraphs are designer choices.

        - ******************************************************************************

Upstream of volume (balancing) damper.

Downstream of each VAV box.

At locations for cleaning kitchen exhaust ductwork in accordance with <<NFPA 96>>​.

        - ******************************************************************************

        - Include the first three subparagraphs below to provide access for duct cleaning. LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1, in which Section 7.2.4 - "Ventilation System Start-up" requires that distribution systems be clean of dirt and debris.

        - ******************************************************************************

At each change in main duct direction greater than 45 degrees and at maximum spacing of every 50 feet of straight duct.

Upstream<< and downstream; or  None - N/A>> of each elbow with turning vanes.

Control devices requiring inspection.

At locations indicated on Drawings.

Install access doors with swing against duct static pressure.

Label access doors according to Section << 22 0554 - Identification for Plumbing,  HVAC, and Fire Piping and Equipment>> to indicate the purpose of access door. Mark access doors for fire and smoke dampers on outside surface, with minimum 1/2-inch-high letters reading: FIRE DAMPER, or SMOKE DAMPER, or FIRE/SMOKE DAMPER.

      - ***************************************************************************************

      - Include only one of the following two paragraphs.

      - ***************************************************************************************

Install permanent duct test holes or pitot tube openings​<< where indicated on Drawings; or  None - N/A>>​ required for testing and balancing purposes, complete with metal can with spring device or screw to prevent air leakage. Where openings are provided in insulated ductwork, install insulation material inside metal ring.

Install temporary duct test holes<< where indicated on Drawings; or  None - N/A>> required for testing and balancing purposes. Cut or drill in ducts. Cap with neoprene plugs, threaded plugs, or threaded or twist-on metal caps.

FIELD QUALITY CONTROL

Tests and Inspections:

Operate dampers to verify full range of movement.

Inspect locations of access doors and verify that purpose of access door can be performed.

Operate fire, smoke, and combination fire and smoke dampers to verify full range of movement and verify that proper heat-response device is installed.

Inspect turning vanes for proper and secure installation.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 23 3300, REV. 4, DATED APRIL 15, 2026.