Section 23 3400 
HVAC Fans

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 3 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Mechanical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects. For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

      - Seismic: If HVAC fans are not exempt from seismic design per ASCE 7 paragraph 13.1.4 then, prior to attempting to edit this section to be project-specific, refer to Sections << 22 0548.23 - Vibration and Seismic Controls for Mechanical Systems>>, and << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>, as applicable. In order to edit this section for job-/Project-specific seismic requirements, refer to author notes that begin with “Seismic.” Also, see the Seismic Specification Guide for Mechanical Non-Structural Components web-posted with the LANL Master Specifications here for guidance on properly editing this section.

  - *************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

      - ***************************************************************************************

      - The following paragraphs are designer choices based on project-specific requirements.

      - ***************************************************************************************

Centrifugal Fans.

Axial Fans.

Plenum Fans.

Propeller Fans.

Centrifugal Roof Ventilators.

Centrifugal Wall Ventilators.

Gravity Roof Ventilators.

      - ***************************************************************************************

      - The Section listed below is provided for reference only and is not listed within the body of this section. It is a designer-choice to include this Section if necessary.

      - Section ​​​<< 01 8113.13 - Sustainable Design>>​​​

      - ***************************************************************************************

RELATED REQUIREMENTS

Section << 01 2500 - Substitution Procedures>>

Section << 01 8113.13 - Sustainable Design>>

Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>

Section ​<< 03 3001 - Reinforced Concrete>>​

Section ​<< 03 3053 - Miscellaneous Cast-in-Place Concrete>>​

Section << 22 0548.23 - Vibration and Seismic Controls for Mechanical Systems>>​

Section ​<< 22 0554 - Identification for Plumbing,  HVAC, and Fire Piping and Equipment>>​

Section ​<< 23 3101 - HVAC Ducts>>​

      - ***************************************************************************************

      - Ensure conformance to codes and standards as applicable to project and type of fan selected. The reference list needs to be adjusted to project specific needs.

      - ***************************************************************************************

REFERENCE STANDARDS

29 CFR 1910 - Occupational Safety and Health Standards.

ABMA STD 9 - Load Ratings and Fatigue Life for Ball Bearings.

ABMA STD 11 - Load Ratings and Fatigue Life for Roller Bearings.

AMCA 99 - Standards Handbook.

AMCA 204 - Balance Quality and Vibration Levels for Fans.

AMCA 210 - Laboratory Methods of Testing Fans for Certified Aerodynamic Performance Rating.

AMCA 300 - Reverberation Room Methods of Sound Testing of Fans.

AMCA 301 - Methods for Calculating Fan Sound Ratings from Laboratory Test Data.

IEEE 841 - IEEE Standard for Petroleum and Chemical Industry--Premium-Efficiency, Severe-Duty, Totally Enclosed Squirrel Cage Induction Motors from 0.75 kW to 370 kW (1 hp to 500 hp).

NEMA EN 10250 - Enclosures for Electrical Equipment (1000 Volts Maximum).

NFPA 70 - National Electrical Code.

SMACNA - Sheet Metal and Air Conditioning Contractors’ National Association.

UL 705 - Power Ventilators.

ACTION SUBMITTALS

Product Data: For each type of product.

Include rated capacities, furnished specialties, and accessories for each fan.

Certified fan performance curves with system operating conditions indicated.

Certified fan sound-power ratings.

Motor ratings and electrical characteristics, plus motor and electrical accessories.

Material thickness and finishes, including color charts.

Dampers, including housings, linkages, and operators.

Fan speed controllers.

Shop Drawings

Include plans, elevations, sections, and attachment details.

Include details of equipment assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

Include diagrams for power, signal, and control wiring.

        - ******************************************************************************

        - The following is a designer choice.

        - ******************************************************************************

Vibration Isolation Base Details: Detail fabrication, including anchorages and attachments to structure and to supported equipment. Include auxiliary motor slides and rails, and base weights.

INFORMATIONAL SUBMITTALS

Field quality-control reports.

Installation instructions.

At Closeout:

Operation and Maintenance Data: For all fans to include in operation, and maintenance manuals.

Warranty

EXTRA MATERIALS

Furnish two additional sets of belts for each belt driven fan.

QUALITY ASSURANCE

Performance Ratings: Conform to <<AMCA 210>> and bear AMCA Certified Rating Seal.

Sound Ratings: <<AMCA 301>>, tested to <<AMCA 300>>, and bear AMCA Certified Sound Rating Seal.

UL Compliance: UL listed and labeled, designed, manufactured, and tested in accordance with <<UL 705>>.

Balance Quality: Conform to <<AMCA 204>>.

Electrical Components, Devices, and Accessories: Listed and labeled as defined in <<NFPA 70>>, by any nationally recognized testing laboratory (NRTL) recognized under <<29 CFR 1910>>.7.

DELIVERY, STORAGE, AND HANDLING

Protect motors, shafts, and bearings from weather and construction dust.

WARRANTY

The equipment manufacturer shall provide, at no additional cost, a standard parts warranty that covers a period of one year from unit start-up or 18 months from shipment, whichever occurs first.

PART 2 - PRODUCTS

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section ​​<< 01 2500 - Substitution Procedures>>​​.

PERFORMANCE REQUIREMENTS

AMCA Compliance:  Comply with AMCA performance requirements and bear the AMCA-Certified Ratings Seal.

HVAC fans and associated motors shall perform satisfactorily in the following service conditions:

Elevation:  7500 feet above sea level.

Maximum ambient temperature:  104 degrees F.

Minimum ambient temperature:  Minus 20 degrees F.

24-hour average temperature:  Not exceeding 86 degrees F.

        - ******************************************************************************

        - Retain and edit the following subparagraph to match project requirements; use only for outdoor equipment.

        - ******************************************************************************

Maximum solar heat gain:  ​<< 110 W/sq. ft.; or  ______>>​

      - ***************************************************************************************

      - For HVAC fans that are not exempt from seismic, if project specification package includes Section ​​<< 22 0548.23 - Vibration and Seismic Controls for Mechanical Systems>>​​, and if mounting and/or anchorage devices are to be used that differ from those specified in that Section, they must be described herein (in PART 2).

      - Seismic: Do not include paragraph below if units are exempt from seismic design. However, if paragraph applies:

      - Edit the paragraph in accordance with content of the chosen seismic Section.

      - ***************************************************************************************

Seismic Performance Requirements: The unit(s) shall remain in place without separation of any parts when subjected to the design basis earthquake ​​​<< per Section  01 8734 - Seismic Qualification of Nonstructural Components (IBC);  as represented by the seismic forces derived from the criteria indicated on the drawings; or  as represented by the seismic forces derived from the criteria indicated in Section 22 0548.23 - Vibration and Seismic Controls for Mechanical Systems>>​​​.

      - ***************************************************************************************

      - The following PART 2 Articles are designer choices based on project-specific requirements.

      - ***************************************************************************************

CENTRIFUGAL FANS

Manufacturers

Acme Engineering and Manufacturing Corp.

Twin City Fans

Chicago Blower Corporation

Cincinnati Fan

Greenheck Corp.

Howden Buffalo, Inc.

Loren Cook Company

Penn Barry

New York Blower Company

Description: Factory fabricated, assembled, tested, and finished, << belt; or  direct>>-driven centrifugal fans consisting of housing, wheel, fan shaft, bearings, motor, drive assembly, support structure, and factory installed and wired disconnect switch.  Deliver fans as factory-assembled units, to the extent allowable by shipping limitations.

Wheel and Inlet

        - ******************************************************************************

        - Retain only one of the three “Wheel and Inlet” Assemblies subparagraphs below.

        - ******************************************************************************

Forward Curved: << Single-width-single-inlet; or  Double-width-double-inlet>> galvanized steel construction with inlet flange, back plate, shallow blades with inlet and tip curved forward in direction of airflow, mechanically secured to flange and back plate; steel hub swaged to back plate and keyed to shaft with set screw.

        - *** OR ***

Airfoil Wheel: ​<< Single-width-single-inlet; or  Double-width-double-inlet>>​ steel construction with smooth curved inlet flange, back plate die formed hollow airfoil shaped blades continuously welded at tip flange, and back plate; cast iron or cast steel hub riveted to back plate and keyed to shaft with set screws.

        - *** OR ***

Backward Inclined: ​<< Single-width-single-inlet; or  Double-width-double-inlet>>​ steel construction with smooth curved inlet flange, back plate, backward curved blades welded or riveted to flange and back plate; cast iron or cast steel hub riveted to back plate and keyed to shaft with set screws.

Housing

Steel, designed to minimize turbulence with spun inlet bell and shaped cut-off.

Factory finish before assembly to manufacturer's standard.

Bolted construction with horizontal flanged split housing, where required.

Shafts

Hot rolled steel, ground and polished, with keyway, protectively coated with lubricating oil, and shaft guard.

Statically and dynamically balanced and selected for continuous operation at maximum rated fan speed and motor horsepower, with adjustable alignment and belt tensioning.

Designed to operate at no more than 70 percent of first critical speed at top of fan's speed range.

Bearings and Sleeves

Bearings:  Self-aligning, pillow block type, ​<< pre-lubricated and sealed shaft bearings; or  grease-lubricated shaft bearings>>​, ball or roller bearings.

Ball Bearings Rating Life:  <<ABMA STD 9>>, << L-10 life at 50,000 hours; or  L-50 life at 100,000 hours>>.

Roller Bearings Rating Life:  <<ABMA STD 11>>, << L-10 life at 120,000 hours; or  L-50 life at 400,000 hours>>.

Belt Drives

Factory mounted, with adjustable alignment and belt tensioning.

Service Factor Based on Fan Motor Size: << 1.5;  1.4;  1.3; or  1.2>>.

Fan Pulleys: Cast iron or cast steel with split, tapered bushing; dynamically balanced at factory.

Motor Pulleys: Adjustable pitch for use with motors through ​<< 5; or  insert number>>​ hp; fixed pitch for use with larger motors. Select pulley so pitch adjustment is at the middle of adjustment range at fan design conditions.

Belts: Oil resistant, non-sparking, and non-static; matched sets for multiple belt drives.

Belt Guards: Fabricate to comply with OSHA and <<SMACNA>> requirements of diamond-mesh wire screen welded to steel angle frame or equivalent, prime coated. Secure to fan or fan supports without short circuiting vibration isolation. Include provisions for adjustment of belt tension, lubrication, and use of tachometer with guard in place.

Motor Mount: Adjustable for belt tensioning.

      - ***************************************************************************************

      - Select the paragraph below and one or more of its subparagraphs appropriate to equipment accessory requirements.

      - ***************************************************************************************

Accessories

Inlet/Outlet Screens: Galvanized steel welded grid.

Access Doors: Shaped to conform to scroll, with quick opening latches and gaskets.

Scroll Drain: 1/2-inch steel pipe coupling welded to low point of fan scroll.

Spark-Resistant Construction: <<AMCA 99>>.

AXIAL FANS

Manufacturers

Acme Engineering and Manufacturing Corp.

Greenheck Corp.

Hartzell Fan Inc.

Howden Buffalo, Inc.

Loren Cook Company

Penn Barry

Description: ​<< Tubeaxial; or  Vaneaxial>>​ fan wheel and housing, factory-mounted motor with ​<< belt; or  direct>>​ drive, ​<< an inlet cone section,; or  None - N/A>>​ and accessories.

Hub and Impeller

Airfoil Impeller Blades: ​<< Adjustable die cast aluminum alloy; or  Welded steel die formed blades with belt drive>>​.

Hub: << Die cast aluminum alloy;  Cast-iron hub; or  Belt drive of spun, welded steel>>, bored and keyed to shaft; to facilitate indexing of blade angle with << manual; or  automatic>> adjustment stops.

        - ******************************************************************************

        - The following is a designer choice.

        - ******************************************************************************

Controllable Pitch Assemblies: Incorporate permanently lubricated and sealed ball bearing counterbalanced blade and variable pitch assembly into hub with mechanical link to casing exterior mounted actuator, or electric actuator incorporated within hub.

Casing

Continuously welded, with inlet and outlet flange connections, and motor or shaft supports.

Integral flow straightening guide vanes designed to straighten airflow.

Shafts

Hot rolled steel, ground and polished, with keyway, protectively coated with lubricating oil, and shaft guard.

Designed to operate at no more than 70 percent of first critical speed at top of fan's speed range.

Bearings

Bearings: Radial, self-aligning, ball or roller bearings.

Ball Bearings Rating Life: <<ABMA STD 9>>, << L-10 life at 50,000 hours; or  L-50 life at 100,000 hours>>.

Roller Bearings Rating Life: <<ABMA STD 11>>, << L-10 life at 120,000 hours; or  L-50 life at 400,000 hours>>.

Lubrication: For direct driven units, extend lubrication lines to outside of casing and terminate with grease fittings.

Direct Drives

Resiliently mounted << induction;  electrically commutated; or  _______>> motor.

​<< Galvanized Steel; or  Powder Coated>>​ housing for ​<< indoor; or  outdoor>>​ service.

Removable service panels.

Extend lubrication fittings to outside of casing.

Belt Drives

V-Belt Drive: Cast iron or steel sheaves, dynamically balanced, keyed. Variable and adjustable pitch sheaves for motors 15 hp and under selected so required rpm is obtained with sheaves set at mid-position; fixed sheave for 20 hp and over, matched belts, and drive rated as recommended by manufacturer or minimum 1.5 times nameplate rating of motor.

Belt Guard: Fabricate to comply with OSHA and <<SMACNA>>​ Standard requirements. Fabricate of steel for motors mounted on outside of fan cabinet, 0.106 inch thick, 3/4-inch diamond mesh wire screen welded to steel angle frame or equivalent, prime coated. Secure to fan or fan supports without short circuiting vibration isolation, with provision for adjustment of belt tension, lubrication, and use of tachometer with guard in place.

      - ***************************************************************************************

      - Select the paragraph below and one or more of subparagraphs appropriate to equipment accessory requirements.

      - ***************************************************************************************

Accessories

Mounting Clips: << Horizontal ceiling; or  Vertical mounting>> clips welded to fan housing, of same material as housing.

Horizontal Support: Pair of supports bolted to fan housing, of same material as housing.

Inlet Bell: Bell mouth inlet, when fan is not attached to duct, fabricated of same material as casing with flange.

Inlet Screens: Galvanized steel welded grid to fit inlet bell.

Inlet Cone: Round-to-round transition of same material as housing.

Outlet Cones: Round-to-round transition, of same material as casing with flanges.

Access Doors: Shaped to conform to casing with quick opening latches and gaskets.

Motor Cover: Cover with side vents to dissipate motor heat, of same material as housing.

        - ******************************************************************************

        - Retain the following subparagraphs as appropriate.

        - ******************************************************************************

Direct-Driven Units: Encase motor in housing outside of airstream, factory wired to disconnect switch located on outside of fan housing.

Stall Alarm Probe: Factory installed sensing probe to detect fan operation in stall.

Vibration Detector: Factory installed vibration switch to stop fan.

PLENUM FANS

Manufacturers

Acme Engineering and Manufacturing Corp.

Greenheck Corp.

Hartzell Fan Inc.

Howden Buffalo, Inc.

Loren Cook Company

Penn Barry

Description: Factory fabricated, assembled, tested, and finished, belt-driven centrifugal fans consisting of wheel, fan shaft, bearings, motor, drive assembly, and support structure. Deliver fans as factory-assembled units, to the extent allowable by shipping limitations. Factory installed and wired disconnect switch.

Airfoil Wheels

Single-width-single-inlet construction with smooth-curved inlet flange.

Heavy backplate.

Hollow die-formed, airfoil-shaped blades continuously welded at tip flange and backplate.

Cast-iron or cast-steel hub riveted to backplate and fastened to shaft with set screws.

Shafts

Statically and dynamically balanced and selected for continuous operation at maximum-rated fan speed and motor horsepower, with adjustable alignment and belt tensioning.

Turned, ground, and polished hot-rolled steel with keyway. Ship with protective coating of lubricating oil.

Designed to operate at no more than 70 percent of first critical speed at top of fan's speed range.

      - ***************************************************************************************

      - Retain only one of the "Shaft Bearings" paragraphs below.

      - ***************************************************************************************

Pre-lubricated and Sealed Shaft Bearings

Self-aligning, pillow-block-type ball bearings.

Ball-Bearing Rating Life: <<ABMA STD 9>>​, L-10 life at << 50,000;  120,000; or  _______>> hours.

Roller-Bearing Rating Life: <<ABMA STD 11>>, L-10 life at << 50,000;  120,000; or  _______>> hours.

      - *** OR ***

Grease-Lubricated Shaft Bearings

Self-aligning, pillow-block-type, tapered roller bearings with double-locking collars and two-piece, cast-iron housing.

Ball-Bearing Rating Life: <<ABMA STD 9>>, L-10 at << 50,000;  120,000; or  _______>> hours.

Roller-Bearing Rating Life: <<ABMA STD 11>>, L-10 at << 50,000;  120,000; or  _______>> hours.

Belt Drives

Factory mounted, with adjustable alignment and belt tensioning.

Service Factor Based on Fan Motor Size: << 1.5;  1.4;  1.3; or  1.2>>.

Fan Pulleys: Cast iron or cast steel with split, tapered bushing; dynamically balanced at factory.

Motor Pulleys: Adjustable pitch for use with motors through << 5; or  insert number>> hp; fixed pitch for use with larger motors. Select pulley so pitch adjustment is at the middle of adjustment range at fan design conditions.

Belts: Oil resistant, non-sparking, and non-static; matched sets for multiple belt drives.

Belt Guards: Fabricate to comply with OSHA and <<SMACNA>> requirements of diamond-mesh wire screen welded to steel angle frame or equivalent, prime coated. Secure to fan or fan supports without short circuiting vibration isolation. Include provisions for adjustment of belt tension, lubrication, and use of tachometer with guard in place.

Motor Mount: Adjustable for belt tensioning.

Accessories

Shaft Cooler: Metal disk between bearings and fan wheel, designed to dissipate heat from shaft.

Spark-Resistant Construction: <<AMCA 99>>.

Shaft Seals: Airtight seals installed around shaft on drive side of single-width fans.

PROPELLER FANS

Manufacturers

Acme Engineering and Manufacturing Corp.

Greenheck Corp.

Hartzell Fan Inc.

Loren Cook Company

Penn Barry

Construction

Impeller: << Shaped steel; or  Steel reinforced aluminum blade>> with hubs, statically and dynamically balanced, keyed and locked to shaft, << directly connected to motor; or  furnished with V-belt drive, sheaves, and belt guard>>.

Frame:  One-piece, square steel with die formed venturi orifice, mounting flanges and supports, with baked enamel finish.

Fan Drive

Fan Shaft: Turned, ground, and polished steel; keyed to wheel hub.

Shaft Bearings: Permanently lubricated, permanently sealed, self-aligning ball bearings.

Pulleys: Cast iron with split tapered bushing; dynamically balanced at factory.

Motor Pulleys: Adjustable pitch for use with motors through 5 hp; fixed pitch for use with larger motors. Select pulley so pitch adjustment is at the middle of adjustment range at fan design conditions.

Belts: Oil resistant, non-sparking, and non-static; matched sets for multiple belt drives.

Belt Guards: Fabricate of steel for motors mounted on outside of fan cabinet.

      - ***************************************************************************************

      - Select the paragraph below and one or more of subparagraphs appropriate to equipment accessory requirements.

      - ***************************************************************************************

Accessories

Back-draft Damper: Multiple blades with offset hinge pin, blades linked.

Outlet Damper: Multiple blades with offset hinge pin, blades linked, line voltage motor drive, power open, spring return.

Wall Sleeve: Galvanized steel to match fan and accessory size.

Motor-Side Back Guard: Galvanized steel, complying with OSHA specifications, removable for maintenance.

Hood: Weather shield, to exclude rain and snow. Galvanized steel to match fan and accessory size.

Fan speed controller for direct driven fans.

Disconnect Switch: Non-fusible type, with thermal-overload protection mounted inside fan housing, factory wired through an internal aluminum conduit.

CENTRIFUGAL ROOF VENTILATORS

Manufacturers

Acme Engineering and Manufacturing Corp

Twin City Fans

Greenheck Corp

Hartzell Fan Incorporated

Loren Cook Company

Penn Barry

Fan Unit: << Downblast type;  Upblast type;  V-belt; or  Direct>> drive, spun aluminum housing with grease tray; resilient mounted motor; aluminum wire bird screen; square base to suit roof curb with continuous curb gaskets.

Sheaves: For V-belt drives, provide cast iron or steel, dynamically balanced, bored to fit shafts and keyed; variable and adjustable pitch motor sheave selected so required rpm is obtained with sheaves set at mid-position; fan shaft with self-aligning permanently lubricated and sealed ball bearings.

Roof Curb: Manufacturer’s standard shop fabricated units modified if necessary to comply with requirements. 18 inch high, self-flashing of galvanized steel construction with continuously welded seams, and factory installed nailer strip.

Disconnect Switch: Factory wired, non-fusible, in housing for thermal overload protected motor <<NEMA EN 10250>><< Type 1;  Type 3R; or  Type 4>> enclosure.

Accessories

        - ******************************************************************************

        - Retain only one of the two following subparagraphs.

        - ******************************************************************************

Backdraft Damper: Gravity actuated, aluminum multiple blade construction, felt edged with offset hinge pin, nylon bearings, blades linked, spring return.

        - *** OR ***

Motor Operated Damper: Aluminum multiple blade construction, felt edged with offset hinge pin, nylon bearings, blades linked, motor drive, power open or closed.

Fan speed controller for direct driven fans.

Bird Screens:  Removable, 1/2-inch mesh, aluminum or brass wire.

CENTRIFUGAL WALL VENTILATORS

Manufacturers

Acme Engineering and Manufacturing Corp.

Aerovent; a Division of Twin City Fan Companies, Ltd.

Greenheck Corp.

Hartzell Fan Incorporated

Loren Cook Company

Penn Barry.

Fan Unit: << V-belt; or  Direct>> drive with spun aluminum housing; resilient mounted motor; aluminum wire bird screen.

Sheaves: For V-belt drives, provide cast iron or steel, dynamically balanced, bored to fit shafts and keyed; variable and adjustable pitch motor sheaves selected so required rpm is obtained with sheaves set at mid-position; fan shaft with self-aligning permanently lubricated and sealed ball bearings.

Disconnect Switch: Factory wired, non-fusible, in housing for thermal overload protected motor <<NEMA EN 10250>><< Type 1;  Type 3R; or  Type 4>> enclosure.

Accessories

        - ******************************************************************************

        - Retain only one of the two following subparagraphs.

        - ******************************************************************************

Backdraft Damper: Gravity actuated, aluminum multiple blade construction, felt edged with offset hinge pin, nylon bearings, blades linked, spring return.

        - *** OR ***

Motor Operated Damper: Aluminum multiple blade construction, felt edged with offset hinge pin, nylon bearings, blades linked, motor drive, power open or closed.

Fan speed controller for direct driven fans.

Wall Grille:  Ring type for flush mounting.

GRAVITY ROOF VENTILATORS

Manufacturers

Acme Engineering and Manufacturing Corp.

Greenheck Corp.

Loren Cook Company

Penn Barry

Product Description: << Square; or  Round>> type, with aluminum constructed housing; aluminum wire bird screen; square base to suit roof curb with continuous curb gaskets.

Roof Curb: Manufacturer’s standard shop fabricated units modified if necessary to comply with requirements. 18 inch high self-flashing of galvanized steel construction with continuously welded seams, and factory installed nailer strip.

Accessories

        - ******************************************************************************

        - Retain only one of the two following subparagraphs.

        - ******************************************************************************

Backdraft Damper: Gravity actuated, aluminum multiple blade construction, felt edged with offset hinge pin, nylon bearings, blades linked, spring return.

        - *** OR ***

Motor Operated Damper: Aluminum multiple blade construction, felt edged with offset hinge pin, nylon bearings, blades linked, motor drive, power open or closed.

MOTORS

Provide motors that comply with <<IEEE 841>>

SOURCE QUALITY CONTROL

Sound-Power Level Ratings: Comply with <<AMCA 301>>. Factory test fans according to <<AMCA 300>>. Label fans with the AMCA-Certified Ratings Seal.

Fan Performance Ratings: Establish flow rate, pressure, power, air density, speed of rotation, and efficiency by factory tests and ratings according to <<AMCA 210>>.

PART 3 - EXECUTION

    - **********************************************************************************************

      - For HVAC fans that are not exempt from seismic, if project specification package includes Section << 22 0548.23 - Vibration and Seismic Controls for Mechanical Systems>>, and if requirements associated with installation, testing, and inspection of mounting and/or anchorage devices differ from those requirements in Section << 22 0548.23 - Vibration and Seismic Controls for Mechanical Systems>>, they must be described herein (in PART 3). Also, if this is applicable, identify special types of seismic-control devices required for each application using the same terminology used for those devices in PART 2.

    - **********************************************************************************************

EXAMINATION

Verify roof curbs are installed and level, and dimensions are as shown on Drawings.

INSTALLATION

Equipment Mounting

For floor mounted equipment, install fans on cast-in-place concrete equipment base(s) using << elastomeric pads;  elastomeric mounts; or  restrained spring isolators>>. << Comply with requirements for equipment bases specified in Section  03 3001 - Reinforced Concrete;  Comply with requirements for equipment bases specified in Section 03 3053 - Miscellaneous Cast-in-Place Concrete; or  None - N/A>>.

For equipment suspended from structure, install continuous-thread hanger rods and << elastomeric hangers;  spring hangers; or  spring hangers with vertical-limit stop>> of size required to support weight of the unit.

Secure << roof; and  wall>> fans<< and gravity ventilators; or  None - N/A>> with << cadmium plated steel;  aluminum; or  stainless steel>> lag screws to << roof curb; and  support frame structure>>.

Install flexible connections between fan and ductwork as specified in Section << 23 3101 - HVAC Ducts>>.  Ensure metal bands of connectors are parallel with minimum one inch flex between ductwork and fan while running.

Install backdraft dampers on inlet to << roof; and  wall>> exhaust fans<< and gravity ventilators used in relief air applications; or  None - N/A>>.

Install safety screen where inlet or outlet is exposed.

Install backdraft dampers on discharge of exhaust fans<< and as indicated on drawings; or  None - N/A>>.

Provide sheaves required for final air balance.

Install fans with sufficient working space for inspection and routine maintenance.

Label fans according to requirements specified in Section << 22 0554 - Identification for Plumbing,  HVAC, and Fire Piping and Equipment>>.

FIELD QUALITY CONTROL

Manufacturer's Field Service:  Engage a factory-authorized service representative to test and inspect components, assemblies, and equipment installations, including connections.

Perform the following tests and inspections with the assistance of a factory-authorized service representative:

Verify that shipping, blocking, and bracing are removed.

Verify that unit is secure on mountings and supporting devices and connections to ducts and electrical components are complete.  Verify that proper thermal-overload protection is installed in motors, starters, and disconnect switches.

Disconnect fan drive from motor, verify proper motor rotation direction, and verify fan wheel free rotation and smooth bearing operation.  Reconnect fan drive system, align and adjust belts, and install belt guards.

Adjust belt tension.

Adjust damper linkages for proper damper operation.

Verify that cleaning and adjusting are complete.

Verify lubrication for bearings and other moving parts.

Verify that manual and automatic volume control and fire and smoke dampers in connected ductwork systems are in fully open position.

Replace fan and motor pulleys as required to achieve design airflow.

Remove and replace malfunctioning units and retest as specified above.

Test and adjust controls and safeties.  Controls and equipment will be considered defective if they do not pass tests and inspections.

Prepare test and inspection reports.

SCHEDULES

See the Equipment Schedule on the drawings.

      - ***************************************************************************************

      - As a minimum, the following information and performance characteristics shall be shown on the drawings as part of the equipment schedule.

      - Capacity:

        - Air Flow, cfm

        - Static Pressure, inch wg

        - Fan RPM

      - Electrical Characteristics and Components:

        - Electrical Characteristics:

          - Motor HP, kW, Rated load amperes.

          - Volts, single or three phase, 60 Hz.

          - Maximum amperes

          - Minimum circuit ampacity

        - Disconnect Switch: Factory mount disconnect switch with indication of switch location (in control panel or on equipment).

      - ***************************************************************************************

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 23 3400, REV. 3, DATED APRIL 15, 2026.