SECTION 23 2300

REFRIGERANT PIPING

************************************************************************************************************

LANL MASTER SPECIFICATION

The designer is encouraged to review the DOE Handbook 1132, Design Considerations and ESM Chapters 6, 13, and 17.

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  This section must also be edited to delete requirements for processes, items, or designs that are not included in the project—and specifier’s notes such as these.

Please contact POC with suggestions for improvements.
When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

This template was developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements might be necessary if increased confidence in procurement or execution is desired, and independent review is necessary.  See ESM Chapter 1 Section Z10 specifications and quality sections.

This template was developed to meet the requirements for ASME B31.5-2016.  Application of this template to a different edition of the ASME code will require a detailed review of the code and ESM Chapter 17.

Seismic: In order to edit this section for Project-specific seismic requirements, refer to author notes that say/begin with “Seismic,” and the Seismic Specification Guide for Nonstructural Components: ASME B31 Piping posted with the templates for guidance on properly editing this section.

************************************************************************************************************

GENERAL

SECTION INCLUDES

Site and building refrigerant piping, fittings, and refrigeration specialties.

RELATED SECTIONS

Section 01 2500, Substitution Procedures

Section 01 3300, Submittal Procedures

Section 01 4000, Quality Requirements

Section 01 4444, Offsite Welding and Joining Requirements

Section 01 4455, Onsite Welding and Joining Requirements

Section 01 7828, Pressure Safety Closeout Submittals

*************************************************************************************************************

Seismic:  Edit “G” per Guide

*************************************************************************************************************

Section 01 8734, Seismic Qualification of Nonstructural Components (IBC), for requirements pertaining to [manufacturer’s certification] [and] [special certification].

Section 22 0529.23, Hangers and Supports for Plumbing Piping and Equipment

*************************************************************************************************************

Seismic:  Edit “I” per Guide

*************************************************************************************************************

Section 22 0548.23, Vibration and Seismic Controls for Mechanical Systems for [seismic-design criteria,] submittal requirements, devices for seismic restraint, and installation requirements for these devices.

Section 22 0554, Identification for Plumbing, HVAC, and Fire Protection and   Equipment

Section 22 0713, Plumbing and HVAC Insulation

Section 22 0813, Testing Piping Systems

Section 31 2000, Earth Moving

[Section 40 0527, Piping and Tubing Inspection Checklist]

References

Most widely or uniquely used at LANL applications are listed. Not all applicable standards are listed.  For ASME codes and standards, the latest published edition in effect at the time this code is specified is the specific edition referenced by the code unless otherwise specified in the engineering design.

*************************************************************************************************************

Designer note:

In the listing below, designer must eliminate standards that are not applicable to the project and add standards that are applicable to the project. Then, designer must either (1) specify each B31.5-listed materials’ national standard edition for each remaining standard listed or (2) determine latest is equivalent.  Then modify 1.3.B to either (1) keep the first option—and also list the edition year after each standard number (e.g., ASTM F493-04) or (2) keep the second option and eliminate outdated edition years from references other than B31.5 itself.

Specific edition reference dates are not always provided for ASME codes and standards. For ASME codes and standards, the latest published edition in effect at the time this Code is specified is the specific edition referenced by the Code unless otherwise specified in the engineering design.

This template was developed to meet the requirements for ASME B31.5-2016.  Application of this template to a different edition of the ASME code will require a detailed review of the code and ESM Chapter 17.

*************************************************************************************************************

ASME B31.5 – [2016][YEAR], Refrigerant Piping and Heat Transfer Components.

[All national standards invoked herein shall be taken to be the edition in effect for the code of record listed above in 1.3.A and shown below, unless noted otherwise]  [All national standards invoked below and herein shall be taken to be the latest edition].

ASME (American Society of Mechanical Engineers)

- ASME B1 Series

  - ASME B1.1, Unified Inch Screw Threads (UN and UNR Thread Form)

  - ASME B1.20.1, Pipe Threads, General Purpose (Inch)

- ASME B16 Series

          - ASME B16.15, Cast Copper Alloy Threaded Fittings Classes 125 and 250

          - ASME B16.18, Cast Copper Alloy Solder Joint Pressure Fittings

          - ASME B16.22, Wrought Copper and Copper Alloy Solder-Joint  Pressure Fittings

          - ASME B16.50, Wrought Copper and Copper Alloy Braze-Joint Pressure Fittings

- ASME Boiler and Pressure Vessel Code (ASME BPVC)

          - ASME BPVC Section V, Nondestructive Examination

          - ASME BPVC Section IX, Welding, Brazing, and Fusing Qualifications

ASTM International

      - ASTM B32-2004, Standard Specification for Solder Metal

      - ASTM B42-2002, Standard Specification for Seamless Copper Pipe, Standard Sizes

      - ASTM B280-2003, Standard Specification for Seamless Copper Tube for Air Conditioning and Refrigeration Field Service

      - ASTM B813-2010, Standard Specification for Liquid and Paste Fluxes for Soldering of Copper and Copper Alloy Tube

AWS (American Welding Society)

      - AWS D1.1-2015, Structural Welding Code —Steel, 23rd Edition

      - AWS A5.8M/A5.8:2004, Specification for Filler Metals for Brazing and Braze Welding

SAE

      - SAE J461-1981 (2002), Wrought and Cast Copper Alloys

      - SAE J513-1999, Refrigeration Tube Fittings General Specifications

ASHRAE (American Society of Heating, Refrigerating and Air-Conditioning Engineers, Inc.

      - ASHRAE 15–2016, Safety Standard for Refrigeration Systems

      - ASHRAE 34–2016, Designation and Safety Classification of Refrigerants

- ACTION Submittals

- All submittals shall be in accordance with the requirements of Section 01 3300.

- The following information shall be submitted for all relevant components:

    - Certified Material Test Report [or Certificate of Conformance (CoC) in the event that a CMTR is not available]

    - Installation, Operation, & Maintenance Manual

    - Product Data: Include the Manufacturer’s name, model number, parts list, and brief description of equipment and its basic operational features

    - Unlisted Items: Submit design data as follows:

      - Unlisted due to component type: Per ASME B31.5 Section 526.2.

      - Unlisted due to material of construction: Per ASME B31.5 Section 523.1.2.

- Before fabrication, submit NDE (non-destructive examination) procedures that will be used for fabrication and examination of the piping, test and inspection plan, and cleaning procedures.

- Prior to receiving materials, submit the Material Control Procedure.

- Provide all submittals required by Section 01 7828, Pressure Safety Closeout Submittals, for the as-built configuration.

- Provide “LANL Refrigerant Service Record Form”, ENV-ES-QP-312.10.

- QUALITY ASSURANCE

- Quality Assurance shall meet section 01 4000, Quality Requirements

- Material Control Procedure

      - Work shall be performed in accordance with an approved Material Control Procedure.  This procedure shall describe the control methods and documentation used to handle and monitor the use of controlled materials (piping component, fasteners, and welding filler rod and other components).

      - The procedure shall follow manufacturer’s requirements for storage and handling.

      - The procedure shall also address procurement controls, segregation of materials, and traceability of materials from receipt at the shop through processing and final assembly.

    - Inspection and Testing

      - Subcontractor shall perform inspection and testing to verify the conformance to the requirements in PART 2 of this section.

      - Subcontractor shall provide an Inspection and Test Plan indicating all testing and inspection functions to be performed, including hold points during fabrication and assembly, as well as during the Factory Acceptance Testing (FAT).  Hold points are required during the fabrication process to allow inspection, verification, or approval by LANL before the Subcontractor does further work. LANL has the right to waive Hold Points at their discretion.

      - Inspection and testing functions shall be performed by qualified personnel using qualified procedures in accordance with specified requirements.

      - Inspection Records: Subcontractor shall appropriately record, submit, and maintain records documenting the inspection and/or test then submit the completed Inspection Record as part of the QA Document Package. The status of all planned and executed inspection and testing activities shall be logged and traceable to ensure that the required inspection and testing have been performed, and any items that have failed inspection or testing are not inadvertently installed or implemented.

#### Qualifications

#### Installer Qualifications

        - Certify that all personnel have passed relevant qualification tests for joining processes involved and that certification is current.

          - Metallic Pipe:  Welders and braziers shall be qualified in accordance with ASME BPVC Section IX in accordance with Sections 01 4444 and 01 4455.

          - Steel Support Welding:  Qualify processes and operators to AWS D1.1/D1.1M.

      - Qualification of Examination Personnel:

        - Certified Welding Inspectors (CWI) shall be in accordance with 01 4444 and/or 01 4455.

        - Personnel performing other examination shall be certified in accordance with Contractor’s written practice.  Personnel performing nondestructive examination shall be qualified and certified for the method to be utilized following a procedure as described in BPV Code, Section V.

        - Certifications of examination personnel shall be maintained for Inspector’s review.

      - Owner’s Inspector will be qualified in accordance with ASME B31.5 Section 537.4 by LANL’s CM-CE Group.  LANL will act for DOE to designate Owner’s Inspectors or Representatives.

      - Manufacturer Qualifications

        - Must have a minimum of 5 years’ of experience

        - Must have maintenance service based within 200 miles radius of installation.

    - Extent and Retention of Records

      - The following shall be maintained by the fabricator for a minimum of 3 years:

        - Procedure specification, procedure qualification, and performance qualification records

        - Results of weld examinations other than visual

        - Records of the testing of each piping system, which shall include the following information:

          - date

          - identification of piping system tested

          - testing medium

          - test pressure

          - signature of examiner and inspector.

Part 2	PRODUCTS

*************************************************************************************************************

Seismic:  If Project Spec includes 22 0548.23, and the devices to be used differ from those specified in 22 0548.23 then these products must be included herein (in PART 2).  If this is applicable, use the same terminology for these devices in PART 3 in order to identify the type of devices required for each application.

*************************************************************************************************************

product options and substitutions

- Alternate products may be accepted per Section 01 2500.

- Proposal of unlisted components is strongly discouraged and will be evaluated in accordance with 01 2500. Substitutions will be allowed only if the Subcontractor can demonstrate that the product can meet the same code requirements of the item specified in the design. Costs associated with evaluation of unlisted components shall be the responsibility of the Subcontractor.

- If an unlisted component alternate is proposed, the Subcontractor must submit design data in accordance with “Action Submittals” article (1.4 B. 4) of this document.

************************************************************************************************************

Design notes

Soft annealed copper tubing larger than 1-3⁄8 in. (35 mm) O.D. shall not be used for field-assembled refrigerant piping, unless it is protected from mechanical damage.

Brazing reduces the tube rating to the fully annealed condition.

Soldered joints shall not be used for piping containing other than Group A1 refrigerants or any other toxic or flammable fluid.  For designation of refrigerants see ASHRAE 34.

Threaded joints larger than NPS 4 (DN 100) should not be used in refrigerant service.

Threaded joints larger than NPS 2 (DN 50) shall not be used for Groups A2 and B2, and Class 3 refrigerants.

Threaded joints larger than NPS 6 (DN 150) should not be used for salt brines.

Solder joints shall not be used for temperatures in excess of those given in ASME B16.22.

Compound or lubricant used on bolt threads shall be suitable for the service conditions and shall not react unfavorably with either the service fluid or the piping material.  Reference Manufacturer’s recommendations for suitable compounds and lubricants.

************************************************************************************************************

SEISMIC PERFORMANCE REQUIREMENTS

### The [Piping][, and __________] shall remain in place without separation of any parts when subjected to the design basis earthquake [per Section 01 8734, Seismic Qualification of Nonstructural Components (IBC)] [as represented by the seismic forces derived from the criteria indicated [on the drawings] [in Section 22 0548.23, Vibration and Seismic Controls for Mechanical Systems].

### The [Piping][, and __________] [is][are] [a] Designated Seismic System[s] and, as such, [it] [they] shall remain in place and [be fully operational] [and] [maintain containment] following the design basis earthquake per Section 01 8734, Seismic Qualification of Nonstructural Components (IBC).

REFRIGERANT PIPING

    - Copper tubing: ASTM B280, type ACR, Alloy 12200, temper shall be soft annealed O60 or drawn general purpose H58.  Copper thickness shall meet the alternative method LANL VAR- 2015-011 for the design pressure.

- Manufacturer:  Mueller/Streamline

- Model Number:  Nitrogenized ®ACR Tube  (Refrigeration Service Tube)

- Temperature Range:  250 F

- Pressure rating:  700 psig

- Size (nominal):   3/8 inch (1/8inch  through 1 3/8 inch ACR Type L, 1/8 inch through 2 5/8 inch ACR Type K)

- Location:  [Above grade, below grade; if below grade specify corrosion control in Part 3, Corrosion Control]

Copper Pipe:  ASTM B42, Alloy C10200 or C12200, O61 Temper, Schedule [40 “regular”, 80 “extra strong”]

      - Manufacturer:  Farmers Copper

      - Model Number:  ASTM B42

      - Temperature Range:  250 F

      - Pressure rating:  1160 psig [1790 psig schedule 80 extra strong]

      - Size (nominal):   2 ½ inch (1/8 inch IPS through 12 inch IPS)

      - Location:  [Above grade, below grade; if below grade specify corrosion control.

Copper Braze and fittings

    - Copper Braze Filler

- Onsite: Per LANL BPS 6000-107-F103-NF (nitrogen purged tube); offsite per Subcontractor BPS in accordance with 01 4444.

#### Process:  Torch Brazing (neutral)

- Filler Metal:  AWS A5.8M/A5.8, BCuP-5 silver/phosphorus/copper alloy with melting range 1190 to 1480°F

- Flux:  N/A

- Comply with [01 4444, 01 4455].

    - Copper Braze Fittings

      - ASME B16.50 Wrought Copper and Copper Allow Braze-Joint Pressure Fittings.  Bores and depth of sockets shall conform to ASME B16.18, Cast Copper Alloy Solder Joint Pressure Fittings and ASME B16.22, Wrought Copper and Copper Alloy Solder-Joint Pressure Fittings.

      - Location:  [Above grade/Below grade]

      - Size:  2 inches and smaller [1/8inch  through 1 3/8 inch ACR Type L, 1/8 inch through 2 5/8 inch ACR Type K]

      - Manufacturer:  [Muller/Streamline, Elkhart, Nibco]

    - Copper Threaded Fittings

      - ASME B16.15, Cast Copper Alloy Threaded Fittings Classes 125 and 250, threads per ASME B1.20.1 tapered.

      - Location:  [Above grade/Below grade]

      - Size:  2 inches and smaller

      - Class:  125 [250]

      - Temperature:  -20 to 200 deg F

      - Pressure:  1400 psig [1/8 2800 psig to 7/8 450 psig]

      - Manufacturer:  [Muller/Streamline, Elkhart, Nibco]

Copper Flare Fittings

      - SAE J513, Refrigeration Tube Fittings General Specifications. Description:  A 45 degree flare flared body and nut for use with annealed copper tubing. Materials are SAE J461 CA 360 (half-hard), CA 345 or CA 377 (forged) brass with CA377 nuts.  Fittings may have a combination of ASME B1.1 UNF (5/16 to 7/8 inch) or UNS 1 1/16 inch and ASME B1.20.1 NPT tapered threads (1/8 through ¾ inch).  Fittings are available based on outside tube diameter.

      - Location:  [Above grade/Below grade]

      - Size:  1/4 inch annealed tube outside diameter [3/16, 1/4, 5/16, 3/8, 1/2, 5/8, 3/4 tube outside diameter inch]

      - Temperature range:  -65 to +250 °F

      - Pressure:  200 psig

      - Manufacturer:  Parker

************************************************************************************************************ Design notes

Specify required refrigeration specialties such as filter-dryers, solenoid valves, expansion valves, moisture and liquid indicators, strainers, pressure regulators, etc., to suit project.  Items must meet the ASME B31.5 requirements for components.

***********************************************************************************************************

REFRIGERANT SPECIALTIES

- Solenoid Valve:  Brass valve, Pilot operator, MKC-2 coil kit, synthetic to metal main port, stainless steel pin to synthetic seal pilot port, stainless steel stem and plunger assembly, piston disc.

      - Manufacturer:  Sporlan

      - Model Number:  E10S240, E10S350

      - Temperature Range:  -40 to120 Ambient, -40 to 240 deg F fluid

      - Pressure rating:  500 psig, Brass

      - Size:  ½ inch through 5/8 inch

- Ball Valve  Forged Brass Body, Polished Brass or Carbon Steel Ball

      - Manufacturer:  Superior Refrigeration Products

      - Model Number:  WA, WAS, MST

      - Temperature Range: -40 to 325 deg F

      - Pressure rating: 700psig

      - Size:  ¼ inch through 4 1/8 inch

- Moisture and Liquid Indicator, Sight Glass

Manufacturer:  Sporlan

Model Number:  "See-All"

Temperature Range:  -50 to 149 oF

Pressure rating:  650 PSIG

Size:  1/4 inch through 2-1/8 inch

- Thermostatic Expansion Valve Fill Valve Machined brass bar body, brass port machined into body, stainless steel pin and pushrod, max external leakage – 0.10 oz/yr at 300 PSIG.

      - Manufacturer:  Parker-Sporlan

Model Number:  Type R

Operating Temperature Range:  -40 oF to 50 oF

Pressure rating: 700 (R-410A), 450 psig (all others)

Size:  1/4 inch inlet 3/8 inch outlet or 3/8 inch inlet ½ inch outlet all SAE J513 flare fittings.

- Metal Hose - Vibration Elimination 	by size and material; Bronze or stainless steel hose and braids, female copper tube ends 1/8 inch to 2 inch.

      - Manufacturer:  Anaconda Universal

Model Number:  1212FY

End Connection:  Inside conforms to ASME B16.18 and B16.22.

Pressure rating:  450 psig

Size:  1/2 inch through 1 inch

# PART 3 EXECUTION

*************************************************************************************************************

Seismic: If Project Spec includes 22 0548.23, and if requirements associated with installation, testing, and inspection of mounting and/or anchorage devices differ from those requirements in 22 0548.23, the differing requirements must be included herein (in PART 3).

*************************************************************************************************************

- PREPARATION

    - Ream pipe and tube ends. Remove burrs.

    - Remove corrosion, scale, and dirt on inside and outside before assembly.

    - Keep open ends of pipe free from scale and dirt. Protect open ends with temporary plugs or caps.

    - Pre Assembly Cleaning

      - Subcontractor shall be responsible for the cleanliness and integrity of the system. Internal and external of pipe, tube, and components shall be free of loose scale, sand, dirt, paint, metal chips, filings, flux, slag, weld spatter, mill scale, rust, grease, oil, waxes, or other contaminants that are easily seen with the unaided eye.

Consult manufacturer’s recommendation for the use of acids and cleaning agents to prevent damage.

Ensure safeguards are taken to protect personnel from hazards of cleaning, which may include but not be limited to flying particulates, corrosive chemicals, and harmful vapors.

A suitable chemical and/or mechanical cleaning method shall be used, if necessary, to clean all surfaces to be fabricated.

*************************************************************************************************************

Seismic:  Edit 3.2 per the Guide.

*************************************************************************************************************

- FLEXIBLE CONNECTIONS

  - Install flexible connections for [_________] where shown on drawings.

- PRE-ASSEMBLY

    - Verify materials are correct before assembly in accordance with the accepted Material Control Procedure.

Fastener materials shall be free of nicks, burrs, chips, dirt, and damage (inspect threads, shank, and nuts). All damaged fasteners must be replaced.

- ASSEMBLY

    - Soldering shall not be used for refrigeration piping.

    - Brazed shall be assembled as follows:

      - Braze per LANL BPS 6000-107-F103-NF.

      - Piping shall be continuously purged prior to, during, and after brazing till cool to prevent copper oxidation on the interior of the tubing. There shall be no visible unfilled joint space.

      - Penetration of filler metal inside the pipe shall not exceed 100 of the wall thickness.

      - There shall be no visible evidence of excessive overheating.

      - Braze joints shall be cleaned after assembly has cooled to remove excessive flux.

    - Threaded Joints (ASME B1.20.1 tapered)

      - Teflon ® (polytetrafluoroethylene) [or other suitable material] thread tape shall be used for assembly.

      - Sealant shall be applied to the male threads only.

      - The threaded joint assembly shall be in accordance with ASME B1.20.1, 3.1.9 Wrench-Tight Engagement between External and Internal Taper Threads.

    - 45 Degree Flare (SAE J513)

      - Cut tubing squarely and clean tube end thoroughly to remove burrs.

      - Place nut onto tube. Place threaded end of nut toward end of tube.

      - Flare tube end with flaring tool to provide 45° flare.

      - No scratches, breaks, or other mars at sealing surface of flare shall be permitted.

      - Clamp tube flare between nut and nose of fitting body by screwing nut on finger-tight.  Tighten with a wrench an additional 1/4 turn for a metal-to-metal seal.

- BURIED PIPING

    - Provide earth cover, bedding, and warning tape per Drawings and Section 31 2000, Earth Moving.

- HANGER AND SUPPORT INSTALLATION

    - Support piping in accordance with Section 22 0529, Hangers and Supports for Plumbing Piping and Equipment.

- INSULATION INSTALLATION

    - Insulate piping in accordance with Section 22 0713, Plumbing and HVAC Insulation.

    - Sleeve pipe passing through partitions, walls and floors.  Provide UL/FM-approved, through-penetration firestop system when penetrating a fire-rated barrier (e.g., certain walls, floors, etc.).

- LAbeling

    - Label piping in accordance with Section 22 0554, Identification for Plumbing, HVAC, and Fire Piping and Equipment.

- EXAMINATION, TESTING, AND INSPECTION

    - Pressure test piping in accordance with Section 22 0813, Testing Piping Systems.

    - After successful completion of pressure tests, remove pressurization gas and evacuate system to [500 microns], [state value microns] to remove moisture and non-condensables.

    - Fully charge completed system with refrigerant after testing. If startup is not within 24 hours, temporarily pressurize to 5 psig with system refrigerant.

- INSTALLATION – Above ground piping system

    - Where more than one piping system material is specified, provide compatible system components and joints.

    - Provide unions or couplings at locations requiring servicing. Use unions or couplings downstream of valves and at equipment connections.  Do not use direct-welded or threaded connections to equipment or major valves.

    - Provide flexible connectors at or near equipment where piping configuration does not absorb vibration.

    - Install flexible connectors at right angles to axial movement of compressor, parallel to crankshaft.

    - Route piping parallel to building structure and maintain gradient.

    - Install piping to conserve building space, and not interfere with use of space.

    - Group piping whenever practical at common elevations.

    - Provide access where valves and fittings are not exposed.

    - Arrange refrigerant piping to return oil to compressor.  Provide traps and loops in piping, and provide double risers as required. Slope horizontal piping 1/2 inch in 10 feet, and in direction of flow.

    - Install valves with stems upright or horizontal, not inverted.

    - Provide external equalizer piping on expansion valves with refrigerant distributor connected to evaporator.

    - Comply with ASHRAE 15 procedures for charging and purging of systems and for disposal of refrigerant.

*************************************************************************************************************

Designer Note

Specification may be altered to allow pipe or tubing bends, but must comply with the ASME B31.5 requirements for pipe bends:

504.2.1 Pipe Bends. Pipe after bending shall conform to the following:

(a) The minimum thickness after bending shall not be less than as required for straight pipe in accordance with para. 504.1.

(b) The difference between maximum and minimum diameters for pipe bends subjected to internal pressure should not exceed 8% of the nominal outside diameter of the pipe.

(c) The difference between maximum and minimum diameters for pipe bends subjected to external pressure should not be greater than 8% of the nominal outside diameter of the pipe.

(d) Bends made with greater flattening than indicated above shall meet the requirements of para. 504.7.

(e) Bends for use on heat transfer components such as U-bends (return bends) shall be designed in accordance with the requirements of para. 504.7.

*************************************************************************************************************

    - No pipe or tube bends are allowed.  Fittings are to be used instead of bends

*************************************************************************************************************

Designer note

The following items should be considered during the design.

- Install moisture/liquid indicators in liquid line at the inlet of the thermostatic expansion valve or at the inlet of the evaporator coil capillary tube.

- Install refrigerant service valves in suction and discharge lines of compressor.

- Install a check valve at the compressor discharge and a liquid accumulator at the compressor suction connection.

- Install refrigerant charging valve in liquid line between receiver shut-off valve and expansion valve.

- Install solenoid valves upstream from each expansion valve.  Install solenoid valves in horizontal lines with coil at top and provide electrical connection to solenoid valves.

- Install thermostatic expansion valves as close as possible to distributors on evaporators and locate expansion valve sensing bulb immediately downstream of evaporator on suction line.

- Install pressure relief valves on ASME receivers. Install relief valve discharge piping to terminate outdoors.

- Install strainer upstream of each automatic valve and install shut-off valves on each side of strainer.

- Install filter dryers in liquid line between compressor and thermostatic expansion valve or in the suction line of the compressor.

- In process examination in accordance with paragraph 536.6.2 may be substituted for all or part of the substituted for all or part of radiographic examination on a weld-for-weld basis if specified in the engineering design and specifically approved by the Inspector.

*************************************************************************************************************

END OF SECTION

***********************************************************

Do not delete the following reference information:

***********************************************************

THE FOLLOWNG STATEMENT IS FOR LANL USE ONLY

This project specification is based on LANL Master Specification Section 23 2300 Rev. 3, dated September 21, 2017.