SECTION 23 3101

HVAC DUCTS

*************************************************************************************************************

LANL MASTER SPECIFICATION

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete items for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  This specification template is tailored to meet requirements contained in the LANL Engineering Standards Manual (ESM). Additional tailoring requirements are contained in ESM Chapter 1 Section Z10 Att. F, Specifications.

To seek a variance from requirements of the ESM that are applicable, contact the ESM Mechanical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

This specification is developed for ML-4 projects and commercial applications.  For industrial or confinement ventilation applications, SMACNA Round and Rectangular Industrial Duct Construction Standards should be used to edit this specification.   For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

Seismic: In order to edit this section for Project-specific seismic requirements, refer to author notes that say/begin with “Seismic” and the Seismic Specification Guide for Nonstructural Components: Mechanical Components posted with the templates for guidance on properly editing this section. 
*************************************************************************************************************

GENERAL

SUMMARY

Section includes ductwork, hangers and supports, duct cleaning, duct sealing, and [duct leakage test].

RELATED SECTIONS

*************************************************************************************************************

Seismic:  Refer to Guide for editing guidance for this article.

*************************************************************************************************************

Section 01 8734, Seismic Qualification of Nonstructural Components (IBC), for requirements pertaining to [manufacturer’s certification] [and] [special certification].

Section 22 0548.23, Vibration and Seismic Controls for Mechanical Systems, for [seismic-design criteria,] submittal requirements, devices for seismic restraint, and installation requirements for these devices.

ACTION SUBMITTALS

Submit the following in accordance with Subcontract submittal procedures:

- Catalog data for duct materials, flexible duct/connectors, sealing materials.

- Shop Drawings:

        - Fabrication, assembly, and installation, including plans, elevations, sections, segmentation/joints, components, and attachments to other work.

        - Factory- and shop-fabricated ducts and fittings.

        - Duct layout indicating sizes, configuration, liner material, and static-pressure classes.

        - Elevation of top of ducts.

        - Dimensions of main duct runs from building grid lines.

        - Fittings.

        - Reinforcement and spacing.

        - Seam and joint construction.

        - Penetrations through fire-rated and other partitions.

        - Equipment installation based on equipment being used on Project.

        - Locations for duct accessories, including dampers, turning vanes, and access doors and panels.

        - Hangers and supports, including methods for duct and building attachment and vibration isolation.

        - <Insert lists of areas or systems requiring Shop Drawings.>

- Test Reports indicating pressure tests performed.  Include segment tested, test pressure, leakage rate, and tester/date following SMACNA HVAC Air Duct Leakage Test Manual.

- Certificates shall be submitted showing conformance with the applicable standards for ductwork materials, brazing materials, mill-rolled reinforcing and supporting materials, welding procedures, shop test procedures and reports.

- Certification of welders and qualified welding procedure per Section [01 4444] [and] [01 4455].

INFORMATIONAL SUBMITTALS

- Coordination Drawings: Plans, drawn to scale, on which the following items are shown and coordinated with each other, using input from installers of the items involved:

        - Duct installation in congested spaces, indicating coordination with general construction, building components, and other building services. Indicate proposed changes to duct layout.

        - Suspended ceiling components.

        - Structural members to which duct will be attached.

        - Size and location of initial access modules for acoustical tile.

        - Penetrations of smoke barriers and fire-rated construction.

        - Items penetrating finished ceiling including the following:

        - Luminaires.

        - Air outlets and inlets.

        - Speakers.

        - Sprinklers.

        - Access panels.

        - Perimeter moldings.

        - <Insert item>.

QUALITY ASSURANCE

Construct ductwork in accordance with SMACNA HVAC Duct Construction Standards—Metal and Flexible, and NFPA 90A.

Qualify welding processes and welding operators in accordance with AWS D1.1 “Structural Welding Code—Steel” for hangers and supports and AWS D9.1 “Sheet Metal Welding Code”.

Fiberboard duct is not acceptable duct material except when used for fabricating return air sound traps.

QUALIFICATIONS

Manufacturer: Company specializing in manufacturing products specified in this section with minimum 3 years experience.

Installer: Company specializing in performing work of this section with minimum 3 years’ experience approved by manufacturer.

ENVIRONMENTAL REQUIREMENTS

Do not install duct sealant when temperatures are less than those recommended by sealant manufacturers.

Maintain temperatures during and after installation of duct sealant.

FIELD MEASUREMENTS

Verify field measurements prior to fabrication.

PRODUCTS

*************************************************************************************************************

Seismic:  If Project Spec includes 22 0548.23, and the devices to be used differ from those specified in 22 0548.23, then these products must be included herein (in PART 2).  If this is applicable, use the same terminology for these devices in PART 3 in order to identify the type of devices required for each application.

*************************************************************************************************************

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

*************************************************************************************************************

Seismic:  For either para 2.2.A or 2.2.B, if there are too many systems/components to list here, then list them in an appendix to this section, and then merely refer to that appendix in the para.

*************************************************************************************************************

SEISMIC PERFORMANCE REQUIREMENTS

The [______] shall remain in place without separation of any parts when

subjected to the design-basis earthquake [per Section 01 8734, Seismic

Qualification of Nonstructural Components (IBC)] [as represented by the seismic

forces derived from the criteria indicated [on the drawings] [in Section 22 0548.23,

Vibration and Seismic Controls for Mechanical Systems].

The [______] is a Designated Seismic System and, as such, it shall remain in

place and [be fully operational] [and] [maintain containment] following the design-

basis earthquake [per Section 01 8734, Seismic Qualification of Nonstructural

Components (IBC)] [as represented by the seismic forces derived from the criteria

indicated [on the drawings] [in Section 22 0548.23, Vibration and Seismic

Controls for Mechanical Systems].

DUCT MATERIALS

Galvanized Steel Ducts and Fittings: ASTM A653 and A924 galvanized steel sheet, lock-forming quality, having G90 zinc coating per ASTM A90.

- Finishes for surfaces exposed to View: Mill Phosphatized.

****** [OR] ******

Steel Ducts: ASTM [A1008] [A1011] [A568].

****** [OR] ******

Aluminum Ducts: ASTM B209, aluminum sheet, alloy 3003-H14.  Aluminum Connectors and Bar Stock: Alloy 6061-T6 or of equivalent strength.

****** [OR] ******

Stainless Steel Ducts: ASTM [A167] [A666] [A480], Type [304.] [316.]

- Exposed surface finish shall be [insert finish], [No. 2D], [No. 3], or [No. 4] as indicated [on drawings] [in Duct Schedule].

****** [OR] ******

PVC Coated Ductwork: Fabricate from ASTM A653 galvanized steel sheet with minimum G60 zinc coating per ASTM A90.  Provide 4-mil coating on both sides meeting UL 181, Class 1 requirements.  PVC coating shall be uniform, smooth, and free from scratches or other imperfections. Cover scratches with manufacturer’s touch-up paint.

Fasteners: Rivets, bolts, or sheet metal screws.

Hanger Rod: ASTM A36; steel, threaded both ends, threaded one end, or continuously threaded.  Use galvanized steel or aluminum, 6061-T6, hangers in contact with aluminum duct.

Hanger Straps: ASTM A653 galvanized steel having G90 zinc coating in conformance with ASTM A90.

Structural Steel Members: ASTM A36 steel.  Use aluminum, 6061-T6 or galvanized steel members for aluminum ducts.

DUCTWORK FABRICATION

Fabricate ductwork, duct access doors and support in accordance with SMACNA HVAC Duct Construction Standards—Metal and Flexible.  Furnish duct material, gages, reinforcing, and sealing for design pressure class indicated.

Construct tees, bends, and elbows with minimum radius 1-1/2 times centerline duct width.  Where not possible and where rectangular elbows are used, provide airfoil turning vanes constructed and installed in accordance with SMACNA Standards.  Vanes are not required in return air sound trap elbows and transfer ducts.

Fabricate continuously welded round and oval duct fittings two gages heavier than duct gages indicated in SMACNA Standard.

Provide, at minimum, rectangular 45 degree entry fittings for rectangular ducts and 45 degree wye takeoffs for round ducts.

Provide 100% full penetration welds for exhaust ductwork serving perchloric and other acid systems and lab/process exhaust.

Duct sizes noted are inside clear dimensions. [For lined ducts, maintain duct sizes inside lining.]

No variation of duct configuration or sizes other than those of equivalent or lower loss coefficient is permitted except by written permission from LANL STR.  Round ducts installed in place of rectangular ducts shall be sized in accordance with ASHRAE table of equivalent rectangular and round ducts.

Increase duct size gradually, not exceeding 15 degree divergence wherever possible.  Do not exceed 30-degree divergence upstream of equipment. Do not exceed 45-degree convergence downstream of equipment.

FLEXIBLE DUCTS (INSULATED, LOW PRESSURE)

Manufacturer: Flexmaster, Type 5.

Duct assembly of a trilaminate of aluminum foil, fiberglass, and aluminized polyester, mechanically locked (no adhesives) into an aluminum helix formed on the ducts outside surface, insulation encased in a fire retardant protective barrier, duct UL listed 181 class 1, and complies with NFPA 90A.

      - Pressure Rating: 6 inches w.g. positive, 4 inches w.g. negative through 16 inches diameter, 1 inch w.g. negative for 18 inches and 20 inches diameter.

      - Rated Velocity: 4000 fpm.

      - Temperature Rating:  Minus 20 degrees F to plus 250 degrees F.

      - Insulation: Fiberglass, K-factor (thermal conductivity) of approximately 0.24 BTU•in/hr•ft2•F at mean temperature of 75 degrees F.

FLEXIBLE DUCTS (INSULATED, HIGH PRESSURE)

Manufacturer: Flexmaster, Type 3.

Duct assembly of a trilaminate of aluminum foil, fiberglass, and aluminized polyester, mechanically locked (no adhesives) into an aluminum helix formed on the ducts outside surface, insulation encased in a fire retardant protective barrier, duct UL listed 181 class 1, and complies with NFPA 90A.

      - Pressure Rating: 12 inches w.g. positive, 5 inches w.g. negative through 16 inch diameter, 1 inch w.g. negative for 18 inches and 20 inches diameter.

      - Rated Velocity: 5500 fpm.

      - Temperature Rating:  Minus 20 degrees F to plus 250 degrees F.

      - Insulation: Fiberglass, K-factor (thermal conductivity) of approximately 0.24 BTU•in/hr•ft2•F at mean temperature of 75 degrees F.

FLEXIBLE DUCTS (NON-INSULATED, LOW TO HIGH PRESSURE)

Manufacturer: Flexmaster, Type NI-35.

Duct assembly of a trilaminate of aluminum foil, fiberglass, and aluminized polyester, mechanically locked (no adhesives) into an aluminum helix formed on the ducts outside surface, insulation encased in a fire retardant protective barrier, duct UL listed 181 class 1, and complies with NFPA 90A.

      - Pressure Rating: 12 inches w.g. positive, 5 inches w.g. negative through 16 inches diameter, 1 inch w.g. negative for 18 inches and 20 inches diameter.

      - Rated Velocity: 6500 fpm.

      - Temperature Rating: Minus 20 degrees F to plus 250 degrees F.

*************************************************************************************************************

Provide flexible connections immediately adjacent to suction and discharge ends of moving equipment, e.g., fans.

NOTE:  Per Ventfabrics, their flexible-connection products aren’t intended to function/perform as seismic flex connections.

*************************************************************************************************************

FLEXIBLE CONNECTIONS (EXPOSED TO SUN AND WEATHER)

Manufacturer: Ventfabrics, Ventlon.

Heavy glass fiber (coated with DuPont’s Hypalon), fire retardant, UL Standard 214, and complying with NFPA-90A.

- Pressure Rating:  10 inches w.g., negative and positive.

- Temperature Rating:  Minus 10 degrees F to plus 275 degrees F.

- Weight:  26 oz/sq yd plus or minus 2 ounces.

FLEXIBLE CONNECTIONS (INDOOR)

Manufacturer: Ventfabrics, Ventglas.

Heavy glass fiber (coated with DuPont’s neoprene), fire retardant, UL Standard 214, and complies with NFPA-90A.

      - Pressure Rating: 10 inches w.g. negative and positive.

      - Temperature Rating: Minus 20 degrees F to plus 200 degrees F.

      - Weight: 30 oz/sq yd plus or minus 3 ounces.

*************************************************************************************************************

When specifying spiral seam ductwork, check the manufacturer’s data for standard stock sizes.

*************************************************************************************************************

SPIRAL ROUND AND FLAT OVAL DUCT

Machine made spiral lock-seam duct constructed of galvanized steel with light reinforcing corrugations.

Fittings:  Welded seam construction, manufactured of at least two gages heavier metal than duct.

Joints:  Either fully welded or bolted flange with gasket material in accordance with manufacturer’s recommendation.

DUCT LINer

*************************************************************************************************************

See ESM Mechanical Chapter, D3040, for duct lining limitations.

*************************************************************************************************************

Manufacturer: CertainTeed, Tough Gard 2 with Enhanced Surface or equivalent.

Composed of long textile type glass fibers with thermosetting resin overlaid with a tough and durable fire resistive black composite surface on the air stream.  The air stream surface shall contain am EPA registered antimicrobial agent to reduce the potential of microbial growth.  Flame spread/smoke developed 25/50 maximum meeting NFPA 90A requirements.

      - Thickness: [1] inch.

      - Velocity Rating: 6000 fpm.

      - Temperature Rating: 250 degrees F.

      - Minimum Density: [1 1/2 ] pcf.

AIR DUCT BOARD

************************************************************************************************************

Use this material ONLY for fabricating return air sound traps per mechanical standard drawing ST-D3040-2.  Specify black mat interior finish where reflection (dark rooms, etc.) or aesthetics is a concern.

************************************************************************************************************

Manufacturer: CertainTeed, Ultra*Duct Black Duct Board.

Rigid resin-bonded fiberglass board faced on exterior side with foil-scrim-kraft (FSK) vapor retarder, and air stream surface faced with a tightly bonded non-woven black mat facing or impregnated with a polymer coating.  Service temperature 250 degrees F maximum, air velocity 5000 fpm maximum, and internal static pressure plus or minus 2 inches water maximum.  The air stream surface shall contain EPA registered antimicrobial agent to reduce the potential of microbial growth.  Flame spread/smoke developed 25/50 maximum meeting NFPA 90A requirements, thickness 1 inch.

EXECUTION

*************************************************************************************************************

Seismic: If Project Spec includes 22 0548.23, and if requirements associated with installation, testing, and inspection of mounting and/or anchorage devices differ from those requirements in 22 0548.23, then the differing requirements must be included herein (in PART 3).

*************************************************************************************************************

  - EXAMINATION

Verify sizes of equipment connection before fabricating transitions.

INSTALLATION

Install, seal, and support ductwork in accordance with SMACNA HVAC Duct Construction Standards—Metal and Flexible.

Seal all ductwork and plenums with pressure class ratings to SMACNA Seal Class A.

During construction, install temporary closures of metal or taped polyethylene on open ductwork to prevent construction dust from entering ductwork system.

Use double nuts and lock washers on threaded rod supports.

Connect flexible ducts to metal ducts with metal screw clamps or draw bands and suitable sealer. Follow manufacturer’s installation instructions.

Locate ducts with sufficient space around equipment to allow normal operating and maintenance activities.

Install balancing dampers with indicating type locking quadrant where noted on drawing.  Inspect and ensure that the construction of balancing dampers, including the hand quadrant, is of good quality prior to installation.

      - Dampers are not required upstream or downstream of VAV boxes serving only one diffuser.

      - Do not use splitter dampers.

      - Locate balancing dampers as far as possible (recommend no closer than 5 feet) from air terminals to avoid excessive noise.

*************************************************************************************************************

Seismic:  If necessary/applicable, include the following paragraph to ensure compliance with the seismic requirements for flexible connections.

For the same reason, the flex-connection-related text in the subsequent paragraph must be edited as necessary/applicable to ensure compliance with the seismic requirements for flexible connections.

Design Note:  Components that are installed in-line with the duct system and have an operating weight greater than 75 lb, such as fans, heat exchangers, and humidifiers, shall be supported and laterally braced independent of the duct system and such braces shall meet the force requirements of Section 13.3.1 [, Seismic Design Force].  Unbraced ductwork [i.e., seismically exempt ductwork] attached to in-line equipment shall be provided with adequate flexibility to accommodate the seismic relative displacements of Section 13.3.2 [, Seismic Relative Displacements].

*************************************************************************************************************

Install flexible connections for [_________] where shown on drawings.

Install flexible connections with minimum 1 inch slack immediately adjacent to equipment in ducts associated with fans and motorized equipment.

Limit flexible ductwork to diffusers, terminal units, or light troffer boots, to 5 feet in length.

      - Do not install flexible ductwork upstream of VAV boxes.

      - Install rigid straight ductwork, 2 duct diameters or a minimum of 12 inches, downstream of VAV boxes.

*************************************************************************************************************

Refer to NFPA 90A, Annex A, Section A.4.3.4.1 and SMACNA Fire, Smoke and Radiation Dampers Installation guide for HVAC System for fire damper access door sizes, locations, etc.

*************************************************************************************************************

Install duct access doors for inspection and cleaning upstream of filters, coils, automatic dampers, rectangular elbows with turning vanes, and equipment as indicated on drawings.  Provide minimum 8 X 8 inch size for hand access, 18 X 18 inch size or 18 inch x the duct height/width less 2 inches for shoulder access.

- Install duct access door upstream of fire damper, size [18 x 18 min., 24 x 24 max.]

Where indicated, weld or braze duct joints and seams in accordance with AWS D9.1.

Repair damaged galvanized ductwork surfaces (welds, scratches, etc.) by applying minimum 2 coats of a zinc base paint.

Paint exposed ductwork in occupied areas to match surroundings. Refer to Section 09 9100, Painting.  [Optional requirement, consult with user.  Specify color if necessary.]

Provide duct drops to diffuser same size as diffuser neck size.

Provide UL/FM approved through-penetration firestop system when penetrating fire-rated barriers (i.e., walls, floors, etc).

Install openings in ductwork where required to accommodate thermometers and controllers. Install pitot tube openings for testing of systems.  Install pitot tube complete with metal can with spring device or screw to prevent air leakage.  Where openings are provided in insulated ductwork, install insulation material inside metal ring.

Secure duct liner with mechanical fasteners and adhesive per SMACNA duct liner standards and/or manufacturer’s installation specifications.  Coat all raw exposed edges per manufacturer’s instructions.

Insulate ductwork in accordance with Section 22 0713, Plumbing and HVAC Insulation.

CLEANING

After completing system installation and inspection, clean duct systems in accordance with National Air Duct Cleaners Association (NADCA) specifications

- The cleaning agency shall be a certified member of NADCA, or shall be certified by a nationally recognized program and organization.

DUCTWORK MATERIAL SCHEDULE

*************************************************************************************************************

Include a material schedule when project contains more than one system with different duct materials (partial industrial/confinement applications).  The following is an example of a schedule.

*************************************************************************************************************

Fabricate ducts from galvanized steel except for the following air systems:

| AIR SYSTEM | MATERIAL |
| --- | --- |
| Fume Hood Exhaust | Stainless Steel [304] [316] |
| Shower Room and Dishwasher Exhaust | Stainless steel |
| Emergency Generator Exhausts | Steel, Schedule 40 pipe. |

DUCTWORK PRESSURE CLASSIFICATIOn

*************************************************************************************************************

Each duct system is constructed for the specific pressure classification selected by the designer.  This information must be noted on the drawings or in this specification if the pressure class exceeds 1-inch w.g.  For guidance on pressure classification refer to SMACNA HVAC Duct Construction Standards, Metal and Flexible. The following is an example.

*************************************************************************************************************

Construct each duct system for a minimum pressure classification of 1 inch w.g., and as follows:

- Supply Ducts: [3] inch w.g. pressure duct from air handling unit to VAV terminal unit.

- Supply Ducts: [2] inches pressure duct from VAV terminal unit to diffuser.

- Return Ducts: [2] inches w.g., negative pressure.

- Exhaust Ducts: [2] inches w.g., negative pressure.

DUCT SEALING

Seal duct seams and joints in accordance to the duct pressure classification as described in SMACNA HVAC Duct Construction Standards-Metal and Flexible.

Seal joints between duct segments and duct seams with welds, gaskets, mastic adhesives, mastic plus embedded fabric systems, or tape.

- Sealants, Mastics and Tapes:  Conform to UL 181A. Provide products bearing appropriate UL 181A markings.

- Do not provide sealing products not bearing UL approval markings.

Do not use pressure-sensitive sealant on ducts with a pressure class of 1 inch w.g. or greater.

DUCT LEAKAGE

*************************************************************************************************************

ASHRAE Standard 90.1 (Section 6.4.4.2.2) does require leakage testing for ducts designed to operate at static pressures in excess of 3 inches w.g. and all ductwork located outdoors.  The following is an example leakage test spec for duct pressure class (4 inches w.g.). Refer to SMACNA HVAC Air Duct Leakage Test Manual for other duct class leakage classification.  Note: It may be inadequate for nuclear facilities.

*************************************************************************************************************

Leak test ducts with a duct pressure class in excess of [4] inches w.g. (over 3 in. up to 4 in. w.g.).  Leak Test all ductwork located outdoors regardless of pressure class.

Perform leakage tests in accordance with the SMACNA HVAC Duct Leakage Test Manual using tests forms equivalent to those outlined in manual.

Disassemble, reassemble, and seal segments of systems to accommodate leakage testing and for compliance with test requirements.

Test for leaks before applying external insulation.

Conduct tests at static pressures equal to maximum design pressure of system or segment being tested. If static-pressure classes are not indicated, test system at maximum system design pressure. Do not pressurize systems above maximum design operating pressure.

Give [seven] <Insert number> days' advance notice for testing.

The entire duct system need not to be tested.  Tests may be made for only representative segments provided these segments represent at least 25 percent of the total installed duct area for the tested pressure class.

Maximum Allowable Leakage: Comply with the following requirements

- Leakage Classification [3] for round and flat oval ducts.

- Leakage Classification [6] for rectangular ducts.

Remake leaking joints and retest to ensure leakage is less than the minimum allowed.

END OF SECTION

****************************************************************

Do not delete the following reference information.

****************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification is based on LANL Master Specification Section 23 3101 Rev. 1, dated September 21, 2017.