section 23 4133.19

HEPA FILTERS – AUXILIARY NUCLEAR GRADE

************************************************************************************************************************

LANL MASTER SPECIFICATION SECTION

This section covers Auxiliary Nuclear Grade HEPA filters that include encapsulated filters with one or two end connections and other filter configuration not included in ASME AG-1, Sections FC or FK.  Those HEPA filters are covered in two other specification sections:

- Section 23 4133.13 HEPA Filters – ASME AG-1, Section FC that includes common sizes of square filters with flow rates of up to 2000 scfm.

- Section 23 4133.16 HEPA Filters – ASME AG-1, Section FK Special includes radial-flow filters, axial-flow circular filters, and axial-flow rectangular filters that are not included in Section FC.

Higher pressure, high efficiency filters for process piping (e.g., Swagelok) are addressed in Section 43 3113.37.

Edit this document so that it only includes the information pertaining to the type of HEPA filter being specified.  To seek a variance from applicable requirements, contact the ESM Mechanical POC.

When editing to a specific suit project, author shall add job-specific requirements and delete only those portions that in no way apply to the activity (e.g., a component that does not apply). When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General Requirements.

Information within “stars” is provided as guidance to the author responsible for revising the specification.  Delete information within “stars” during editing.  Information within [ ] needs to be edited for the specific project.  Some of this information starting and ending with “stars” is also guidance that needs to be removed during editing

This template was prepared by an organization operating under a quality assurance program that meets the requirements of 10 CFR 830 (suitable for ML-1 through ML-4 projects); however, it should only be used for ML-3 and -4 projects since, per DOE-STD-3020, these Auxiliary Nuclear Grade HEPA filters cannot be specified for Safety Class (ML-1) or Safety Significant (ML-2) applications without Field Office concurrence.

Implementation of this document requires modification to meet project-specific requirements; responsibility for this lies with the author.  The author shall apply a graded approach to quality assurance based on the management level designation of the project.  When this document is used with nuclear facilities subject to 10 CFR 830, modification to it must be performed by an individual or organization operating under a quality assurance program that meets the requirements of that CFR.

Attachment 1 is a list of Auxiliary Nuclear Grade HEPA filters that have been used at LANL and for which the included AAF|Flanders drawings and Camfil drawings have been sufficiently detailed so that they can be used as the basis for ordering these specific filters.

************************************************************************************************************************

general

Summary

Section Includes

Auxiliary nuclear grade HEPA filters and housings for ML-3 and ML-4 applications.

Related Sections

[Section 23 4133.13 HEPA Filters - ASME AG-1, Section FC]

[Section 23 4133.16 HEPA Filters - ASME AG-1, Section FK, Special]

Applicability

Filters to be installed in confinement ventilation systems for containing radioactive particles; their non-credited safety function and primary design characteristic is particle removal efficiency of at least 99.97 percent for 0.3 micrometer particles of an approved aerosol test.

Procurement and installation of HEPA filters for Department of Energy (DOE) facilities at Los Alamos National Laboratory.

Filters for use in air and gas streams with a 250 degrees F maximum continuous temperature.

References

Follow latest edition of all documents invoked herein (editions below reflect those used in the development of this template).

American Society of Mechanical Engineers (ASME).

ASME AG-1-2017, Code on Nuclear Air and Gas Treatment, Section FC, HEPA Filters

ASME AG-1-2017, Section FK, Special HEPA Filters

ASTM International (ASTM; formerly American Society for Testing and Materials)

ASTM A240/A240M-17, Standard Specification for Chromium and Chromium-Nickel Stainless Steel Plate, Sheet, and Strip for Pressure Vessels and for General Applications.

ASTM A269/A269M-15a, Standard Specification for Seamless and Welded Austenitic Stainless Steel Tubing for General Service.

ASTM A312/A312M-17, Standard Specification for Seamless, Welded, and Heavily Cold Worked Austenitic Stainless Steel Pipes.

ASTM A479/A479M-18, Standard Specification for Stainless Steel Bars and Shapes for Use in Boilers and Other Pressure Vessels, and for general application.

ASTM A492-95(2013), Standard Specification for Stainless Steel Rope Wire.

ASTM A554-16, Standard Specification for Welded Stainless Steel Mechanical Tubing.

ASTM A778/A778M-16, Standard Specification for Welded, Unannealed Austenitic Stainless Steel Tubular Products.

ASTM E2016-15, Standard Specification for Industrial Woven Wire Cloth

ASTM D2000-18, Standard Classification System for Rubber Products in Automotive Applications.

Institute of Environmental Sciences and Technology (IEST)

IEST-RP-CC001.6, HEPA and ULPA Filters.

International Organization for Standardization

ISO 9001:2015, Quality Management Systems Requirements.

Department of Energy (DOE)

DOE-STD-3020-2015, Specification for HEPA Filters Used by DOE Contractors.

DOE-HDBK-1169-2003, Nuclear Air Cleaning Handbook, Appendix A.

Underwriter Laboratories

UL-586, Standard for High Efficiency Particulate Air Filter Units.

Code of Federal Register

10 CFR 830.122, Quality Assurance Criteria.

40 CFR 261, Identification and Listing of Hazardous Waste.

Manufacturers Standardization Society

MSS SP-114 Corrosion Resistant Pipe Fittings Threaded and Socket Welding Class 150 and 1000.

Definitions, acronyms and abbreviations

Acceptance Test: Inspection and testing of a filter to verify certain characteristics or properties, which determine the acceptance or rejection of that filter.

Air Flow:  The volume of air through a system per unit of time, expressed as standard cubic feet per minute (scfm) or actual cubic feet per minute (acfm).

Approved Test Aerosol: Particle-generating materials approved by DOE and used as test aerosols for performing testing of HEPA filters.

ASME AG-1, Section FC HEPA Filters: Axial flow square open faced, fire resistant, HEPA filters used in nuclear air cleaning systems.

ASME AG-1, Section FK Special HEPA Filters:  Radial-flow, axial-flow circular open face, and axial-flow rectangular open face (not covered by Section FC), fire-resistant, HEPA filters used in nuclear air cleaning systems.

Auxiliary Nuclear Grade HEPA Filters: HEPA Filters that are not specifically addressed in ASME AG-1, Sections FC or FK.

CMTR: Certified Material Test Report

C of C: Certificate of Conformance

DOE:  Department of Energy

EPA: Environmental Protection Agency

Filter Test Facility (FTF): A facility established by the DOE specifically to conduct performance tests and quality assurance inspections of HEPA filters.

High Efficiency Particulate Air (HEPA) Filter: A filter with a particle removal efficiency of at least 99.97 percent for 0.3 micrometer particles of an approved aerosol test.

LANL: Los Alamos National Laboratory

Nominal Air Flow Rating: The flow rate which HEPA filters are identified by the manufacturer and confirmed at the FTF.

NPT: National Pipe Thread

Nuclear Facility: A DOE facility in which radioactive materials are produced or handled to the degree that environmental protection is required.

Penetration: The downstream test aerosol concentration, expressed as a percentage of the upstream test aerosol concentration.

PTFE: Polytetrafluoroethylene

QA: Quality Assurance

Qualification Test: A test, often destructive, of a prototype or randomly selected production filter to establish its capability to meet certain functional and specification requirements.  The results of the test are considered to be typical of individual items or model number, which are of the same design and are manufactured by the same process.

SST: Stainless steel

wg:  water gage

LANL- PERFORMED WORK

LANL will do in-place leakage testing of HEPA filter(s) after successful installation in systems required to be tested.

LANL will perform receipt inspection on filters ordered by LANL organizations in accordance with LANL Form 1952-listed requirements.

DESIGN REQUIREMENTS

*************************************************************************************************************

Auxiliary Nuclear Grade HEPA filters cannot be specified for Safety Class (ML-1) or Safety Significant (ML-2) applications.

Edit Design Requirements as necessary and add additional criteria as needed.  Be sure to specify the following:

- Pressure differential at specified flow rate

- Housing leak tightness

- End fittings

- Overall dimensions

Attachment 1 lists Auxiliary Nuclear Grade HEPA filters that have been used at LANL. (The drawings are posted on the LANL internal web as a Div 23 reference under this section.)  If using a filter from this list, just specify the Manufacturer’s Drawing Number (including Rev. where present) instead of filling in the information requested in Article 1.5, paragraphs D–K below.  If the filter needed does not exactly match one of those shown, then fill in the information in D–K.

*************************************************************************************************************

Particle removal efficiency of 99.97 percent for 0.3 micrometers or better of an approved test aerosol.

Manufacture using materials and methods of construction consistent with filters that have passed wet-overpressure testing (per ASME AG-1, Article FC-5140) when tested in a rectangular, open-face configuration.

[Filter will meet specifications called out in the following Drawing(s):]

- [Camfil Drawing Number 508450 Rev A] [with mark-ups]

- [AAF|Flanders Drawing Number Z02083B] [with mark-ups]

- [AAF|Flanders Drawing Number Z93555G] [with mark-ups]

- [AAF|Flanders Drawing Number Z08211] [with mark-ups]

- [AAF|Flanders Drawing Number Z99436M] [with mark-ups]

- [AAF|Flanders Drawing Number Z03257D] [with mark-ups]

- [AAF|Flanders Drawing Number Z03258B] [with mark-ups]

- [AAF|Flanders Drawing Number Z03255] [with mark-ups]

- [AAF|Flanders Drawing Number Z03232C] [with mark-ups]

- [AAF|Flanders Drawing Number Z83138M] [with mark-ups]

- [AAF|Flanders Drawing Number Z96687B] [with mark-ups]

- [AAF|Flanders Drawing Number Z18080A] [with mark-ups]

[OR INCLUDE ALL OF THE FOLLOWING]

[Pressure differential of less than or equal to [       ] in. of water gauge at a flow rate of [       ] scfm.]

[***specify housing materials***]

[***specify filter pack type (separator (with or without coating) or separatorless)***]

[***specify pack to frame sealant***]

[***specify end connections***].

[***specify overall dimensions***].

[***specify if and where faceguards are installed and what material is used***]

[***specify leak tightness of housing and test method to use if one or both ends have end connection***]

ACTION Submittals

*************************************************************************************************************

Submittal of QA plan is not necessary if filter manufacturer is on the current LANL IESL (internal IQPA web site).

The submittals as listed are required for ML-3 HEPA filters.  For ML-4 HEPA filters, the submittals listed may be edited to include fewer requirements.

Consider requiring CMTRs for materials used in pressure boundaries of custom-fabricated Auxiliary Nuclear Grade HEPA filter housings.

*************************************************************************************************************

Submittals from the Filter Manufacturer

      - Certified performance test results by the manufacturer for aerosol penetration and airflow resistance.  Test results are to be identified for each filter by serial number.

      - [Copy of the HEPA filter manufacturer’s QA plan identifying procurement, fabrication, test & inspection, material traceability and non-conformity controls for approval.]

      - Documentation showing that the filter meets the design requirements of Article 1.5, including material requirements of Article 2.3.  Examples of such documents include supplier performance test information, inspection reports, drawings, etc.

      - Certification that all custom-built filter housings are fabricated and leak tested to meet the requirements of this Section.  Examples of such documents include inspection and leak test procedures and reports.

      - Certificate of Conformance (C of C) that is signed or otherwise authenticated by an authorized individual certifying the degree to which items or services meet specified requirements. (Paraphrased from definition in ASME AG-1, Article AA-1400.)

The C of C shall include:

Purchase Order (PO) number

Purchased item identified by model number.

The serial numbers of all filters included in the shipment to which the C of C is applicable.

Any approved changes, waivers, or deviations from this Section.

Statement indicating that filters meet the following requirements:

        - The filters and filter media have been designed, manufactured, and constructed in accordance with manufacturer’s QA plan and Article 1.7.

        - Filter construction and dimensions are per referenced drawings and/or Article 1.5.

        - Acceptance test Reports submitted above are applicable to the items delivered, and (if necessary) cross referenced by serial number and any other item identifier.

        - [Gaskets shall be glued firmly and continuously to the case (when applicable).]

************************************************************************************************************* The following statement regarding case panels only applies to rectangular filters with a metal case.  It is included here to meet guidance in DOE-HDBK-1169-2003, Appendix B.

*************************************************************************************************************

        - [Case panels have been assembled into the frame by potting a sub-assembly consisting of the filter pack and side panels into the top and bottom panels (but not corners) using adhesive meeting the requirements of DOE-STD-3020-2015.]

        - Certification of compliance with UL-586 and appropriate label applied to filter case, as evidence of compliance with requirements for resistance to flame and heated air.

Warranty documentation – guarantee against failure in proper use or operation caused by defective materials and/or workmanship for a period of one year from the date of acceptance at LANL.

*************************************************************************************************************Most Auxiliary Nuclear Grade HEPA filters do not need to be sent to the FTF so the following requirement is normally deleted.

*************************************************************************************************************

[Submittals from the FTF]

      - [Certified performance test results by the FTF for aerosol penetration and airflow resistance.  Test results are identified for each filter by serial number.]

quality assurance

Seller’s Quality Assurance Requirements

Develop, implement, and maintain an approved QA system (including program/plan, procedures, and process control documents) in accordance with 10 CFR 830.122.  If the seller’s QA plan is not in accordance with 10 CFR 830.122, then a LANL-approved QA plan based on appropriate industry consensus standards such as ISO 9001 is acceptable.

Packaging and shipping

Package and ship filters in accordance with Article FK-7000, DOE-STD-3020-2015 (Sections 7.2 and 7.3), and:

Place filter cartons in a sturdy wooden crate with the lid/top secured with removable screws or lag bolts to eliminate unit handling at carrier inter change points and avoid unnecessary damage.  Shipping crates shall be labeled in accordance with Article FK-9200.

Do not stack HEPA filters with a height dimension of 24 inches or greater more than three high.  It is acceptable to stack filters more than three high, if the individual filter does not exceed 24 inches in size, but the stacked height cannot exceed 6 ½ feet.

Ship filters properly oriented, in accordance with manufacturer’s recommendation.

For large shipments, ship the entire shipment in a sealed dedicated trailer to provide an additional quality assurance of product shipping and handling.

Filters returned to the manufacturer from the FTF or shipped from the FTF to LANL must be re-packaged per the above requirements.

products

*************************************************************************************************************

ASME AG-1, Sections FC and FK HEPA filters are designed specifically for use in nuclear facilities.  For Auxiliary Nuclear Grade HEPA filters, consider filter environment when selecting acceptable materials.  Example: PTFE may not be an acceptable material for a radiation environment.  Also note, the listing of materials for Auxiliary Nuclear Grade HEPA filters is not a complete list of all possible materials; others may be acceptable.  Again, carefully consider the environment (corrosion, radiation, etc.) in which the filter will be operating.

*************************************************************************************************************

product options and substitutions

No substitutions allowed.

manufacturers

The following is a list of some of the manufacturers that produce nuclear grade HEPA filter products that may meet the requirements of this Section.  However, these manufacturers are not exempt from any seller requirements.

AAF International (American Air Filter)

AAF|Flanders

Camfil Inc.

Materials of construction

General

The following are unacceptable materials of construction:  particle board, asbestos, cadmium-coated metals, and any material that generates EPA regulated wastes as specified in 40 CFR 261.

Filter Media

Manufacture silicate media in accordance with Article I-3000 of ASME AG-1, Appendix FC-I.

[Separatorless filter packs shall use formed media to fulfill the function of the separator.]

Housing

[Type 300 series stainless steel, minimum 14 gauge, conforming to ASTM A240, ASTM A269, ASTM A554, or ASTM A778.]

[OR]

[Type 409 stainless steel, minimum 14 gauge, conforming to ASTM A240.]

[OR]

[Plywood, 3/4 in. thick in accordance with DOE-STD-3020-2015 (Section 5.3.2).]

[Fittings conforming to MSS SP-114, ASTM A312, or ASTM A479.]

[Fasteners (when used)]

[Use fasteners that are in accordance with DOE-STD-3020-2015 (Section 5.3.7).]

*************************************************************************************************************

Select only one type of separator per filter type.

*************************************************************************************************************

[Separators (when used)]

[Aluminum, conforming to ASME AG-1, Article FC-3160, (a).]

[OR]

[Acid Resistant Aluminum, conforming to ASME AG-1, Article FC-3160, (b).]

[OR]

[Glass Ribbon, conforming to ASME AG-1, Article FC-3160, (c).]

[OR]

[String, conforming to ASME AG-1, Article FC-3160, (d).]

[OR]

[Hot Melt, conforming to ASME AG-1, Article FK-3160, (e).]

************************************************************************************************************* A single splice is allowed only for radial flow filters.  Axial flow filters are not allowed to have splices.

*************************************************************************************************************

Adhesives used to [splice the media,] fasten gaskets to filter case, and seal the filter pack or faceguards to the case

Self-extinguishing in accordance with the spot-flame test of ASME 
AG-1, Article FC-5160 or UL-586.

Gaskets and Seals

[Elastomer Gasket – in accordance with DOE-STD-3020-2015 (Section 5.3.5.1).]

[OR]

[Gelatinous Seal – in accordance with DOE-STD-3020-2015 (Section 5.3.5.2).]

[OR]

[Elastomer Gasket – Viton in accordance with ASTM D2000]

[Faceguards (when used)]

[Faceguards – galvanized steel in accordance with ASME AG-1, Article FC-3140.]

[OR FOR HIGHLY-CORROSIVE ATMOSPHERES]

[Faceguards - 4 x 4 mesh made from 0.025 in. minimum Type 304 stainless steel in accordance with ASTM E2016.]

*************************************************************************************************************Wire rope handle is only used on the AAF|Flanders drawing number Z96687 filter.

*************************************************************************************************************

[Handle]

[Wire rope - minimum 1/8” diameter, fabricated from wire conforming to ASTM A492.]

Fabrication

*************************************************************************************************************

Add additional fabrication requirements as necessary, such as welding.  Be sure to specify leak tightness and end connections for Auxiliary Nuclear Grade Filters.

*************************************************************************************************************

General

Fabricate in accordance with manufacturer’s approved QA plan.

Assemble filter from materials designated in Article 2.3.

Do not patch holes or tears in filter media.

Ensure that filter is free from foreign matter and damage.

Fabricate housing to [***specify leak tightness or reference attached drawings that include leak tightness***].

Provide [***specify end connections or reference attached drawings that detail the end connection(s)***].

Label each filter with the following minimum information.  Labels must be permanently affixed to the filter.

  - Manufacture’s name or symbol

  - Model number

  - Serial number

  - Rated flow capacity

  - Direction of airflow for penetration and pressure drop tests (except for radial flow filters)

  - Pressure drop, in inches of water at 100% rated flow

  - Overall penetration at rated flow

  - UL label indicating successful testing per UL-586 (if applicable).

  - Date of manufacture

  - Date the filter was tested

  - The effective media area

Label each shipping container (carton containing one filter) with the following minimum information:

Manufacturer’s name

Arrows and “THIS SIDE UP” indicating orientation for shipping and storage, and “FRAGILE” in letters no less than 3/8 in.

Filter model number

Purchase order number

*************************************************************************************************************As of the date of this template, the wire rope handle is only used on AAF|Flanders drawing number Z96687 filters.

*************************************************************************************************************

[Install wire rope handle on the outlet side of filter.]

Acceptance testing

Acceptance Test Criteria

- Filters shall be manufactured using materials and methods of construction consistent with filters qualified to ASME AG-1, Article FC-5000 or to ASME AG-1, Article FK-5000.

- Perform factory production testing in the following categories:

- Penetration – Test with DOE- approved aerosol and test method or the particle counter scanning method as described in IEST-RP-CC001.6 (or latest revision).  If penetration of 0.3 micrometers exceeds 0.03 percent, filter is not acceptable.

- Resistance to airflow – The clean filter resistance to airflow shall meet the requirements of Article 1.5.

*************************************************************************************************************
Leak testing is only required for filters with end plates and nipple or flanged connections.
*************************************************************************************************************

- [Leak testing – Perform a pressure decay leak test of the filter housings that have a nipple connection on [one end] [both ends] per ASME AG-1-2017, Mandatory Appendix TA-III at a pressure of [+ 10]” w.g.  Maximum acceptable leakage rate is 0.0005 SCFM per cubic foot of housing volume.]

*************************************************************************************************************Most Auxiliary Nuclear Grade HEPA filters do not need to be sent to the FTF so the following requirement is normally deleted.  However, the end user can always request that their filters are sent to the FTF to better ensure the quality of the product they receive.

*************************************************************************************************************

- [Ship filters to the FTF (Air Techniques International Testing Laboratories, Suite 104, 1708 Whitehead Rd., Baltimore, MD 21207, phone 410-277-8981, fax 410-277-3448, email ATITL@atitest.com) to have inspection and performance acceptance testing performed in accordance with ASME AG-1, Article FK-5600 and DOE-STD-3020-2015.]

execution (performed by AND AT lanl)

Examination

    - Inspect all filters upon shipment receipt to the requirements contained on LANL Form 1952. Verify documentation from Article 1.6 is included and is complete.

Storage

- Store filters in accordance with DOE-HDBK-1169, Appendix A, or in accordance with the manufacturer’s requirements, whichever is more restrictive and:

  - Do not stack HEPA filters with a height dimension of 24 inches or greater more than three high.  It is acceptable to stack filters more than 3 high if the individual filter does not exceed 24 inches in size, but the stacked height cannot exceed 6 ½ feet.

  - Store filters properly oriented, in accordance with manufacturer’s recommendations.

  - Alternate the position of each level so as to not have one filter support the one above it when stored out of the shipping container.

  - Shelf life: Do not store filters for more than 10 years after manufacture date.

Handling and installation

- Handle and install HEPA filters in accordance with DOE-HDBK-1169, Appendix A, Parts A.5 and A.6.

Field Quality control

- Test filters (when required) after installation for leakage in accordance with LANL requirements.

- Replace all filters that fail the LANL in-place leakage test.

- Notify Seller, Purchasing Group, and Quality Assurance Group of filter rejections and re-evaluate the future procurement status of that manufacturer and/or model.

Attachment

*************************************************************************************************************Edit Attachment 1 to remove all of the filter types and the associated drawings in the list that are not needed.  Mark-up drawings as necessary to indicate changes needed.  Some drawings have already been marked-up to include necessary information to ensure the filter is as close to an ASME AG-1, Section FC or Section FK filter as possible.  When they become available, drawings that have been updated by the manufacturer to include the LANL mark-ups should be referenced and used. The drawings are posted on the LANL internal web as a reference under this Div 23 section.

*************************************************************************************************************

Attachment 1 - Auxiliary Nuclear Grade HEPA Filters

end of section MAIN BODY

*********************************************************

Do not delete the following reference information:

*********************************************************

THIS STATEMENT FOR lanl use only

This project specification section is based on LANL Master Specification Section 23 4133.19 Rev. 0, dated December 12, 2018.

ATTACHMENT 1

Auxiliary Nuclear Grade HEPA Filters

Caution:  These drawings contain proprietary information, are for LANL business purposes, and must not be shared with competing manufacturers.

| Item | M/N | Description | Drawing |
| --- | --- | --- | --- |
| Camfil |
| A | 02ES-08Z08Z09-00-2-F-M-AU-B/NC | 8 inch square, 14 gauge, 304 SST housing, aluminum separators, open inlet with SST faceguard, 3 inch KERKAU Class 150 RF, 316L flange on outlet | 508450 Rev A with mark-ups |
| AAF¦Flanders |
| B | 0-007-C-15-R0-NU-00-00-Z02083B | 4 inch round, 316 SST housing, aluminum separators, open inlet and outlet. For use in glovebox exhaust push-thru housing | Z02083 Rev B with mark-ups |
| C | 0-007-D-43-R0-NU-00-00-Z93555G | 8 inch round, 304 SST housing, separatorless filter pack, open inlet and outlet. For use in glovebox exhaust push-thru housing | Z93555 Rev G with mark-ups |
| D | 0-007-U-43-R0-NU-00-00-Z08211 | 12 inch round, 304 SST housing, separatorless filter pack open inlet and outlet. For use in glovebox exhaust push-thru housing | Z08211 with mark-ups |
| E | 0-007-C-15-N1-NU-00-21-Z99436M | 4 inch round, 316L SST housing, aluminum separators, open inlet with SST faceguard, 2” MNPT x 1-1/2” FNPT 316 SST class 150 pipe bushing on outlet | Z99436 Rev M with mark-ups |
| F | 0-007-C-15-N1-NU-00-00-Z03257D | 4 inch round, 316L SST housing, aluminum separators, open inlet, 1-1/2” MNPT x 1-1/4” FNPT 316 SST class 150 pipe bushing on outlet | Z03257 Rev D with mark-ups |
| G | 0-007-C-15-N1-NU-00-00-Z03258B | 4 inch round, 316L SST housing, aluminum separators open inlet, 1” MNPT x 3/4" FNPT 316 SST class 150 pipe bushing on outlet | Z03258 Rev B with mark-ups |
| H | 0-007-D-03-N1-NU-00-21-Z03255 | 6 inch round, 304 SST housing, separatorless filter pack, open inlet with SST faceguard, 2” MNPT x 1-1/2” FNPT 304 SST class 150 pipe bushing on outlet | Z03255 with mark-ups |
| I | 0-007-D-03-N2-NU-00-00-Z03232C | 4 inch round, 304 SST housing, separatorless filter pack, 1” MNPT x ¾” FNPT 304 SST class 150 pipe bushing on inlet and outlet | Z03232 Rev C with mark-ups |
| J | 0-007-D-04-N1-NU-00-11-Z83138M | 8 inch square, plywood housing, separatorless filter pack, open inlet with galvanized faceguard, 2” IPS SCH 40 MNPT 304 SST pipe nipple on outlet | Z83138 Rev M with mark-ups |
| K | X-007-8-42-01-NU-13-13-Z96687B | 12-1/2” square, 409 SST metal case, separatorless filter pack. 14” square flange on outlet with gaskets on both sides of the flange face. Galvanized faceguards on each face | Z96687 Rev B with mark-ups |
| L | B-007-D-43-RX-NU-X2-23-Z18080A | 8 inch round, 304 SST housing, separatorless filter pack, open inlet with SST faceguard and lifting bail, ½ inch wide inside flange on outlet with SST faceguard. (For use in RLUOB open front box exhaust.) | Z18080 Rev A with mark-ups |