SECTION 23 6200

PACKAGED COMPRESSOR AND CONDENSER UNITS

*************************************************************************************

LANL MASTER SPECIFICATION

This template must be edited for each project.   In doing so, specifier must add job-specific requirements.  Brackets are sometimes used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Mechanical POC.  Please contact the POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

This master was developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

*************************************************************************************

GENERAL

SUMMARY

Section includes air-cooled, packaged refrigerant compressor and condenser units, suitable for [on-the-ground] [or] [rooftop] installation.

PERFORMANCE REQUIREMENTS

- Compressor, condenser units, and associated motors shall perform satisfactorily in the following service conditions:

      - Elevation: 7500 feet above sea level.

      - Maximum ambient temperature: 104 degrees F.

      - Minimum ambient temperature: -20 degrees F.

      - 24-hour average temperature: not exceeding 86 degrees F.

      - Maximum solar heat gain: 110 W/sq ft.

- Supplier-provided control systems, including instruments, signal transmissions, panels, cabinets, and other instrumentation and control requirements shall be coordinated with the I&C Subcontractor and in accordance with Section 25 5000, “Integrated Automated Facility Controls”.  Some equipment controls are specified in other portions of the subcontract documents.  As part of the work of this section, coordinate with these other suppliers and trades to provide a complete and working equipment controls.

- It is the responsibility of the bidder to read and conform to all sections of the specifications, review all subcontract drawings of all divisions, and coordinate with all equipment suppliers of material specified under other sections of the specifications.

- Seismic Protection and Performance:  The seismic protection and performance of air-cooled packaged compressor and condenser units shall be in accordance with Section 22 0548, Vibration and Seismic Controls for Plumbing Piping and Equipment.

*******************************************************************************************

Retain paragraph below if Subcontractor is required to assume responsibility for the design.

*******************************************************************************************

- Delegated Design:  Design vibration isolation and seismic-restraint details, including comprehensive engineering analysis by a professional engineer licensed in the State of NM, using performance requirements and design criteria indicated.

REFERENCES (Conformance to Codes and Standards as Applicable to Project)

Air-Conditioning, Heating and Refrigeration Institute (AHRI)

AHRI 210/240 – Performance Rating of Unitary Air-Conditioning and Air-Source Heat Pump Equipment.

AHRI 270 – Sound Rating of Outdoor Unitary Equipment.

AHRI 340/360 – Performance Rating of Commercial and Industrial Unitary Air-Conditioning and Heat Pump Equipment.

AHRI 365 – Commercial and Industrial Unitary Air-Conditioning Condensing Units.

AHRI 370 – Sound Rating of Large Outdoor Refrigerating and Air-Conditioning Equipment.

AHRI 460 – Performance Rating of Remote Mechanical-Draft Air-Cooled Refrigerant Condensers.

American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE)

- ASHRAE 15 – Safety Standard for Mechanical Refrigeration.

- ASHRAE 20 – Method of Testing for Rating Remote Mechanical-Draft Air-Cooled Refrigerant Condensers.

- ASHRAE 23 – Methods of Testing for Rating Positive Displacement Refrigerant Compressors and Condensing Units.

- ASHRAE 90.1 – Energy Standard for Buildings Except Low-Rise Residential Buildings.

National Electrical Manufacturers Association (NEMA)

NEMA 250 – Enclosures for Electrical Equipment (1000 Volts Maximum).

National Fire Protection Association (NFPA)

NFPA 70 – National Electric Code.

Underwriters Laboratories Inc. (UL)

UL 207 – Refrigerant-Containing Components and Accessories, Nonelectrical.

UL 1995 – Heating and Cooling Equipment.

SUBMITTALS

Product Data:  For each air-cooled packaged compressor and condenser unit, include rated capacities, operating characteristics, furnished specialties, and accessories.

Shop Drawings:  Indicate components, assembly, dimensions, weights and loading, required clearances, location and size of field connections, electrical requirements, and wiring diagrams for power, signal and control wiring.  Include schematic layouts showing condenser, refrigeration compressors, cooling coils, refrigerant piping and accessories required for complete system.  Include plans, elevations, sections, details, and attachments to other work.

Manufacturer's Installation Instructions.

- Operation and Maintenance Data:  Submit instructions for lubrication, filter replacement, motor and drive replacement, spare parts lists, and wiring diagrams.

***************************************************************************************************

Provide LEED submittals only if the project is pursuing LEED certification.

***************************************************************************************************

        - LEED Submittals:

Product Data for Prerequisite EA 2:  Documentation indicating that units comply with applicable requirements in ASHRAE/IESNA 90.1.

Product Data for Credit EA 4:  Documentation indicating that compressor and condenser units and refrigerants comply.

****************************************************************************************************

Retain if Work of this Section is required to withstand specific design loads and design responsibilities have been delegated to Subcontractor or if structural data are required as another way to verify compliance with performance requirements.

****************************************************************************************************

    - Delegated-Design Submittal:  For vibration isolation and seismic restraints indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the NM licensed professional engineer responsible for their preparation.

      - Vibration Isolation Base Details:  Installation details including anchorages and attachments to structure and to supported equipment.  Include auxiliary motor slides and rails and equipment mounting frames.

      - Design Calculations:  Calculate requirements for selecting vibration isolators and seismic restraints, and for designing vibration isolation bases.

QUALITY ASSURANCE

Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, and any nationally recognized testing laboratory (NRTL), and marked for intended location and application.

Fabricate and label refrigeration system according to ASHRAE 15, "Safety Standard for Refrigeration Systems."

Performance Ratings:  Seasonal Energy Efficiency Ratio (SEER) not less than prescribed by ASHRAE 90.1, Section 6, "Heating, Ventilating, and Air-Conditioning.”

WARRANTY

The equipment manufacturer shall provide, at no additional cost, a standard parts warranty in which manufacturer agrees to repair or replace components of compressor and condenser units that fail in materials or workmanship within the warranty period.

Failures include, but are not limited to, the following:

Compressor failure.

Condenser coil leak.

PRODUCTS

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

Manufacturer must clearly define any exceptions made to Plans and Specifications.  Any deviations in layout or arrangement shall be submitted to LANL Engineering Services prior to bid date.  Acceptance of deviation(s) from specifications shall be in the form of written approval from LANL Engineering Services.  Vendor is responsible for expenses that occur due to exceptions made.

Compressor and Condenser Units, Air Cooled (1 To 5 Tons)

Manufacturers:

Carrier Corporation; Commercial HVAC Systems.

Lennox International Inc.

Trane; a business of American Standard Companies.

York; a Johnson Controls company.

Description:  Packaged, factory assembled and tested, suitable for outdoor use; consisting of casing, compressors, condenser coils, condenser fans and motors, and unit controls.

Unit Casing:  Galvanized steel finished with baked enamel; with removable panels for access to controls, weep holes for water drainage, and mounting holes in base.  Mount service valves, fittings, and gage ports on exterior of casing.  Meet salt spray test in accordance with ASTM B117.

Nonfused disconnect switch, factory mounted and wired, for single external electrical power connection.

Compressor:  Scroll, hermetically sealed, with rubber vibration isolators.

Motor:  [Single] [Two] speed, and includes thermal- and current-sensitive overload devices, start capacitor, relay, and contactor.

Two-Speed Compressor:  Include manual-reset, high-pressure switch and automatic-reset, low-pressure switch.

Refrigerant:  R-410A [or] [R-407C].

Condenser Coil:  Seamless copper-tube, aluminum-fin coil; circuited for integral liquid subcooler, with removable drain pan and brass service valves with service ports.

Condenser Fan:  Direct-drive, aluminum propeller fan; with permanently lubricated ball bearings, totally enclosed fan cooled motor with thermal-overload protection.

Accessories:

*******************************************************************************************

Select one or more of the following subparagraphs appropriate to equipment requirements.

*******************************************************************************************

Cycle Protector:  Automatic-reset timer to prevent rapid compressor cycling.

Electronic programmable thermostat to control compressor and condenser unit and evaporator fan.

Evaporator Freeze Thermostat:  Temperature-actuated switch that stops unit when evaporator reaches freezing temperature.

Crankcase heater.

Filter-dryer.

High-Pressure Switch:  Automatic-reset switch cycles compressor off on high refrigerant pressure.

Liquid-line solenoid.

Low-Ambient Controller:  Cycles condenser fan to permit operation down to 0 degrees F ambient temperature.

Low-Pressure Switch:  Automatic-reset switch cycles compressor off on low refrigerant pressure.

Precharged and insulated suction and liquid tubing.

Sound Hood:  Wraps around sound attenuation cover for compressor.

Thermostatic expansion valve.

Time-Delay Relay:  Continues operation of evaporator fan after compressor shuts off.

Condenser coil hail guard.

Compressor and Condenser Units, Air Cooled, 6 to 120 Tons

Manufacturers

Carrier Corporation; Commercial HVAC Systems.

Dunham-Bush, Inc.

Engineered Air.

Lennox International Inc.

McQuay International.

Trane; a business of American Standard Companies.

YORK; a Johnson Controls company.

Product Description:  Packaged, factory assembled and tested, suitable for outdoor use; consisting of casing, compressors, condenser coils, condenser fans and motors, and unit controls.

Unit Casings:  Steel, galvanized or zinc coated, for exposed casing surfaces; treated and finished with manufacturer's standard paint coating.  Provide removable panels for access to compressors, controls, condenser fans, motors, and drives.  Meet salt spray test in accordance with ASTM B117.  Additional features include the following:

Perimeter base rail with forklift slots and lifting holes to facilitate rigging.

Gasketed control panel door.

Nonfused disconnect switch, factory mounted and wired, for single external electrical power connection.

Condenser coil hail guard.

Compressor:  Hermetic scroll compressor [Hermetic or semi-hermetic rotary screw compressor] designed for service with crankcase sight glass, crankcase heater, and backseating service access valves on suction and discharge ports.

Capacity Control:  [On-off compressor cycling] [Hot-gas bypass] [Variable-frequency controller] [Modulating slide-valve assembly or port unloaders].

Refrigerant:  R-410A [or] [R-407C].

Condenser Coil:  Seamless copper-tube, aluminum-fin coil, including subcooling circuit and backseating liquid-line service access valve.  Factory pressure test condenser coils and dehydrate by drawing a vacuum and fill with a holding charge of nitrogen or refrigerant.

Condenser Fan:  Propeller-type vertical discharge; either directly or belt driven.  Dynamically and statically balanced fan assemblies.  Permanently lubricated, ball-bearing totally enclosed fan cooled motors.

Accessories:

*******************************************************************************************

Select one or more of the following subparagraphs appropriate to equipment requirements.

*******************************************************************************************

Electronic programmable thermostat to control compressor and condenser unit and evaporator fan.

Low-Ambient Controller:  Cycles condenser fan to permit operation down to 0 degrees F ambient temperature.

Gage Panel:  Package with refrigerant circuit suction and discharge gages.

Hot-gas bypass kit.

Part-winding-start timing relay, circuit breakers, and contactors.

Operating and safety controls include the following:

Manual-reset, high-pressure cutout switches.

Automatic-reset, low-pressure cutout switches.

Low-oil-pressure cutout switch.

Compressor-winding thermostat cutout switch.

Three-leg, compressor-overload protection.

Control transformer.

Magnetic contactors for compressor and condenser fan motors.

Timer to prevent excessive compressor cycling.

CONTROLS

Factory wired and mounted control panel, NEMA 250 Type [1] [4] [     ] enclosure, containing fan motor starters, compressor interlock and control transformer [fan cycling thermostats,] [head pressure controls].

See Article 1.2 for Control Requirements.

        - Refer to Section 25 5000, “Integrated Automated Facility Controls”.  All necessary controls shall be factory installed and wired.

        - Evaporator defrost control shall be included to prevent compressor slugging by temporarily interrupting compressor operation when low evaporator coil temperatures are encountered.

SOURCE QUALITY CONTROL

Testing Requirements:  Factory test sound-power-level ratings according to [ARI 270] [ARI 370].

Pressure test condenser coils at a minimum of 480 psig.

***************************************************************************************************

Retain "Energy Efficiency" Paragraph below for compliance with ASHRAE/IESNA 90.1.  LEED Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1.

***************************************************************************************************

Energy Efficiency:  Equal to or greater than prescribed by ASHRAE/IESNA 90.1, "Energy Efficient Design of New Buildings except Low-Rise Residential Buildings," Section 6, "Heating, Ventilating, and Air-Conditioning."

EXECUTION

EXAMINATION

Examine rough-in for refrigerant piping systems to verify actual locations of piping connections before equipment installation.

Examine condition of locations where the packaged compressor and condenser unit will be installed.

Proceed with installation only after unsatisfactory conditions have been corrected.

INSTALLATION

Comply with ASHRAE 15 procedures for charging and purging of systems and for disposal of refrigerant.

Install packaged units level and plumb, firmly anchored in locations indicated; and maintain manufacturer's recommended clearances for service and maintenance.

Furnish vibration isolators as required or as shown on the drawings.  Vibration isolation devices and installation requirements are specified in Section 22 0548, “Vibration and Seismic Control for Plumbing Piping and Equipment”.

***************************************************************************************************

Retain paragraph below for compressor and condenser units mounted on concrete base/housekeeping pad.

***************************************************************************************************

Concrete Bases:

          - For equipment supported on concrete pad, install anchor bolts according to anchor-bolt manufacturer's written instructions.

          - Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

          - Install anchor bolts to elevations required for proper attachment to supported equipment.

          - Provide and install per Section 22 0548, Vibration and Seismic Controls for Plumbing Piping and Equipment.

CONNECTIONS

Install refrigerant piping and refrigerant specialties (pressure relief, service valve, filter-dryer, and moisture indicator on each refrigerant-circuit liquid line) in accordance with Section 23 2300, Refrigerant Piping.

Where installing piping adjacent to equipment, allow space for service and maintenance of equipment.

Connect precharged refrigerant tubing to unit's quick-connect fittings.  Install tubing so it does not interfere with access to unit.  Install furnished accessories.

Install electrical components, devices, and accessories and connection to electrical power wiring that are not factory mounted.

FIELD QUALITY CONTROL

Perform field tests and inspections and prepare test reports.

Tests and Inspections:

Perform each visual and mechanical inspection and electrical test.  Certify compliance with test parameters.

Leak Test:  After installation, charge system with refrigerant and oil and test for leaks.  Repair leaks, replace lost refrigerant and oil, and retest until no leaks exist.

Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor operation and unit operation, product capability, and compliance with requirements.

Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

Verify proper airflow over coils.

Verify that vibration isolation and flexible connections properly dampen vibration transmission to structure.

STARTUP SERVICE

Complete installation and startup checks according to manufacturer's written instructions and perform the following:

          - Inspect for physical damage to unit casing.

          - Verify that access doors move freely and are weathertight.

          - Clean units and inspect for construction debris.

          - Verify that all bolts and screws are tight.

          - Adjust vibration isolation and flexible connections.

      - Verify that controls are connected and operational.

    - Lubricate bearings on fans.

Verify that fan wheel is rotating in the correct direction and is not vibrating or binding.

Start unit according to manufacturer's written instructions and complete manufacturer's startup checklist.

Measure and record airflow over coils.

Verify proper operation of capacity control device.

Verify that vibration isolation and flexible connections properly dampen vibration transmission to structure.

    - After startup and performance test, lubricate bearings.

SCHEDULE

***************************************************************************************************

As a minimum, the following information and performance characteristics shall be shown on the drawings as part of the equipment schedule.

***************************************************************************************************

Capacities and Characteristics:

Compressor and Condenser Unit:

Full-Load Cooling Capacity, MBh

Compressor Suction Temperature,  F

Capacity Steps

Seasonal Energy-Efficiency Ratio (SEER)

Refrigerant Connections:

Liquid Pipe Size

Suction Pipe Size

Compressors:

Number of Compressors

Rated-Load Amperes

Power Input, kW

Air-Cooled Condenser:

Ambient-Air Temperature,  F

Airflow, cfm

Number of Condenser Fans

Condenser Fan Motor Size, HP

Electrical Characteristics:

Kilowatt Input

Volts, single or three phase, 60 Hz.

Maximum Circuit Amperes

END OF SECTION 23 6200

****************************************************************

Do not delete the following reference information.

****************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 23 6200 Rev. 0, dated 
July 20, 2010.