Section 26 0519 
Low Voltage Electrical Power Conductors and Cables

  - ************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 9 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Electrical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable specification sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality Sections.

  - ************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

      - ***************************************************************************************

      - The following paragraphs are designer-choice based on project-specific requirements.

      - ***************************************************************************************

Building wire (600 V).

Metal-clad cable (600 V).

Wire and cable connectors.

Insulating tape and tubing.

Wire pulling lubricant.

Related Requirements

Section << 01 2500 - Substitution Procedures>>​

Section << 01 4000 - Quality Requirements - Non-Nuclear>>​

Section << 26 0813 - Electrical Acceptance Testing>>​

Section << 26 0533 - Raceways and Boxes for Electrical Systems>>

REFERENCE standards

ASTM B3 - Standard Specification for Soft or Annealed Copper Wire.

ASTM B800 - Standard Specification for 8000 Series Aluminum Alloy Wire for Electrical Purposes - Annealed and Intermediate Tempers.

ASTM B801 - Standard Specification for Concentric-Lay-Stranded Conductors of 8000 Series Aluminum Alloy for Subsequent Covering or Insulation.

ASTM D3005 - Standard Specification for Low-Temperature Resistant Vinyl Chloride Plastic Pressure-Sensitive Electrical Insulating Tape.

NECA / NEIS 120 - Standard for Installing Armored Cable (AC) and Metal-Clad Cable (MC).

NECA 1 - Standard for Good Workmanship in Electrical Construction.

NECA 104 - Standard for Installing Aluminum Building Wire and Cable.

NETA ATS - Standard for Acceptance Testing Specifications for Electrical Power Equipment And Systems.

NFPA 70 - National Electrical Code.

UL 486A-486B - Wire Connectors.

UL 486C - Splicing Wire Connectors.

UL 486D - Sealed Wire Connector Systems.

UL 510 - Polyvinyl Chloride, Polyethylene, and Rubber Insulating Tape.

      - ***************************************************************************************

      - The following Article, "Action Submittals," is a designer choice.  Torquing may not always be a part of the project.

      - Certification of the Subcontractor’s tool and instrument calibration program is an element of the Subcontractor’s Quality Assurance Program required by Section ​<< 01 4000 - Quality Requirements - Non-Nuclear>>​; submit under that Section. If not present in Specification, submit under this Section.

      - ***************************************************************************************

ACTION SUBMITTALS

Certification of the Subcontractor’s tool and instrument calibration program.

      - ***************************************************************************************

      - The following article "Informational Submittals" is a designer choice.  Retain the subparagraphs according to project requirements.

      - ***************************************************************************************

INFORMATIONAL SUBMITTALS

At Closeout:

Field Test Records

Tool and instrument calibration records

Termination torque records

Cable pulling records

Field Quality Control reports and tests results

Documentation of the witness of torquing.  Note: For further information, refer to Section << 01 4000 - Quality Requirements - Non-Nuclear>>.

QUALITY ASSURANCE

Comply with the National Electrical Code (NEC), <<NFPA 70>>, for installation requirements.

Provide products that are listed and labeled by a Nationally Recognized Testing Laboratory (NRTL).  If listed products are unavailable, contact LANL Electrical Safety Office via LANL Subcontract Technical Representative (STR) for instructions.

Calibrated tools and test instruments shall be maintained and calibrated per <<NETA ATS>>.

​Delivery, Storage, and handling

Receive, store, and protect, and handle products per <<NECA 1>>.

PART 2 - PRODUCTS

    - **********************************************************************************************

      - The following article "Product options and substitutions" is a designer choice, based on project scope.

    - **********************************************************************************************

PRODUCT OPTIONS AND SUBSTITUTIONS

Refer to Section << 01 2500 - Substitution Procedures>>.

When manufacturers or products are listed in this Section, the lists are meant to be examples of products that meet it and not meant to be all-inclusive.  Any product that meets the same salient features listed is acceptable.

      - ***************************************************************************************

      - The following Articles are designer-choice based on project-specific requirements.

      - ***************************************************************************************

BUILDING WIRE

Provide building wire as shown on the Drawings with the following characteristics:

Description: Single conductor 600 V insulated wire.

Conductor:

98% conductivity, annealed, uncoated copper, <<ASTM B3>>, solid or stranded as specified in Part 3 of this Section.

Aluminum conductors may be used under the following conditions:

Conductors are AA 8000 series aluminum alloy registered in <<ASTM B800>>, or compact stranded per <<ASTM B801>>

Conductors are 8AWG or larger.

If construction drawings show copper conductors, Subcontractor is responsible for recalculating wire sizes, voltage drop, raceway sizes, junction box sizes, and conduit body sizes. Note: If the raceway size is 2 inches or less, it is exempt from seismic design. If, by using aluminum conductors instead of copper, the size of the raceway exceeds 2 inches, the raceways are subject to seismic design.

Insulation: The following types, rated 600 volts:

          - **********************************************************************

          - Use thermoset (XHHW-2) conductor insulation for all branch circuits and feeders for Safety Class; Safety Significant; and NEC Article 695, 700, 701, and 708 systems. Thermoset insulation may also be needed for wiring in high temperature or high radiation environments. If these systems or conditions do not exist on this Project, the use of THHN/WHWN-2 shall be permitted.

          - **********************************************************************

Unless otherwise indicated on the drawings:  Type THHN/THWN-2, or XHHW-2.

Where indicated on the drawings:  Type XHHW-2.

      - ***************************************************************************************

      - The following paragraph is a designer-choice, applicable to new facilities.

      - NOTE: Color codes are really only meaningful during construction. After construction, the only colors that matter are for the Neutral and the Grounding. All other colors are ungrounded conductors and it is not practical to assume that a particular line or phase is a consistent color throughout the installation.

      - ***************************************************************************************

Color-code conductors in new installations as follows:

Use colored insulation for color coding conductors 6 AWG and smaller, unless part of a cable assembly. Conductors that are part of a cable assembly may be marked at termination points.

Use  water and oil resistant colored plastic adhesive tape, 3/4 inch minimum width, for color coding conductor 4 AWG and larger.

Manufacturer: 3M “Scotch 35"

Use the following color codes for AC power system conductors:

| Conductor | 480Y/277V | 208Y/120V | 208Y/120V Isolated Ground* |
| --- | --- | --- | --- |
| Phase A | Brown | Black | Black |
| Phase B | Orange | Red | Red |
| Phase C | Yellow | Blue | Blue |
| Grounded (Neutral) | Gray | White | White |
| Equipment Grounding | Green | Green | Green |
| Isolated Ground | --- | --- | Green/Yellow |
| Switched | Purple or color of feeding circuit with labels: S1, S2… | Pink or color of feeding circuit with labels: S1, S2… | --- |

          - *Isolated grounds may only be used with the approval of the LANL Electrical Standards Point of Contact

        - Note:  The phasing at the load terminals of a breaker in a Schneider Electric I-Line panel may not be ABC top to bottom.. Color-code the conductors by phase as noted in the table, and as marked on the terminals of the circuit breakers.

        - Note: The rotation of a system might require colors to be swapped thus changing the physical location of where an expected color for a line or phase may be.  This is acceptable.

Use the following color codes for DC power system conductors:

          - Positive:     Red

          - Negative:   Black

Use the following color codes for 120/240 volt AC single-phase systems:

          - Line 1:   Black

          - Line 2:   Red

          - Grounded Conductor:  White

          - Equipment grounding conductor:  Green

Provide color code for control conductors as indicated on equipment or control system manufacturer’s drawings.

      - ***************************************************************************************

      - The following is a designer-choice, applicable to existing facilities. If multiple color codes exist in a facility such that there is no predominant one, use the color codes for new installations.

      - If the color code for a facility is not known at the time of design, it might require an outage to ascertain the facility color code unless the responsible system engineer knows.  In the absence of being able to obtain the facility color code, assume the color code for new installations.  Brown-Orange-Yellow for 480/277 and Black-Red-Blue for 208/120.  If, upon opening the panels, the colors are the same but in a different sequence, e.g., Orange-Yellow-Brown, the existing color code for the facility should be used.

      - ***************************************************************************************

Color-code conductors in existing facilities as follows:

Use colored insulation for color coding conductors 6 AWG and smaller, unless part of a listed cable assembly. Conductors that are part of a listed cable assembly may be marked at terminations.

Use  water and oil resistant colored plastic adhesive tape, 3/4 inch minimum width, for color coding conductor 4 AWG and larger.

Manufacturer: 3M, “Scotch 33+,” or “Scotch 35"

Use the following color codes for AC power system conductors:

        - ******************************************************************************

        - Edit the following: Design engineer shall complete the following table to identify the existing facility's color code requirements.

        - ******************************************************************************

| ​ Conductor | ​ 480Y/277V | ​ 208Y/120V | ​ 208Y/120V Isolated Ground*​ |
| --- | --- | --- | --- |
| Phase A |  |  |  |
| Phase B |  |  |  |
| Phase C |  |  |  |
| Grounded (Neutral) |  |  |  |
| Equipment Grounding | Green | Green | Green |
| Isolated Ground | --- | --- | Green/Yellow |
| Switched | Purple or color of feeding circuit with labels: S1, S2… | Pink or color of feeding circuit with labels: S1, S2… | --- |

        - * Isolated grounds may only be used with the approval of the LANL Electrical Standards Point of Contact

        - Note: The phasing at the load terminals of a breaker in a Schneider Electric I-Line panel may not be ABC top to bottom, color-code the conductors by phase as noted in the table, and as marked on the terminals of the circuit breakers.

Provide color code for control conductors as indicated on equipment or control system manufacturer’s drawings.

        - Note: In existing facilities, in order to maintain rotation, it is sometimes necessary to swap two conductors in a three-phase feeder. In this situation, the color code sequence of the line side of the conductors will be different from the color code sequence on the load side of the conductors.

      - ***************************************************************************************

      - Type MC cable may be used in IBC Business Group B occupancies for branch circuit wiring systems. Refer to LANL ESM Chapter 7 - Electrical, Section D5020 for additional information.

      - ***************************************************************************************

METAL-CLAD CABLE

Manufacturer: AFC Cable Systems Inc.

Provide metal-clad cable (Type MC) that complies with <<NFPA 70>>, and this Section.

Provide MC cables with quantities and sizes (minimum 12 AWG) of conductors as indicated on the Drawings.

Metal-clad cable shall consist of 600 V THHN/THWN-2 insulated circuit conductors, an insulated equipment-grounding conductor, a Mylar wrapping around the conductor bundle, and a close-fitting aluminum or galvanized steel outer sheath.

Provide metal-clad cables with conductors solid or stranded as specified in Part 3 of this Section.

Provide insulated-throat or insulating-bushing connectors for Type MC cables.

      - ***************************************************************************************

      - The following paragraph is a designer-choice and applicable to circuits with isolated grounds. Isolated grounds may only be installed with the permission of the electrical standards POC.  This is rare.

      - ***************************************************************************************

Metal-clad cables used to supply isolated-ground branch circuits shall have a neutral conductor, isolated ground conductor and equipment grounding conductor.  Identify each isolated ground conductor with a yellow-colored stripe on the green insulation.

      - ***************************************************************************************

      - The following paragraph is a designer-choice and applicable to multiple branch circuits in the same MC cable.  This is rare.

      - ***************************************************************************************

Metal-clad cables used to supply multiple branch circuits shall have the appropriate phase conductors for the number of circuits, a separate neutral conductor for each circuit, and one equipment ground conductor per cable. Uniquely identify each neutral with a colored stripe on the white insulation corresponding to the phase conductor insulation color.

      - ***************************************************************************************

      - The following paragraph is a designer-choice and applicable to circuits with isolated grounds. Isolated grounds may only be installed with the permission of the electrical standards POC.  This is rare.

      - ***************************************************************************************

Metal-clad cables used to supply multiple isolated-ground branch circuits shall have the appropriate phase conductors for the number of circuits, a separate neutral and isolated ground conductor for each circuit, and one equipment ground conductor per cable. Uniquely identify each neutral with a colored stripe on the white insulation corresponding to the phase conductor insulation color. Uniquely identify each isolated-ground conductor with one or more yellow-colored stripes on the green insulation.

WIRING CONNECTORS

For splices and taps on copper wire, sizes 12 to 10 AWG solid and 12 to 6 AWG stranded, use push-on, insulated, spring type connectors, or twist on connectors with helical coiled spring rated 600 V and 105 degrees C that are NRTL-listed to <<UL 486C>>, and provide a means of visual inspection, if applicable, of the connection. Use connectors within their identified and marked ranges and wire types.

Manufacturers and Products:

IDEAL “In-Sure”

IDEAL “Twister Series”

3M “Scotchlock”

Wago “773 Series”

For splices and taps on copper wire, sizes 6 AWG through 1 AWG, use the following materials:

Tin-plated copper split-bolt connectors meeting <<UL 486A-486B>>. Provide with matching 600-volt snap-on insulating cover.

Multi-tap connectors meeting <<UL 486A-486B>> that have two or more range-taking mechanical lugs and matching 600-volt insulated cover.

For wire, sizes 1 AWG and larger, use <<UL 486A-486B>> listed mechanical terminals, splices, or adapters.

Provide mechanical terminals and splices made from aluminum, aluminum alloy, copper or a copper alloy, and marked “CU,” “AL-CU,” or “CU-AL.”

Manufacturers: FCI Burndy, Ilsco, or Thomas & Betts.

For aluminum wire, use <<UL 486A-486B>> listed mechanical terminals, splices, or adapters.

Provide mechanical terminals and splices made from aluminum, aluminum alloy, and marked “AL,” “AL-CU,” or “CU-AL.”

Manufacturer: FCI Burndy, Ilsco, or Thomas & Betts.

For control wiring use nylon insulated crimp-on terminals with insulation grip that meeting <<UL 486A-486B>>.

Manufacturer: 3M “Scotchlok MNG,” Thomas & Betts “Sta-Kon.”

Use ring tongue terminals for nutted studs.

Use flanged fork terminals for barrier terminal blocks.

Use pin terminals or ferrules for DIN type terminal blocks.

Insulation-piercing type connectors are not acceptable for power or control wiring.

INSULATING TAPE AND TUBING

Insulate taped splices and connections using ethylene propylene rubber (EPR) tape meeting <<UL 510>>, and is rated for 90 degrees C continuous operation and 130 degrees C short-term overload service.

Manufacturer: 3M “Scotch 130C”

For the outer covering of tape-insulated splices and connections, use vinyl plastic tape meeting <<UL 510>>​​​​, <<ASTM D3005>>, and with the following characteristics:

8.5 mil minimum thickness.

Rated 600 volts and 105 degrees C, suitable for indoor and outdoor applications.

Retains flexibility, adhesion, and applicable at temperature ranges from 0–100ºF without loss of physical or electrical properties.

Resistant to abrasion, moisture, alkalis, acid, corrosion, and sunlight.

Manufacturer: 3M “Scotch Super 88.”

Provide heat shrinkable tubing meeting <<UL 486D>>, and with the following characteristics:

Rated 600 volts.

Factory applied adhesive/sealant.

Split resistant.

Manufacturer: 3M “ITCSN”.

Use motor lead splicing kits to insulate and seal connections to leads for motors rated 480V and less.

Manufacturer: 3M “5300 Series.”

WIRE PULLING LUBRICANT

Provide wire-pulling lubricant that is identified for use with the conductor insulation or jacket, has a maximum coefficient of dynamic friction of 0.25, and leaves no flammable residue. For cold weather installations, provide wire-pulling lubricant suitable for conduit temperature.

PART 3 - EXECUTION

EXAMINATION

Verify that work of other trades likely to damage wire and cable is completed.

Verify raceway installation is complete and supported.

Field-verify dimensions shown on Drawings.

Wire and cable routing shown on Drawings is approximate unless dimensioned.

Route wire and cable as required to meet Project conditions.

Where cable routing is not shown, and destination only is indicated, determine exact routing and lengths required to meet Project conditions.

PREPARATION

Examine raceways and building finishes that are to receive wires and cables for compliance with installation tolerances and other conditions. Do not proceed with installation until unsatisfactory conditions have been corrected.  Ensure conduit bodies meet the Code requirements for the number of conductors.

<<NFPA 70>>, 314.16, for conductors 6 AWG and smaller.

<<NFPA 70>>, 314.28, for conductors 4 AWG and larger.

      - ***************************************************************************************

      - The following paragraph is a designer-choice and applicable to underground ducts.

      - ***************************************************************************************

All ducts shall be cleaned by passing a wire brush mandrel and/or rubber duct swab (or approved alternative) of appropriate size back and forth until all foreign materials and water are removed.

Do not handle or pull cables that are colder than +14 degrees F, unless allowed by manufacturer’s recommendations. Store cold cables for at least 24 hours in a heated building prior to installation.

      - ***************************************************************************************

      - The following Article is a designer-choice and applies when existing construction is affected.

      - ***************************************************************************************

EXISTING WORK

Provide access to existing wiring connections remaining active and requiring access. Modify installation or install access panel.

      - ***************************************************************************************

      - The following paragraph is a designer-choice and applies when extending existing circuits.

      - ***************************************************************************************

Extend existing circuits using materials and methods as specified.

Determine and record the existing power distribution system phase rotation, ABC clockwise or ABC counterclockwise.  Maintain the existing phase rotation throughout the new installation.

      - ***************************************************************************************

      - The following four Articles are designer-choice based on project-specific requirements.

      - ***************************************************************************************

BUILDING WIRE INSTALLATION

Install building wire per <<NFPA 70>>, the requirements in this Section, and the following NECA installation standards, as applicable:

<<NECA 1>>​

<<NECA 104>>​

Do not “through-pull” conductors at boxes, fittings or cabinets where a change of raceway alignment occurs.

Ensure manufacturer’s minimum cable bend radius is not violated during installation.

Do not damage conductor, insulation, or jacket by excessive installation pulling tension or sidewall bearing pressure.

Use a tension measuring device to monitor pulling force on conductors 1/0 AWG and larger where any of the following combinations of bends and raceway length is exceeded between accessible pull points:

4 equivalent 90-degree bends and 10 feet of raceway.

3 equivalent 90-degree bends and 40 feet of raceway.

2 equivalent 90-degree bends and 80 feet of raceway.

1 equivalent 90-degree bend and 150 feet of raceway.

Straight pull with more than 250 feet of raceway.

Where a pulling winch is used, use a tension measuring device to monitor pulling force on each pull of conductors for ML-1, ML-2, fire pump, and emergency circuits. Record and submit the maximum measured pulling tension for each cable pull.

Record the maximum measured pulling tension for each monitored cable or conductor pull.

Obtain recommended maximum conductor or cable pulling tension and sidewall bearing pressure values from the manufacturer, or use the following maximum allowable values:

Maximum sidewall bearing pressure: 500 lb/ft.

Maximum tension, pulling directly on conductor: 0.008 lb./cmil.

Maximum tension, pulling on basket grip over insulation jacket: 2000 lb., not to exceed 0.008 lb/cmil of conductor.

Submit the recorded cable, or conductor, pulling tension for each monitored pull and the corresponding maximum allowable pulling tension.

Notify the LANL STR of any cable where the minimum bending radius was violated during installation.

Notify the LANL STR of any conductor or cable pull where the maximum measured pulling tension exceeded 80 percent of maximum allowable pulling tension or sidewall bearing pressure. Replace the conductors where the maximum measured pulling tension exceeded 100 percent of maximum allowable pulling tension or sidewall bearing pressure.

Use solid copper conductors for power circuits 10 AWG and smaller.

Where both ends of conductor 10 AWG and smaller are terminated in pressure plate terminations or in crimped lugs, stranded conductors may be used.

Use stranded conductors for power circuits 8 AWG and larger.

Use copper conductors not smaller than 12 AWG for power and lighting branch circuits.

Install wiring at outlets with at least 6 inches of slack conductor at each outlet, a minimum of 3 inches of which extends beyond the box opening.

Splices in feeder conductors may only be used with the permission of the Authority Having Jurisdiction (AHJ).

Use copper conductors for ML-1, ML-2, fire pump, and emergency systems.

      - ***************************************************************************************

      - The following article is a designer-choice, depending on if Type MC Cable is allowed on the project. Note that use of Type MC Cable at LANL is restricted to International Building Code “Business Group B” occupancy. Refer to LANL ESM Chapter 7 - Electrical, Section D5020 for additional information.

      - ***************************************************************************************

TYPE MC CABLE INSTALLATION

Install MC cables per <<NECA / NEIS 120>>​​​​​, <<NFPA 70>>, and requirements in this Section.

Route MC cables to meet Project conditions.

      - ***************************************************************************************

      - The following paragraph is a designer-choice.

      - ***************************************************************************************

For branch circuits serving multiple outlets use conduit for the “homerun” from the branch circuit panelboard to the first outlet or junction box. Use Type MC cables for branch circuit wiring beyond the first outlet or junction box.

Use Type MC cables in interior, dry locations where they will be concealed above ceilings, in dry-wall partitions, in equipment enclosures, or below raised floors. Type MC cables may be installed exposed in dedicated electrical rooms and mechanical rooms if they will not be exposed to physical damage or deteriorating agents.

Install and support Type MC cables as required in Article 330 of <<NFPA 70>>. Use spring steel MC cable supports or UV resistant tie wraps, listed as a means of support, to support Type MC cables; do not use wire to support Type MC cables.

CONNECTOR INSTALLATION

Install conductors in terminals, splices, adapters, and connectors per the manufacturer’s instructions. Have the manufacturer’s installation instructions available at the construction site.

Do not nick conductors when removing insulation.

Do not cut conductor strands to fit into connectors, splices, adapters, or terminals.

Make connections using clean connection surfaces. Wire brush conductors immediately before installing lugs, terminals, splices, or adapters.

Terminate all power conductors using mechanical lugs.

Terminate control conductors using crimp-on terminals or ferrules. Do not place stranded conductors directly under terminal screws. Install terminals or ferrules on conductors using ratchet-type compression tools.

      - ***************************************************************************************

      - The following paragraph is a designer-choice and applies to new facilities.

      - ***************************************************************************************

In new facilities only, the power distribution system’s phase rotation shall be ABC clockwise, downstream of the utility transformer.  This phase rotation shall be maintained throughout the power distribution system.  Make or correct connections at rotating equipment input terminal to ensure proper equipment rotation.

      - ***************************************************************************************

      - The following paragraph is a designer-choice and applies to existing facilities.  It is fairly common to find that existing equipment might have different phase rotations.  For example.  Switchgear that has a clockwise rotation might feed an MCC that has a counter-clockwise rotation.  Leave all existing equipment as is.  Do not make changes to existing distribution equipment.

      - ***************************************************************************************

In existing facilities, the phase rotation of new distribution equipment shall match the existing phase rotation of the existing equipment upstream.   Rotating equipment (e.g. motors) must always be checked for proper rotation.  Make connections in the motor connection box as necessary to ensure proper rotation.

Terminate wiring on devices and components as indicated on the drawings or per the manufacturer’s instructions.

The LANL STR shall be given 2 weeks written, advance-notice of the date and time when the torquing of connectors and terminals, including screws and bolts in major electrical distribution equipment, will be performed. Major electrical distribution equipment includes: transformers, switchgear, switchboards, MCCs, panelboards, disconnect switches, motors greater than 10HP, receptacles sized greater than 50A.  The LANL STR shall be contacted two weeks prior to torquing such that the LANL STR can arrange witnessing of the torquing, or a percentage thereof.

Tighten connectors and terminals, including screws and bolts, to manufacturers published torque-tightening values using a calibrated torque wrench, torque screwdriver, or other approved method. Note: Some equipment, or fasteners, have features or indicators that do not necessitate the use of a torque tool. For example: heads that sheer off when the proper torque is applied, fasteners that have built in indicators of proper torque, or terminals that are manufactured for the purpose of not needing a torque tool.

Where manufacturer's torque-tightening values are not indicated, tighten connectors and terminals to torque-tightening values specified in <<UL 486A-486B>>, or  <<NETA ATS>>​ Tables 100.12.1, 100.12.2, 100.12.3, or 100.12.4, as appropriate.

        - Note: On older equipment that needs to be re-terminated, the metallurgy or grade isn’t always known. Types of terminations may also be very unusual and might not fit into one of the categories in the tables. The system engineer or other authority should be consulted as to how to proceed in cases such as this.

Provide a tabulated torquing record.  This shall include as a minimum:

The torque values applied to all connectors and terminals that are required to be torqued.

The identification of the torque tools used.

The torque tools next calibration due date.

The person making each termination.

Signing and dating by the person(s) performing the torquing.

If applicable, the report will be signed and dated by the LANL STR or LANL STR representative witnessing the torquing.

INSULATING TAPE AND TUBING Installation

Install insulating tape and tubing per the manufacturer’s instructions. Have the manufacturer’s installation instructions available at the construction site.

Insulate splices and taps of irregular shapes with manufactured insulating covers or insulating tape built up to not less than 150 percent of insulation rating of conductor.

For voltages over 600 volts: Use rubber insulating-tape in half-lapped layers to develop the basic insulation over splices and taps.

For circuits less than 600 volts: Use vinyl plastic tape in half-lapped layers to provide the outer protective covering over splices and taps, or for the sole means of protection.

Insulate cylinder shaped splices and taps, connector barrels and adapter barrels using heat shrinkable insulating tubing, insulating covers manufactured for the connector, or tape insulation as described above.

      - ***************************************************************************************

      - Retain the following two Articles for building wire and metal-clad cable.

      - ***************************************************************************************

IDENTIFICATION

Identify wire and cable under provisions of Section << 26 0533 - Raceways and Boxes for Electrical Systems>>.

Identify each conductor with its circuit number or other designation indicated on Drawings.

If color-coding tape is used for the re-identification of conductors, the tape must be applied at each termination or splice.

FIELD QUALITY CONTROL

The LANL STR shall be given 2 weeks, written advance-notice of the date and time when inspection and testing required by this Section will be conducted. At the discretion of the LANL STR, any of the following tests or inspections may be witnessed by the LANL STR or LANL STR representative.

Pre-installation Inspection and Tests

Inspect conductors and cables for:

Freedom from material defect or physical damage.

Correct conductor size, material, and insulation type.

For cables that contain conductors 1/0 and larger, or those supplying critical loads as determined by the responsible engineer or FOD, use a megohm meter in a 1-minute test to verify the insulation integrity of the conductors while still on the reel. Record all test results.

Use 1000-volts dc to test conductors rated 600 volts.

Conductors with insulation resistances over 50 megohms are acceptable.

Conductors with insulation resistances less than 2 megohms are defective.

If the conductor insulation resistance is between 50 megohms and 2 megohms, consult the LANL STR for further direction.

Reject and replace entire reels, rolls, or boxes containing conductors or cables with material or manufacturing defects.

Observe conductors and cables during the installation process.

Reject and replace cable or conductor segments that have been kinked, dented, or otherwise damaged during handling or installation.

After installation of wires and cables, perform the following inspections and tests

Inspect conductors and cables for:

Freedom from material defect or physical damage,

Correct conductor size, material, and insulation type, and

Correct color coding and identification.

Before energizing the circuit, perform the following and tests

Before connecting conductors to equipment, use a megohm meter in a 1-minute test to verify the insulation integrity of each service conductor, feeder conductor 1/0 AWG or larger, critical system branch circuit conductor, or critical system control conductor with respect to ground and other associated conductors in the same cable or raceway.

Use 1000-volts dc to test conductors rated 600 volts.

Conductors with insulation resistances over 50 megohms are acceptable.

Conductors with insulation resistances less than 2 megohms are defective.

If the conductor insulation resistance is between 50 megohms and 2 megohms, consult the LANL STR for further direction.

After connecting conductors to equipment, inspect connections for correct connector size and type.

Witness and document torquing on not less than 10% of each type of connector and terminal.

Remove and replace defective, incorrect, or improperly installed conductors and connectors. Re-inspect and re-test replacement conductors and connectors.

Submit test and inspection records to the LANL STR.

      - ***************************************************************************************

      - The following paragraph is a designer-choice if formal electrical acceptance testing is required. Refer to LANL ESM Chapter 7 - Electrical, Section D5000 for additional information.

      - ***************************************************************************************

Refer to Section << 26 0813 - Electrical Acceptance Testing>> for other inspections and tests that are required before conductors may be energized.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 26 0519, REV. 9, DATED APRIL 15, 2026.