Section 26 0526 
Grounding and Bonding for Electrical Systems

  - ************************************************************************************************************

    - LANL MASTER SPECIFICATION section

Rev. 4 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Electrical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality Sections.

  - ************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

      - ***************************************************************************************

      - The following paragraphs are designer-choices based on project-specific requirements.  A Concrete Encased Electrodes are the preference.  This will be available whenever there is a concrete slab.  In the absence of concrete encased electrodes, ground rods will be used.

      - ***************************************************************************************

Concrete Encased Electrode

Ground Rods

Electrical System Grounding Bar and Grounding Bar Extensions

Low-Voltage Distribution Transfer Grounding Terminal Bar

Ground Plates

Grounding Electrode Conductor

Equipment Grounding Conductors

Conduit Grounding Bushings

Compression Grounding Connections

Exothermic Weld Grounding Connections

Pipe Grounding Connectors

      - ***************************************************************************************

      - Refer to LANL ESM Chapter 7 - Electrical, Section D5020 for static electricity grounding and bonding design requirements.

      - ***************************************************************************************

Static Electricity Grounding and Bonding

Main Grounding Electrode System

System Grounding (Main Bonding Jumper, System Bonding Jumper)

Enclosure and Equipment Grounding System (components and construction of the effective ground-fault current path).

      - ***************************************************************************************

      - Isolated ground systems may only be installed with the permission of the LANL ESM electrical standards point of contact. Isolated ground systems were popular in the 1980's and 1990's in an effort to create a 'clean ground.' The issue was multiple bonding jumpers in a system that gave neutral current an additional path. This created magnetic fields which interfered with electronic equipment. The real solution is to remove redundant bonding jumpers. If facilities think they need isolated grounds, a walkdown needs to be scheduled with the facility to address the real issues.

      - ***************************************************************************************

Isolated Ground System.

related requirements

Section << 01 2500 - Substitution Procedures>>.

Section << 01 3300 - Submittal Procedures>>.

Section << 01 4000 - Quality Requirements - Non-Nuclear>>

REFERENCE STANDARDS

ANSI C135.30 - Zinc-Coated Ferrous Ground Rods for Overhead or Underground Line Construction.

ASTM B8 - Standard Specification for Concentric-Lay-Stranded Copper Conductors, Hard, Medium-Hard, or Soft.

NECA 1 - Standard for Good Workmanship in Electrical Construction.

NETA ATS - Standard for Acceptance Testing Specifications for Electrical Power Equipment And Systems.

NFPA 70 - National Electrical Code.

NFPA 77 - Recommended Practice on Static Electricity.

      - ***************************************************************************************

      - The following Article Informational Submittals is a designer-choice, based on  required inspections performed.

      - ***************************************************************************************

INFORMATIONAL SUBMITTALS

Submit the following in accordance with Section ​​<< 01 3300 - Submittal Procedures>>​​.

Provide documentation of quality control inspections performed under Part III of this Section.  Meet the requirements of Section << 01 4000 - Quality Requirements - Non-Nuclear>> when present in Project Specification package.

​quality assurance

Provide products that are listed and labeled by a Nationally Recognized Testing Laboratory (NRTL) where such products are required by <<NFPA 70>>  to be listed, or when such products enclose an electrical hazard as follows:

For AC circuits – greater than 50 volts

For DC circuits and batteries – greater than 100 volts.

​Delivery, Storage, and handling

Receive, store, and protect, and handle products according to <<NECA 1>>.

PART 2 - PRODUCTS

    - **********************************************************************************************

      - The following is a designer choice, based on if substitutions are allowed on the project.

    - **********************************************************************************************

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section << 01 2500 - Substitution Procedures>>.

      - ***************************************************************************************

      - The following Articles are designer-choices based on project-specific requirements and are all automatically activated by the corresponding paragraphs in Article SECTION INCLUDES.

      - ***************************************************************************************

GROUND RODS

<<ANSI C135.30>>​ with high-strength steel core and electrolytic-grade copper outer sheath, molten welded to core.

Manufacturers: Blackburn, Thomas & Betts, Harger.

ELECTRICAL SYSTEM GROUNDING BAR AND GROUNDING BAR EXTENSIONS

Provide grounding bar, 12 inches long or greater length as indicated on the Drawings, fabricated from 1/4 inch thick, 4 inch wide copper stock with 1.75 inch x 2" bolt-hole pattern to accept NEMA standard lugs. Mount grounding bar on 2,700 volt standoff insulators.

LOW-VOLTAGE DISTRIBUTION TRANSFORMER GROUNDING TERMINAL BAR

Furnish, if one is not already installed by the factory, a terminal bar that is suitably sized for the type and size of the following conductors:

System bonding jumper.

Supply side bonding jumper.

Grounding electrode conductor.

Primary equipment grounding conductor.

GROUND PLATES

Provide ground plates designed for flush mounting in concrete structures.

Furnish copper alloy castings with four 1/2 inch x 13 threaded holes at 1.75 inch x 1.75inch NEMA spacing and a welding stud or compression connection suitable for 2 AWG to 250 kcmil copper conductor.

Furnish ground plates that are identified for direct burial..

Manufacturer: Burndy “YGF”.

GROUNDING ELECTRODE CONDUCTOR

      - ***************************************************************************************

      - Retain either the first or the second paragraph, based on project

      - ***************************************************************************************

Provide bare-stranded, soft-temper copper conductor that conforms to <<ASTM B8>>.

      - *** OR ***

Provide green insulated THWN-2 copper conductor.

EQUIPMENT GROUNDING CONDUCTORS

Provide << THHN/THWN-2; or  XHHW-2>>  insulated copper wire.

Use solid equipment grounding conductors 10 AWG and smaller where not subject to vibration or repeated flexing. Where both ends of the conductor are terminated in pressure plate terminations or in crimped lugs, stranded conductors may be used.

Use stranded equipment grounding conductors for 8 AWG and larger.

Use stranded equipment grounding conductors where subject to vibration or repeated flexing.

Color code equipment grounding conductors as follows:

Equipment grounding conductor:

Conductors 6 AWG and smaller: Green colored insulation.

Conductors 4 AWG and larger: Green colored insulation or other colored insulation, not white, with 3/4-inch-wide band of water and oil-resistant green vinyl electrical tape.

        - ******************************************************************************

        - The following subparagraph is a designer-choice and is automatically activated if "isolated ground system" is activated in Part 1. Isolated ground systems may only be installed with the permission of the LANL ESM electrical standards point of contact. Isolated ground systems were popular in the 1980's and 1990's in an effort to create a 'clean ground.' The issue was multiple bonding jumpers in a system that gave neutral current an additional path. This created magnetic fields which interfered with electronic equipment. The real solution is to remove redundant bonding jumpers. If facilities think they need isolated grounds, a walkdown needs to be scheduled with the facility to address the real issues.

        - ******************************************************************************

Isolated grounding conductor:

Conductors 6 AWG and smaller: Green colored insulation with continuous yellow stripe.

Conductors 4 AWG and larger, or any size conductor that is part of a cable assembly: Green-colored insulation with continuous yellow stripe—or other-colored insulation (except white,) with 3/4-inch wide bands of water- and oil-resistant green and yellow vinyl electrical tape.

CONDUIT GROUNDING BUSHINGS

Provide 150 Degrees C rated insulated throat grounding bushings with lay-in type ground cable lugs.

Manufacturers: O-Z/Gedney Type “BLG”.

COMPRESSION GROUNDING CONNECTIONS

Provide wrought copper connectors, terminals, taps, and splices for making compression grounding connections.

      - ***************************************************************************************

      - The following paragraphs are designer-choice, based on underground installations.

      - ***************************************************************************************

Furnish grounding connectors that are identified for direct burial.

Provide connector manufacturer’s hydraulic compression tools and dies that match the connectors.

Match connector and die size to material shapes and conductor sizes to be joined.

Use two-hole, heavy-duty compression lugs for bolted connections to ground bars, ground plates, and equipment ground pads for conductors that are 2 AWG and larger.

Manufacturer: Burndy “Hyground”.

EXOTHERMIC WELD GROUNDING CONNECTIONS

Provide molds and welding material for making exothermic weld connections

In interior locations and in vaults, use low smoke emission type welding material

Match mold and weld material to material types, shapes and sizes to be joined

Manufacturer: ERICO Cadweld.

PIPE GROUNDING CONNECTORS

Provide copper-alloy connectors for making cable to pipe connections.

Manufacturer: O-Z/Gedney “ABG” or “CG”.

Static Electricity Grounding and Bonding

Furnish static electricity grounding and bonding material as indicated on the Drawings and as required for a complete installation.

      - ***************************************************************************************

      - The following paragraphs  are designer-choices.  Do not use exothermic unless specifically required by the project.

      - ***************************************************************************************

Provide static ground bus complete with clamps, connectors, and mounting hardware.

Ground bus cable: 1/0 AWG bare stranded, soft temper copper cable that conforms to <<ASTM B8>>.

Connectors: Copper compression ring tongue terminals. Provide connector manufacturer’s compression tools and dies that match the connectors.

Manufacturer: Burndy YAV-L.

Cable holders: Preformed copper support loops, 5/8 inch wide.

Manufacturer: Thompson Lighting Protection No. 166.

Provide retractable static grounding reels with an enclosed cable drum and ​<< 20; or  50>>​ feet of 3/32 inch galvanized cable having a spring compression grounding clamp.

Manufacturer: Stewart R. Browne Manufacturing type << R-20; or  R-50>>​.

Provide spring compression grounding clamps having a plier type cast aluminum body and two stainless steel contact points.

Manufacturer: Stewart R. Browne Manufacturing type REB2960.

Provide cast bronze clamps for static bonding of metal pipes.

Manufacturer: Stewart R. Browne Manufacturing JR150 series.

Provide cast bronze or galvanized steel C-clamps for making semi-permanent connections to drums and containers.

Manufacturer: Stewart R. Browne Manufacturing type EP.

PART 3 - EXECUTION

EXAMINATION

Measurements shown on Drawings are approximate. Verify with field measurements.

Electrode locations and grounding cable routing shown on Drawings are approximate unless dimensioned.

Install electrodes and route cable as required to meet Project conditions.

Where electrode location or cable routing is not shown, and destination only is indicated, determine exact locations, routing, and lengths required to meet Project conditions.

GENERAL

Install grounding and bonding material according to manufacturer's instructions.  Have the manufacturer’s installation instructions available at the construction site.

      - ***************************************************************************************

      - Do not use the grounding electrode systems specified in this section for lightning protection grounding.  Lightning protection grounding is covered in Section << 26 4100 - Facility Lightning Protection>>.  Lightning protection grounding for structures that house explosives is covered in Section << 26 4115 - Lightning Protection for Explosive Facilities>>.

      - ***************************************************************************************

Do not use the grounding electrode systems specified in this section for lightning protection grounding.

Use the following connection methods unless otherwise specified or indicated on the Drawings:

        - ******************************************************************************

        - The following five subparagraphs are designer-choices.  The first subparagraph is for connections that are accessible.  The second subparagraph is for connections that are not accessible (e.g. underground).  Do not use exothermic unless specifically required by the project.  More than one of these methods may exist on the same project.

        - ******************************************************************************

Make bolted connections using bolts, nuts, flat washers, and toothed lock washers suitable for the connector and the installation environment; acceptable materials include high strength silicon bronze and 18-8 alloy stainless steel.

Make irreversible bolted connections using stainless steel tamper-resistant bolts and tamper-resistant nuts along with flat washers, and toothed lock washers. Tamper-resistant nuts and bolts must resist loosening with common tools; acceptable tamper-resistant fasteners include penta-head, break-away, and oval designs.

Use exothermic weld grounding connections for underground or concealed connections of dissimilar materials.

Use exothermic weld or compression grounding connections for underground or concealed connections of like materials.

Use exothermic weld, compression, or bolted grounding connections for accessible connections.

Use a connector that is identified for the application.

Tighten grounding and bonding connectors and terminals, including screws and bolts, in accordance with manufacturer's published torque tightening values for connectors and bolts. Where manufacturer's torquing requirements are not indicated, tighten connections to comply with torque tightening values specified in <<NETA ATS>> Tables 110.12.1, 110.12.2, 110.12.3, or 110.12.4 as appropriate. Use a calibrated torque wrench.  Manufacturer’s alternate methods for achieving proper torque values are acceptable.

        - Note: On older equipment that needs to be re-terminated, the metallurgy or grade isn’t always known. Types of terminations may also be very unusual and might not fit into one of the categories in the tables. The system engineer or other authority should be consulted as to how to proceed in cases such as this.

Use hydraulic compression tools to provide the correct circumferential pressure for compression connectors. Follow connector manufacturer’s installation instructions and use tools and dies recommended by the manufacturer of the connectors. Provide embossing die code or other standard method to make a visible indication that a connector has been adequately compressed.

Install exothermic welds in accordance with manufacturer's instructions and recommendations.

Make connections in such a manner as to minimize possibility of galvanic action or electrolysis. Select connectors, connection hardware, conductors, and connection methods so metals in direct contact will be galvanically compatible.

Use electroplated or hot-tin-coated materials to assure high conductivity and make contact points closer in order of galvanic series.

Make connections with clean bare metal at points of contact.

Make aluminum to steel connections with stainless steel separators and mechanical clamps.

Make aluminum to galvanized steel connections with tin-plated copper jumpers and mechanical clamps.

In underground, damp, or wet locations, coat and seal connections involving dissimilar metals with inert material to prevent future penetration of moisture to contact surfaces.

HOLD POINTS

The grounding electrode system must be inspected before the system is covered up, by earthwork, concrete, or building finish.

      - ***************************************************************************************

      - The following Articles: "Grounding Electrode System Installation," "Electrical System Grounding Bar and Grounding Bar extension," "System Grounding Installation," "Enclosure and Equipment Grounding Installation," "Isolated Ground System Installation," and "Static Electricity Grounding and Bonding Installation" are all designer-choices and are all automatically activated by the corresponding paragraphs in Article SECTION INCLUDES.

      - ***************************************************************************************

GROUNDING ELECTRODE SYSTEM installation

Concrete Encased Electrode: Install in accordance with <<NFPA 70>>, and as shown on drawings.

Ground Rod Electrode: Install a ground rod electrode system.

Install at least 20 feet of 2 AWG bare copper conductor in direct contact with the earth at a depth below the earth’s surface of not less than thirty (30) inches.  The 2 AWG bare copper conductor shall be installed in a continuous trench that is at least twenty (20) feet in length and be augmented with a minimum of two (2), eight (8) foot long, minimum, grounds rods one at each end of the 2 AWG conductor.

ELECTRICAL SYSTEM GROUNDING BAR AND GROUNDING BAR EXTENSION installation

Install a grounding bar in an accessible location in the main electrical room adjacent to the service equipment or main equipment.

Connect the grounding electrode conductor to the grounding bar.

If there is a lightning protection system, do not connect the lightning protection system grounding electrode system at this location.  Make the connection between the building grounding electrode system and the lightning protection electrode system at a point outside the building.

      - ***************************************************************************************

      - The following paragraph is a designer choice, depending on if more that one ground bar will be installed in the structure.

      - ***************************************************************************************

Ground bars may be established at additional locations by installing ground bars or ground plates connected to the main ground bar using 4/0 AWG ground conductor.

Bond exterior underground metal fire protection and potable water service pipes to the main ground electrode bar; use pipe grounding fittings and ground conductor as indicated on the Drawings, but not smaller than the conductor required by <<NFPA 70>> section 250.66, and not smaller than 4 AWG. Make bond to each water pipe at an accessible location within 5 ft of where it enters the structure. Comply with <<NFPA 70>> requirements for bonding around water meters and insulating joints.

      - ***************************************************************************************

      - The following paragraph is a designer-choice, depending on if the building has steel columns.

      - ***************************************************************************************

Bond the nearest building perimeter structural steel column or effectively grounded metal structure to the main ground electrode ground bar; use ground conductor as indicated on the Drawings, or not smaller than the conductor required by <<NFPA 70>> section 250.104.

SYSTEM GROUNDING installation (GEC for Service, system bonding jumper for separately derived system)

      - ***************************************************************************************

      - The following is a designer-choice, depending on if the structure is fed by the utility or if it is fed by a separately derived system.  The following paragraph is for systems fed by a utility transformer.

      - ***************************************************************************************

Service equipment

Connect the service equipment ground bus to the electrical system grounding bar; use a grounding electrode conductor as indicated on the Drawings, or not smaller than the grounding electrode conductor required by <<NFPA 70>>, section 250.66.

      - ***************************************************************************************

      - The following is a designer-choice, depending on if the structure is fed by the utility or if it is fed by a separately derived system.  The following paragraph is for separately derived systems.  For separately derived systems, the System Bonding Jumper must be in the transformer, not the first disconnect.  This means that the Grounding Electrode Conductor will also be connected at the transformer location.

      - ***************************************************************************************

Separately Derived Systems

Install system bonding jumper in transformer enclosure, from the neutral point of the transformer to the transformer grounding terminal bar. Size system bonding jumper as shown on drawings, but not less than the <<NFPA 70>> requirement in Table 250.102(C)(1).

When the system bonding jumper is in the transformer, grounding electrode conductor shall be terminated to transformer grounding bar.

First means of disconnect shall have no system bonding jumper installed and shall have separate neutral and ground bars.

ENCLOSURE AND EQUIPMENT GROUNDING installation

Provide permanent and effective bonding for equipment, enclosure, and raceways, in accordance with <<NFPA 70>>​ requirements, and as further specified or shown on the Drawings.

Provide an equipment ground bar, if one is not already a part of the equipment, in all switchgear, switchboards, panelboards, transformers, motor control centers, starters, and disconnect switches, for grounding the enclosure and for connecting other equipment and raceway grounding and bonding conductors.

If the grounding bar is a listed accessory to the equipment, no additional bonding jumper is needed between the grounding bar and the enclosure.

If the grounding bar is not a listed accessory to the equipment, install a bonding jumper between the grounding bar and the enclosure.  Size the bonding jumper to Table 250.122 based on the largest branch circuit or feeder overcurrent protection, or to Table 250.102(C)(1) if their are transformer secondary conductors feeding the panel.  Use whichever is largest.

Bonding Bushings

Install bonding bushings on metallic conduits entering enclosures through concentric, eccentric or oversize knockouts.

Install bonding bushings on metallic conduits that terminate to a metallic enclosure without effective electrical connection such as locknuts or threaded bushings.

Bond conduit bonding bushing lug to the equipment ground bar or ground lug in switchgear, panelboards, transformers, motor control centers, starters, disconnect switches, cabinets, etc. Size bonding jumpers in accordance with <<NFPA 70>>.

If bonding jumpers are part of the effective ground-fault current path that is downstream of overcurrent protection, the bonding jumper is an “equipment bonding jumper” and is sized per Table 250.122 in <<NFPA 70>>.

If bonding jumpers are part of the effective ground-fault current path that is upstream of overcurrent protection, the bonding jumper is a “supply-side bonding jumper” and is sized per Table 250.102(C)(1) in <<NFPA 70>>.

Provide an insulated equipment grounding conductor, of the wire type, for each raceway containing feeder or branch circuits.

Install the equipment grounding conductor within the common conduit or raceway, along with the phase and neutral conductors in that raceway.  Connect to the grounding terminal or grounding bus in each box or cabinet where a splice or termination of the associated conductors is made.

Size equipment grounding conductor as shown on the Drawings.

In each 15 or 20 ampere branch circuit outlet box and junction box where a splice of the ungrounded conductors is made, install a green-colored, washer-head grounding screw with a 12 AWG equipment grounding conductor pigtail and connect it to the equipment grounding conductor of the associated circuit.

Connect receptacle grounding terminals to the effective ground-fault current path  using minimum 12 AWG equipment grounding conductor of the wo.  Do not use a "self-grounding" receptacle strap as the only equipment grounding path.

      - ***************************************************************************************

      - The following paragraph is a designer-choice, depending on if busways are a part of the project.

      - ***************************************************************************************

Provide busways with a separate, internal equipment grounding conductor bus bar.  Install separate insulated equipment grounding conductor from the ground bus in the switchgear, switchboard, or distribution panel to the equipment grounding conductor bar terminal on busway.  Size conductor in accordance with <<NFPA 70>>​.

      - ***************************************************************************************

      - Isolated ground systems may only be installed with the permission of the LANL Electrical Standards Point of Contact. This is rare. Isolated ground systems were popular in the 1980's and 1990's in an effort to create a 'clean ground.' The issue was multiple bonding jumpers in a system that gave neutral current an additional path. This created magnetic fields which interfered with electronic equipment. The real solution is to remove redundant bonding jumpers. If facilities think they need isolated grounds, a walkdown needs to be scheduled with the facility to address the real issues.

      - ***************************************************************************************

ISOLATED GROUND SYSTEM installation

Install an isolated ground system as shown on the Drawings. In addition to the equipment ground bar, provide a separate, insulated, isolated copper ground bar in panelboards and switchboards supplying isolated ground circuits.

Run the isolated equipment grounding conductor together with the phase, neutral, and equipment grounding conductors in isolated ground system feeder and branch circuit conduits.

Make the isolated equipment grounding conductor the same size as the associated line or phase conductors.

At the first isolated ground system overcurrent device or disconnecting means, or where shown on drawings, bond the isolated ground bus to the equipment ground bus.  Make no other isolated ground to equipment ground connections on the load side of the separately derived system disconnect.

Connect the isolated ground conductors to the isolated ground bars in switchboards and panelboards and to the isolated ground terminals at receptacles and equipment.

Static Electricity Grounding and Bonding installation

Install static electricity grounding and bonding material as indicated on the Drawings.

Comply with <<NFPA 77>>.

Install ground bus cable from the ​<< main electrode ground bar or extension; or  effectively grounded building structural steel>>​ to the static electricity grounding and bonding locations indicated on the Drawings.

Support exposed ground bus cable with cable holders installed at intervals not exceeding 24 inches.

Make connections to and between ground bus cable using compression connectors, nuts, bolts, flat washers, and lock washers. Install compression connectors using tools and compression dies recommended by the connector manufacturer.

Install static grounding cable reels at locations indicated on the Drawings; coordinate location with luminaires, equipment, piping, and ductwork.

Install pipe clamps and C-clamps to bond pipes, drums, and tanks in the static electricity control areas.

FIELD QUALITY CONTROL

General: Constructor shall perform onsite quality control inspections.  Inspection shall be visual for workmanship and adherence to requirements before grounding electrode system is covered up by earth or concrete.

Notify the LANL Subcontract Technical Representative (STR) ten (10) working days in advance of the expected completion of a grounding system installation.  Inspection can be scheduled in parts or by area depending on the system and construction schedule.

Before work is concealed, it must be inspected by the office of the Chief Electrical Inspector to verify and certify that the following grounding installations have been made correctly

The electrical system grounding electrode system. This includes the bonding of the foundation reinforcing bars, bonding of the structural steel columns, and bonding of other metallic systems and other grounding electrode systems.

Ground plates and grounding bars.

All other underground grounding installations.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 26 0526, REV. 4, DATED APRIL 15, 2026.