Section 26 0529 
Hangers and Supports for Electrical Systems

  - ************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 8 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Electrical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable Sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality Sections.

      - ==========================================================

      - This section is for non-seismic supports only. For seismic, use Section << 26 0548.16 - Seismic Controls for Electrical Systems>>.

      - Electrical raceways that are 2 inches or less are exempt from seismic design. This should be considered when designing systems. For example, for a 400-amp system, the designer might want to use parallel 3/0 conductors in two, 2-inch raceways instead of 600 kcmil conductors in a single larger raceway that might require seismic design.

      - This section is usually issued with most paragraphs turned on.  This is because raceways are field routed and it is up to the constructor to determine what devices are needed.

  - ************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

Coatings and Materials

Raceway Supporting Devices

Outlet Box Supporting Devices

Hanger Rods

Fasteners

Framing Channel Systems

Fabricated Supporting Devices

Support of Boxes and Cabinets

      - ***************************************************************************************

      - The following is a designer-choice, based on if housekeeping pads are a part of the project. Concrete bases must be designed by the Engineer of Record based on the properties of the load to be supported, the properties of the supporting structure, the required anchor bolt embedment lengths, and so forth. Construction details and dimensions for concrete bases must be shown on the Drawings.

      - ***************************************************************************************

Concrete Bases

Related requirements

Section << 01 2500 - Substitution Procedures>>​

Section << 03 3001 - Reinforced Concrete>>

Section ​<< 05 0520 - Post-Installed Concrete and Grouted Masonry Anchors - Normal Confidence>>​

Section ​​​<< 05 0521 - Post-Installed Concrete Anchors - Nuclear Safety>>​​​

Section << 26 0533 - Raceways and Boxes for Electrical Systems>>.

REFERENCE STANDARds

ASTM A307 - Standard Specification for Carbon Steel Bolts, Studs, and Threaded Rod 60 000 PSI Tensile Strength.

ICC (IBC) - International Building Code.

ICC-ES - International Code Council - Evaluation Service.

MFMA-4 - Metal Framing Standards Publication.

NECA 1 - Standard for Good Workmanship in Electrical Construction.

NFPA 70 - National Electrical Code.

QUALITY ASSURANCE

Furnish and install hangers and supports that conform to the requirements of the following codes and standards:

<<NFPA 70>>

<<ICC (IBC)>>

<<NECA 1>>

<<MFMA-4>>

      - ***************************************************************************************

      - The following is a designer-choice. In most cases, this Article should be omitted as these are, generally, commodity items. If there is a special hanger or support, the Engineer of Record might want to have this reviewed. In this case, specify the particular item in the bracket.

      - ***************************************************************************************

ACTION SUBMITTALS

Submit the following in accordance with project submittal procedures.

Catalog Data: Submit catalog data for ​<< each type of product specified; or  _______>>​. Include information substantiating equivalent corrosion resistance to zinc coated steel of alternative treatment, finish, or inherent material characteristic.

DELIVERY, STORAGE, AND HANDLING

Receive, store, and protect products according to <<NECA 1>>.

PART 2 - PRODUCTS

PRODUCT OPTIONS AND Substitutions

Alternate products may be accepted; follow Section << 01 2500 - Substitution Procedures>>.

COATINGS and Materials

Furnish products for use indoors protected with zinc coating or with treatment of equivalent corrosion resistance using approved alternative treatment, finish, or inherent material characteristic.

Furnish products for use outdoors or in damp or corrosive indoor locations with hot-dip galvanized coating or with treatment of equivalent corrosion resistance using approved alternative treatment, finish, or material such as stainless steel with inherent corrosion resistant characteristics.

RACEWAY SUPPORTING DEVICES

Furnish supports as described below for the installation of raceway systems.

Use pressed steel, conduit hangers to support individual RMC, IMC, or EMT raceways from threaded rods or beam clamps.

Manufacturer: Steel City “6H_ B Series,” or equivalent.

For individual runs of EMT up to trade size 1, above accessible ceilings, use spring steel conduit clips with positive snap closure.

Manufacturer: ERICO CADDY “M Series,” or equivalent.

Use malleable iron conduit clamps to secure individual RMC, IMC, or EMT raceway runs across, parallel, or perpendicular to beams, channels and angle supports.

Manufacturer: Steel City “RC, EC, and PC Series,” or equivalent.

Use two-piece carbon steel riser clamps for individual vertical raceways passing through floors.

Manufacturer: Kindorf “C-210 Series,” or equivalent.

Use snap-on type, one-hole steel straps to secure individual raceways up to trade size 2 to flat, dry interior surfaces.

Manufacturer: T&B “1210 Series” for RMC and IMC, and “4100 Series” for EMT, or equivalent.

Use one-hole straps to secure individual raceways up to trade size 4 to flat, dry interior surfaces.

Manufacturer: T&B “1275 Series,” or equivalent.

Use one-hole straps and backing plates to secure individual conduits to flat exterior or damp flat interior surfaces.

Manufacturer: T&B “1275 Series” straps with 1350 Series” spacers, or equivalent.

OUTLET BOX SUPPORTING DEVICES

Furnish prefabricated sheet steel brackets to support outlet boxes from metal studs in dry-wall construction.

Single outlet boxes: Provide brackets that are inset to allow for dry-wall ring and have a far-side support leg.  Manufacturer: ERICO CADDY “H Series” or “MEB1” attached with “SMS8” low-profile, self-tapping screws, or equivalent.

Multiple outlet boxes: Provide brackets that are inset to allow for dry-wall rings and span from stud to stud.  Manufacturer: ERICO CADDY “RBS Series” attached with “SMS8” low-profile, self-tapping screws, or equivalent.

HANGER RODS

Furnish mild steel rods that conform to <<ASTM A307>>, 60 000 PSI Tensile Strength.

Furnish rods that are threaded on both ends, threaded on one end, or continuous threaded with UNC (coarse) thread pitch.

Fasteners

Pre-set Concrete Inserts

Furnish pre-set concrete inserts as shown on the Drawings.

Manufacturers:

Continuous inserts for wood forms: B-Line “B22I-12” or longer.

Spot inserts for wood forms or metal decks: B-Line “B2500” with “N2500” nut, “B2501”

Post-installed Concrete Anchors

Furnish post-installed expansion, adhesive, or undercut concrete and masonry anchors as shown on the Drawings and Section ​​​​​<< 05 0520 - Post-Installed Concrete and Grouted Masonry Anchors - Normal Confidence; or  05 0521 - Post-Installed Concrete Anchors - Nuclear Safety>>​​​​​.

Power-actuated threaded studs: Use zinc-plated carbon steel or stainless steel suitable for the intended service:

1/4-20 threaded stud: Manufacturer: Hilti X-W6.

3/8-16 threaded stud: Manufacturer: Hilti W10.

Beam Clamps:

Furnish beam clamps that are NRTL-listed and compliant with Federal Specification WW-H-171E Type 23 or Manufacturers’ Standardization Society SP-69 and SP-58 Type 23.

Provide beam clamps with a locknut on the setscrew.

Provide NRTL-listed restraining strap for each beam clamp. Strap shall be not less than 16-gauge thickness, not less than 1 inch wide, and of sufficient length to wrap around the beam flange not less than 1 inch.

      - ***************************************************************************************

      - ML-1/2 caution on U-channel systems when using an upgraded version of this section (or if specifying in other sections) for SC/SS nuclear safety related installations:

      - Based on TRP II project experience, projects should not purchase B-Line (and possibly not competitor) products through a typical distributor who is on the LANL Institutional Evaluated Suppliers List (IESL) (LANL access only) and consider it as meeting NQA-1, due to material traceability problems.  Instead, use the Commercial Grade Dedication method for all safety credited components and have sufficient testing and documentation with traceability to allow use.  The exception may be Unistrut when NOVA Machine Products, their sole IESL/NQA-1 nuclear-pedigree-line distributor is utilized (verify on current IESL).

      - ***************************************************************************************

FRAMING CHANNEL SYSTEMS

Furnish U-channel framing systems that conform tare fabricated using minimum 12-gauge steel.

Furnish fittings and accessories that mate and match with U-channel and are of the same manufacturer. Use two-piece, single bolt type conduit straps on U-channel supports.  In existing buildings, where items from the same manufacturer are not available, fittings and accessories that mate and match are acceptable.

Manufacturers: Unistrut, B-Line, Superstrut.

FABRICATED SUPPORTING DEVICES

Furnish shop- or field-fabricated supports or manufactured supports assembled from U-channel components.

Furnish steel brackets fabricated from angles, channels, and other standard structural shapes.  Connect with welds, machine bolts, or both to form rigid supports.

PART 3 - EXECUTION

GENERAL

Install hangers and supports according to <<NFPA 70>>, <<ICC (IBC)>>, <<NECA 1>>, the requirements in this Section, and specific supporting requirements in other Sections.

Conform to manufacturer's instructions and recommendations for selection and installation of hangers and supports.

Do not use wire or perforated strap for permanent supports.

Refer to Section << 26 0533 - Raceways and Boxes for Electrical Systems>> for required flexible sections.

Do not support boxes, or raceways from ceiling suspension wires.

EXAMINATION

Examine surfaces to receive hangers and supports for compliance with installation tolerances and other conditions affecting performance of the system.  Do not proceed with installation until unsatisfactory conditions have been corrected.

FASTENERS

      - ***************************************************************************************

      - Select either "pre-set inserts" or "post-installed concrete anchors," as appropriate for the project. It is typical for the anchors to be post-installed. In some cases, both will be omitted. Confirm with structural as to who should specify this.

      - ***************************************************************************************

Pre-set inserts: Install pre-set inserts, in accordance with design drawings or as specified by structural engineering, for anchoring to reinforced concrete slabs, sides of reinforced concrete beams, and reinforced concrete walls.

      - *** OR ***

Post-installed concrete anchors: Install in accordance with Section ​​<< 05 0520 - Post-Installed Concrete and Grouted Masonry Anchors - Normal Confidence; or  05 0521 - Post-Installed Concrete Anchors - Nuclear Safety>>​​ and the product's <<ICC-ES>> report conditions of use.

Masonry screw anchors: Use in accordance with <<NECA 1>> and the product’s <<ICC-ES>>​ conditions of use.

Powder-actuated threaded studs:

Use only to fasten clips or straps for individual RMC or IMC conduits trade size 1.5 and smaller or EMT trade size 2.5 and smaller.

Install in accordance with the product’s <<ICC-ES>>​ conditions of use and the manufacturer’s instructions using recommended tools and loads.

Use only in uncracked concrete.

Install to provide embedment as indicated on the Drawings.

Hollow wall anchors: Use hollow wall anchors for fastening to wallboard, or paneling.

Toggle bolt anchors: Use toggle bolt anchors for fastening to block, wallboard, or plaster.

Use wood screws for fastening to wood construction.

Use beam clamps for fastening to structural metal beams, joists, and purlins.

Install a restraining strap at each beam clamp. Wrap the restraining strap around the beam flange not less than 1 inch. Where purlins or beams do not provide a secure lip for the restraining strap, secure the strap with a self-tapping screw or by through-bolting.

Use a locknut on each beam clamp set screw.

Use self-tapping screws or machine bolts, nuts, and washers for fastening to metal studs or metal surfaces.

The use of lead-cinch drop-in anchors is not allowed.

Torque threaded fasteners as recommended by the manufacturer’s instructions.

RACEWAY SUPPORTS.

Install individual and multiple (trapeze) raceway hangers and riser clamps as necessary to support raceways.  Provide U-bolts, clamps, attachments, and other hardware necessary for hanger assembly and for securing hanger rods and conduits.

Support three or more parallel runs of horizontal raceways together on trapeze hangers.

Support individual horizontal raceways by separate conduit hangers.

Do not support raceways from ceiling suspension wires.

support of BOXES AND CABINETS

Support sheet metal boxes directly from the building structure, or by approved brackets or bar hangers, as shown on the Drawings or as required.  Where bar hangers are used, attach the bar to structure on opposite sides of the box.

Install surface-mounted cabinets and panelboards as shown on the Drawings or as required.

Framing Channel Systems

Use framing channel to support electrical equipment that is mounted free of walls.

Use framing channel to support equipment mounted on walls that do not have sufficient strength to resist pull-out or wallowing out of equipment mounting bolts.

      - ***************************************************************************************

      - The following Article is automatically activated when the corresponding paragraph is activated in Article SECTION INCLUDES.  Concrete bases must be designed by the Engineer of Record based on the properties of the load to be supported, the properties of the supporting structure, the required anchor bolt embedment lengths, etc. Construction details and dimensions for concrete bases must be shown on the Drawings.

      - ***************************************************************************************

CONCRETE BASES

Install a reinforced concrete base for each piece of floor-mounted electrical equipment. Refer to Section << 03 3001 - Reinforced Concrete>>, for materials and installation requirements.

Form concrete equipment bases using framing lumber with form release compounds.

Construct concrete bases as shown on the Drawings and not less than 4 inches high and not less than 4 inches larger in both directions than the supported equipment.

Place pre-set anchors, conduits, and sleeves using the equipment manufacturer's installation template or instructions. Install post-installed anchors in accordance with FASTENERS article above.

Place concrete and provide a steel trowel finish on top; chamfer top edges and corners.

Cure concrete not less than seven days before installing equipment.

HANGER RODS

Use minimum 3/8-inch diameter threaded rod; use larger diameter rod as indicated on the Drawings, in other Sections, or in the supported equipment manufacturer’s installation instructions.

Install a locknut at every hanger rod connection.

Where threaded rod supports slotted channel, use a nut and helical split ring lock washer on both the top and bottom of the slotted channel.

END OF SECTION

    - *********************************************************************************************

      - Do not omit the following reference information:

    - *********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 26 0529, REV. 8, DATED APRIL 15, 2026.