Section 26 0533 
Raceways and Boxes for Electrical Systems

  - ***********************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 11 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Electrical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality Sections.

      - ==========================================================

      - Seismic: To edit this section for job-specific seismic requirements, refer to author notes that begin with “Seismic”. Also, see the Seismic Specification Guide for Mechanical Non-Structural Components webposted with the LANL Master Specifications here for guidance on properly editing this section.

      - Raceways Trade Size 2 and smaller are exempt from Seismic design per ASCE 7, Section 13.6.5. Raceways Trade Size 2.5 and smaller are considered flexible and do not need flexible connections to equipment.

  - ************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

      - ***************************************************************************************

      - The following paragraphs are designer-choices based on project-specific requirements.  As many raceways are field-routed, the designer will not know ahead of time if a particular device/component/raceway/fitting will be used on a project.  One way to handle this is to select everything in this article, except for only those items where it is known for certain that they will not be used.

      - ***************************************************************************************

Coatings and finish

Electrical metallic tubing and fittings

Intermediate metal conduit and fittings

Rigid metal conduit and fittings

Rigid polyvinyl chloride conduit and fittings

Flexible metal conduit and fittings

Liquid-tight flexible metal conduit and fittings

Reinforced thermosetting resin conduit

Insulating Bushings

Grounding bushings

Expansion fittings

Raceway seals

Concrete Encasement

Firestopping

Corrosion protection tape

      - ***************************************************************************************

      - Raceway measuring tape is typically only used when one company installs the raceway and a different company installs the conductors.

      - ***************************************************************************************

Raceway measuring tape

Surface metal raceway

Power and communications surface metal raceway

Wireway

Outlet boxes

Recessed floor boxes

Multi-service recessed floor boxes

Pull and junction boxes

RELATED REQUIREMENTS

Section << 01 2500 - Substitution Procedures>>

Section << 01 3300 - Submittal Procedures>>

Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>​

Section << 03 3053 - Miscellaneous Cast-in-Place Concrete>>​

Section << 07 8400 - Firestopping>>

Section ​<< 26 0526 - Grounding and Bonding for Electrical Systems>>​

Section << 26 0529 - Hangers and Supports for Electrical Systems>>

Section << 26 0548.16 - Seismic Controls for Electrical Systems>>

Section << 26 0553 - Identification for Electrical Systems>>​

Section << 26 2726 - Wiring Devices>>

Section << 27 3000 - Voice Communications>>

Section << 28 4600 - Fire Detection and Alarm>>

Section << 33 7119 - Electrical Underground Ducts and Manholes>>

REFERENCE Standards

ANSI C80.1 - American National Standard for Electrical Rigid Steel Conduit (ERSC).

ANSI C80.3 - American National Standard for Electrical Metallic Tubing -- Steel (EMT-S).

ANSI C80.6 - American National Standard for Electrical Intermediate Metal Conduit.

NECA 1 - Standard for Good Workmanship in Electrical Construction.

NECA 101 - Standard for Installing Steel Conduits (Rigid, IMC, EMT).

NECA 111 - Standard for Installing Nonmetallic Raceways (RNC, ENT, LFNC).

NEMA FB 1 - Fittings, Cast Metal Boxes, and Conduit Bodies for Conduit, Electrical Metallic Tubing, and Cable.

NEMA OS 1 - Sheet-Steel Outlet Boxes, Device Boxes, Covers, and Box Supports.

NEMA OS 3 - Selection and Installation Guidelines for Electrical Outlet Boxes.

NEMA TC 2 - Electrical Polyvinyl Chloride (PVC) Conduit.

NEMA TC 3 - Polyvinyl Chloride (PVC) Fittings for Use with Rigid PVC Conduit and Tubing.

NFPA 70 - National Electrical Code.

SCTE 77 - Specifications for Underground Enclosure Integrity.

UL 1 - Flexible Metal Conduit.

UL 5 - Surface Metal Raceways and Fittings.

UL 6 - Electrical Rigid Metal Conduit-Steel.

UL 50 - Enclosures for Electrical Equipment, Non-Environmental Considerations.

UL 360 - Liquid-Tight Flexible Metal Conduit.

UL 498 - Attachment Plugs and Receptacles.

UL 514A - Metallic Outlet Boxes.

UL 514B - Conduit, Tubing, and Cable Fittings.

UL 514C - Nonmetallic Outlet Boxes, Flush-Device Boxes, and Covers.

UL 651 - Schedule 40, 80, Type EB and A Rigid PVC Conduit and Fittings.

UL 797 - Electrical Metallic Tubing-Steel.

UL 1203 - Explosion-Proof and Dust-Ignition-Proof Electrical Equipment for Use in Hazardous (Classified) Locations.

UL 1242 - Electrical Intermediate Metal Conduit-Steel.

UL 2420 - Belowground Reinforced Thermosetting Resin Conduit (RTRC) and Fittings.

UL 2515 - Aboveground Reinforced Thermosetting Resin Conduit (RTRC) and Fittings.

      - ***************************************************************************************

      - The following Article "Action Submittals" is a designer-choice and applies to floor boxes, surface metal raceways, and wireways.  Include the items that are present on the project.

      - ***************************************************************************************

ACTION SUBMITTALS

Submit the following in accordance with Section << 01 3300 - Submittal Procedures>>. Include data substantiating that materials comply with specified requirements.

Catalog data describing floor boxes

Catalog data describing surface metal raceways

Catalog data describing wireways

QUALITY ASSURANCE

Comply with <<NFPA 70>> for unlisted components and for installation requirements.

Provide products that are listed and labeled by a Nationally Recognized Testing Laboratory (NRTL) where such products are required by <<NFPA 70>> to be listed, or where such products contain an electrical hazard as follows:

For AC circuits – Greater than 50 volts

For DC circuits and/or batteries – Greater than 100 volts.

​delivery, storage, and handling

Receive, store, protect, and handle products according to <<NECA 1>>.

PART 2 - PRODUCTS

    - **********************************************************************************************

      - The following Article is designer-choice; retain when substitutions are permitted on project.

    - **********************************************************************************************

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section << 01 2500 - Substitution Procedures>>.

      - ***************************************************************************************

      - Retain the paragraphs in the following Article that apply. For items that are subject to seismic design requirements, if project specification package includes Section ​​<< 26 0548.16 - Seismic Controls for Electrical Systems>>​​, and if mounting and/or anchorage devices are to be used that differ from those specified in Section ​​<< 26 0548.16 - Seismic Controls for Electrical Systems>>​​, they must be described herein (in PART 2).

      - Seismic: See Seismic Specification Section Guide for editing guidance. If either paragraph in Article Seismic Performance Requirements below apply, and there are too many systems/components to list here, then list them in an appendix to this section, and add a reference to that appendix in the applicable paragraph below. Designated Seismic Systems (DSS) are rare at LANL, as the entire utility system will be non-functioning after a design event. A DSS must be fed from a seismically credited generator or UPS.

      - Raceways TS2 and smaller are exempt from seismic design. Omit the article below when raceways or boxes are exempt from seismic design.

      - ***************************************************************************************

SEISMIC PERFORMANCE REQUIREMENTS

The raceways, or boxes, shall remain in place without separation of any parts when subjected to the design basis earthquake.

per Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>​.

        - *** OR ***

as represented by the seismic forces derived from the criteria indicated ​<< on the drawings; or  in Section  26 0548.16 - Seismic Controls for Electrical Systems>>​.

The raceway, or boxes, are Designated Seismic Systems and, as such, shall remain in place and be fully operational following the design basis earthquake.

per Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>.

        - *** OR ***

as represented by the seismic forces derived from the criteria indicated ​​​<< on the drawings; or  in Section  26 0548.16 - Seismic Controls for Electrical Systems>>​​​.

FINISHes

Provide products that are identified for the environment in which the products will be installed and used.

The following raceway colors shall only be used for the indicated purposes:

Blue: For building automation systems

Red: For fire alarm systems

Raceways shall not be painted to match the building finish.

      - ***************************************************************************************

      - The following Articles are designer-choices, based on project-specific requirements.

      - ***************************************************************************************

ELECTRICAL METALLIC TUBING AND FITTINGS (EMT)

Furnish galvanized electrical metallic tubing (EMT) that conforms to <<UL 797>> and <<ANSI C80.3>>.

Furnish compression- or set-screw-type fittings that meet <<UL 514B>> and <<NEMA FB 1>>.  Furnish insulated-throat connectors.

INTERMEDIATE METAL CONDUIT AND FITTINGS (IMC)

Furnish intermediate metal conduit (IMC), nipples, elbows, and couplings that conform to <<UL 1242>>  and <<ANSI C80.6>>.

Furnish zinc-plated, threaded, malleable iron fittings and conduit bodies that meet the requirements of <<UL 514B>> and <<NEMA FB 1>>​.

RIGID METAL CONDUIT AND FITTINGS (RMC)

Furnish rigid metal conduit (RMC) that meets the requirements of <<UL 6>> and <<ANSI C80.1>>.

Furnish zinc-plated, threaded, malleable iron fittings and conduit bodies that meet the requirements of <<UL 514B>> and ANSI/<<NEMA FB 1>>.

RIGID POLYVINYL CHLORIDE CONDUIT AND FITTINGS (PVC)

Furnish rigid polyvinyl chloride conduit (PVC) that conforms to <<UL 651>> and <<NEMA TC 2>>.

Furnish non-metallic, solvent-welded socket fittings that meet the requirements of <<UL 514C>> and <<NEMA TC 3>>.

FLEXIBLE METAL CONDUIT AND FITTINGS

Furnish galvanized steel flexible metal conduit that meets the requirements of <<UL 1>>.

Furnish zinc-plated fittings that meet the requirements of <<UL 514B>> and ANSI/<<NEMA FB 1>>.  Furnish insulated throat connectors.

LIQUID-TIGHT FLEXIBLE METAL CONDUIT AND FITTINGS

Furnish liquid-tight flexible metal conduit that meets the requirements of <<UL 360>>.

Furnish zinc-plated malleable iron or zinc-plated steel liquid-tight fittings that meet the requirements of <<UL 514B>> and ANSI/<<NEMA FB 1>>. Furnish insulated-throat connectors.

REINFORCED THERMOSETTING RESIN CONDUIT (RTRC)

      - ***************************************************************************************

      - Note UL 2515 can be used for above or below ground applications, whereas UL 2420 can only be used for below ground applications.

      - ***************************************************************************************

Furnish RTRC that meets the requirements of <<UL 2515>> for above ground or below ground applications.

Furnish RTRC that meets the requirements of <<UL 2420>> for below ground applications only.

INSULATING BUSHINGS

Provide insulating bushings with 105-degrees C-rated insulation.

Manufacturer: O-Z/Gedney, Type IB.

GROUNDING BUSHINGS

Provide 150-degrees C-rated insulated-throat grounding bushings with lay-in type ground cable lugs.

EXPANSION FITTINGS

Furnish expansion fittings with hot dipped galvanized malleable iron body, factory installed packing and a bonding jumper.

Manufacturer: O-Z/Gedney, Type AX, TX or EXE with Type BJ bonding jumper.

RACEWAY SEALS

      - ***************************************************************************************

      - The following paragraphs are designer-choices, based on project requirements.  The first paragraph covers most usages of seals.  Temperature differences, moisture control, and radiological.  The second paragraph is only required for Hazardous (Classified) locations, i.e. explosive locations.

      - ***************************************************************************************

Raceway Sealant for use in temperature differences, radiological, or moisture control

Furnish a two-part, foam-based, duct sealing system.

Provide sealing compound specifically listed for use with the foam damming materials.

Provide sealing compound that is identified for use with the conductor or cable insulation.

Manufacturer: Polywater FST-MINI for raceways up to 2 inches.

Manufacturer: Polywater FST-250 for raceways 2 inches to 8 inches.

Sealing Fittings for Use in Hazardous-Classified Locations

Furnish zinc-plated, malleable iron sealing fittings that meet the requirements of <<UL 1203>>​.

Select each sealing fitting so the cross-sectional area of conductors passing through the seal is not more than 25 percent of the cross-sectional area of a rigid metal conduit of the same trade size unless the fitting is specifically identified for a higher percentage of fill.

Provide sealing compound specifically listed for use with the sealing fitting.

Manufacturer: Crouse-Hinds Type EYS, EYSX, EYD.

CORROSION PROTECTION TAPE

Furnish pressure-sensitive, 10 mil thick. PVC based tape for corrosion protection of metal raceway and fittings.

Manufacturer: 3M, Type 50.

RACEWAY MEASURING TAPE

Furnish raceway measuring tape with permanently printed measurements in one-foot increments and minimum 1200 lb. average breaking strength.

Manufacturer: Greenlee “39243”.

SURFACE METAL RACEWAY

Furnish surface metal raceway that meets the requirements of <<UL 5>>​.

Furnish surface metal raceway fabricated from cold rolled galvanized steel with a thickness of not less than 0.040 inches and coated with a baked enamel finish.

Furnish fittings required for a complete installation.

Manufacturer: Wiremold ​<< 500;  700; or  4000>>​ series.

POWER AND COMMUNICATIONS SURFACE METAL RACEWAY

Furnish power and communications surface metal raceway that meets the requirements of <<UL 5>>.

      - ***************************************************************************************

      - Select one of the following three paragraphs below to match project requirements. Gray is a standard finish; it should be used in utilitarian spaces, where it will match or accent architectural finishes, or where the raceway will be field painted. Ivory should be used where it will match or accent architectural finishes. Stainless steel should be used only in laboratory spaces where there is the possibility of corrosion.

      - ***************************************************************************************

Furnish power and communications surface metal raceway fabricated from cold rolled galvanized steel with a thickness of not less than 0.04 inches and coated with a gray, baked-enamel finish.

      - *** OR ***

Furnish power and communications surface metal raceway fabricated from cold rolled galvanized steel with a thickness of not less than 0.04 inches and coated with a polyester topcoat over an ivory-colored base.

      - *** OR ***

Furnish power and communications surface metal raceway fabricated from Type 304 stainless steel with a thickness of not less than 0.04 inches.

Raceway shall consist of a metal base and a snap-on metal cover.

Nominal dimensions of the assembled raceway shall be 4-3/4 inches wide by 1-3/4 inches high.

Furnish fittings required for a complete installation to include a full-length partition separating the power wiring from the communications cables.​​<< Provide suitable internal fittings to accommodate bending radii for fiber optic cables.; or  None - N/A>>​​​

Provide a plastic snap-in plate for each 36 inches of the power and communications surface metal raceway.  Each snap-in plate shall include one duplex receptacle, if applicable, and one connector faceplate for two RJ11/8P8C telecommunications connectors.

Manufacturer: Wiremold << 4000; or  6000>>.

WIREWAY

Provide << general purpose;  oil-tight and dust-tight; or  rain-tight>> type wireway with covers, elbows, tees, and fittings required for a complete system.

Supply wireway << with manufacturer's standard;  without; or  with bottom only>> knockouts.

Provide 45-degree angle and tee fittings to accommodate bending radii for fiber optic cables.

Manufacturer: Hoffman

OUTLET BOXES

Provide outlet boxes selected for specific installations using the guidance in <<NEMA OS 3>> and the requirements of this Section.

For dry locations provide galvanized steel outlet boxes that comply with <<UL 514A>>  and ANSI/<<NEMA OS 1>>.

For fire detection and alarm device outlets, use boxes specified in Section << 28 4600 - Fire Detection and Alarm>>.

For flush outlets in stud walls or above-grade cast-in-place concrete walls, use 4-inch square or 4-11/16 square boxes; provide deeper boxes or multiple gang boxes as required to fit devices. Provide raised device covers that match the thickness of the wallboard and the number of devices. Provide supplemental box supports to prevent movement of the box.

For flush outlets in above-grade masonry walls use masonry boxes with knockouts. Provide boxes with depth suitable for the masonry unit size. Provide multiple gang boxes as required by the number of devices.

For surface outlet boxes in EMT raceway systems, use 4 inch square or 4 11/16 inch square boxes. Provide deeper boxes or multiple gang boxes as required to fit devices. Provide square surface covers that match the installed device and have not less than two holes for securing the device to the cover. Note: 4 square boxes are also known as 1900 boxes and 4 11/16 square boxes are also known as 2100 boxes.

For damp or wet locations and for surface-mounted RMC or IMC raceway systems, provide outlet boxes that comply with <<UL 498>>, <<UL 514A>>, and ANSI/<<NEMA FB 1>>.

For lighting fixture outlets, use 4-inch round, cast gray or malleable iron boxes with threaded hubs, or as required by the manufacturer.

For flush or surface wall-mounted outlet boxes, use cast gray or malleable iron boxes with threaded hubs. Provide multiple gang boxes as required to fit devices. Provide gasketed cast gray, malleable-iron, or cast copper-free aluminum covers that match the installed device and have not less than two holes for securing the device to the cover.

RECESSED FLOOR BOXES

Provide recessed floor boxes with threaded conduit entrances for use in floor slabs on grade or below grade. Floor boxes in suspended floor slabs may be the formed steel type.

Provide fully adjustable floor boxes as follows:

External means to adjust the height of the box before concrete is placed.

Internal means to adjust the cover to be flush and level with the finished floor after the flooring material is placed.

Provide floor boxes with brass covers as required for the system or device to be installed in the box.

Provide carpet flanges or covers with integral carpet flanges for floor boxes in carpeted areas.

Manufacturer: Hubbell

MULTI-SERVICE RECESSED FLOOR BOXES

Provide fully adjustable multi-service recessed floor boxes for use in floor slabs on grade or below grade. Multi-service floor boxes in suspended floor slabs may be the formed steel type.

Provide multi-chamber floor boxes with provisions for routing wires between chambers.

Provide service plates as required for the systems or devices to be installed in the floor box.

Provide flush covers with integral carpet flange and cable doors.

Manufacturer: Hubbell

PULL AND JUNCTION BOXES

For pull and junction boxes, <<NFPA 70>> size requirements must be met:

For conductors 6 AWG and smaller, meet <<NFPA 70>> 314.16

For conductors 4 AWG and larger, meet <<NFPA 70>> 314.28

      - ***************************************************************************************

      - The drawings show raceway sizes, but conduit bodies are not raceways.  For example, if a drawing shows that the raceway size should be 1.5 inches, it doesn't mean that a 1.5 inch conduit body can be used.  In fact, for conductor sizes 4 AWG and larger, conduit bodies are almost always Code violations.  Sometimes, Mogul conduit bodies will fit the requirements, but for every instance that a conduit body will be used, the calculations must be made to ensure Code compliance.

      - ***************************************************************************************

Conduit bodies are acceptable if the above requirements, in <<NFPA 70>>, are met.

For dry locations in clean, non-contaminated environments, use galvanized sheet steel pull and junction boxes that comply with <<UL 50>>​ Type 1.

For dry locations in dusty or possible contamination (e.g., beryllium, explosives, or uranium) environments, use galvanized steel pull and junction boxes that comply with <<UL 50>>  Type 12. Use boxes not less than 6 inches square x 4 inches deep with gasketed covers. Provide larger boxes as required by the number and size of raceways and conductors.

For damp or wet, non-corrosive locations, in raceway runs up to trade size 3/4, provide cast gray or malleable iron pull and junction boxes with threaded hubs and gasketed cast gray or malleable iron or cast copper-free aluminum covers.

For damp or wet, non-corrosive locations, in raceway runs trade size 1 and larger, provide galvanized sheet-steel pull and junction boxes and covers that comply with <<UL 50>> Type 3R.

For damp or wet, non-corrosive locations that are subject to hose-directed water, provide pull and junction boxes and covers that comply with <<UL 50>>Type 4.

For damp or wet, corrosive locations provide pull and junction boxes and covers that comply with <<UL 50>> Type 4X.

For locations subject to occasional submersion, provide pull and junction boxes and covers that comply with <<UL 50>> Type 6.

For in-ground flush-mounted cast metal boxes, provide <<UL 50>> Type 6 boxes with flanged, recessed cover.

Material: Galvanized cast iron or galvanized gray or malleable iron.

Cover: Non-skid cover with neoprene gasket and stainless-steel screws.

Identification: Permanent mark or logo on cover prominently identifying the function of the enclosure.

For in-ground, non-metallic, open-bottom handholes, use products that are NRTL-listed to ANSI/<<SCTE 77>>.

Material: Polymer concrete.

Minimum ANSI/<<SCTE 77>> load rating:

Located in sidewalks: Tier 8.

Located in driveways, parking lots, and off-roadway locations: Tier 15.

Size: Up to 30 inches x 48 inches

Cover: Non-skid cover with stainless steel cover bolts.

Identification: Permanent mark or logo on cover prominently identifying the function of the enclosure.

Manufacturer: Quazite “Style PC, PG, or PT”

PART 3 - EXECUTION

    - **********************************************************************************************

      - For raceways or boxes that are subject to seismic design, if project specification package includes Section << 26 0548.16 - Seismic Controls for Electrical Systems>>, and if requirements associated with installation, testing, and inspection of mounting and/or anchorage devices differ from those requirements in Section << 26 0548.16 - Seismic Controls for Electrical Systems>>, they must be described herein (in PART 3).  Also, if this is applicable, identify special types of seismic-control devices required for each application using the same terminology used for those devices in PART 2.

      - The following Article is a designer-choice​ and applies to existing work.

    - **********************************************************************************************

EXISTING WORK

Cap, plug, or seal remaining raceway openings to restore the original fire rating​​<< and acoustical STC rating; or  None - N/A>>​​ of floors, walls, and ceilings after electrical demolition. Patch surfaces to match existing.

Maintain access to existing boxes and other installations remaining active and requiring access. Modify installation or provide access panel.

Extend existing raceway and box installations using materials and methods ​​<< compatible with existing electrical installations, or; or  None - N/A>>​​ as specified.

Clean and repair existing raceway and boxes that are to remain or to be reinstalled, as a part of the job scope.

EXAMINATION

Examine surfaces to receive raceways and boxes for compliance with installation tolerances and other conditions affecting performance of the raceway system. Do not proceed with installation until unsatisfactory conditions have been corrected.

GENERAL

Install complete systems of raceways and boxes for wiring systems.

Install raceways and boxes according to <<NECA 1>>, <<NECA 101>>, <<NECA 111>>, <<NFPA 70>>, the manufacturer’s instructions, and requirements in this Section.

Raceway termination points and box locations shown on the drawings are in approximate locations unless dimensioned. Verify locations before rough-in.

Raceway routing is shown on the drawings in approximate locations unless dimensioned.  Coordinate routing with structure and with work of other trades. Route as required for a complete wiring system.

Ground and bond raceways and boxes as required in Section << 26 0526 - Grounding and Bonding for Electrical Systems>>​.

      - ***************************************************************************************

      - If the entirety of the raceway is exempt from seismic design, then only Section ​<< 26 0529 - Hangers and Supports for Electrical Systems>>​ in the following paragraph is applicable.  If only some of the components are exempt, then Sections ​<< 26 0529 - Hangers and Supports for Electrical Systems>>​ & ​<< 26 0548.16 - Seismic Controls for Electrical Systems>>​ or ​<< 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>​ are applicable.  Regarding the applicability of Section ​<< 26 0548.16 - Seismic Controls for Electrical Systems>>​ or ​<< 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>​​, see Seismic Specification Editing Guide for editing guidance.  Raceways TS2 and smaller are exempt from seismic design.

      - ***************************************************************************************

Support raceways and boxes in accordance with the requirements of <<NFPA 70>>; Section << 26 0529 - Hangers and Supports for Electrical Systems>><< ; and, if applicable, Section 26 0548.16 - Seismic Controls for Electrical Systems;  ; and, if applicable, Section  01 8734 - Seismic Qualification of Nonstructural Components (IBC); or  None - N/A>>.

Identify raceways and boxes as required in Section ​<< 26 0553 - Identification for Electrical Systems>>​​.

Arrange raceway and boxes to maintain headroom and present neat appearance.

Install knockout closures in unused openings in boxes or raceways.

      - ***************************************************************************************

      - The following Articles are designer-choices (except Field Quality Control and Cleaning), based on project-specific requirements.

      - ***************************************************************************************

RACEWAY INSTALLATION

For low-voltage wiring systems (less than 1000 volts), use raceway materials according to <<NFPA 70>>  and the following:

Outdoors–Underground:

Direct buried: Use PVC, RTRC, tape-wrapped RMC, or tape-wrapped IMC. Do not use PVC where subject to physical damage. Install with 24 inches minimum cover from top of raceway to finished grade or top of paving.

Concrete encased: Use PVC, RTRC, RMC, or IMC for concrete encased underground work. Install with 24 inches minimum cover from top of encasement to finished grade or paving.

Align and support ducts to prevent trapping moisture at any point.

Risers.  Use RTRC for risers into equipment, from underground runs.  RTRC elbows do not have the burn through issues that PVC has.  RTRC is non-metallic and, therefore, does not need to be bonded to the equipment.  RTRC also has a lower coefficient of friction, for pulling, than PVC has.

Outdoors–Exposed: Use RMC or IMC.

Outdoor corrosive locations (including cooling towers): Use RTRC.

Outdoors–in contact with earth: Do not use bare RMC or IMC in direct contact with earth. EMT may be used for concealed outdoor work where not in contact with earth, not encased in concrete, and where not exposed to deteriorating agents.

Indoors–Exposed outside of designated electrical rooms or telecommunications rooms:

Exposed to severe physical damage during or after installation: Use RMC or IMC.

Exposed to moisture: Use RMC or IMC.

Exposed to corrosives: Use RTRC.

Not exposed to deteriorating agents and not subject to severe physical damage during or after installation: Use RMC, IMC, or EMT.

Indoors–Concealed:

Within drywall partitions and above false ceilings: Use RMC, IMC or EMT.

Within masonry or cast-in-place concrete walls or floors: Use RMC or IMC.

Direct-buried under building floor slabs on grade: Use PVC, RTRC, tape-wrapped RMC, or tape-wrapped IMC. Locate top of raceways not less than 12 inches below the bottom of the concrete slab. Install warning tape approximately 6 inches above the raceways; install multiple warning tapes above parallel raceway runs wider than 18 inches.

Concrete encased under building floor slabs on grade: Use PVC, RTRC, RMC, or IMC. Locate top of concrete encasement not less than 12 inches below the bottom of the concrete slab.

        - ******************************************************************************

        - Seismic:  Having flexible connections (between the boxes, or rigid raceways, and other nonstructural components to which these are associated) are one of the requirements for seismic design.  Ensure such connections are indicated on the drawings in the applicable location(s).  Raceways TS2.5 and smaller are considered flexible and do not require flexible raceway at connections.

        - Regardless of whether the system is exempt from seismic, flexible connections shall be used at seismic-control joints.

        - ******************************************************************************

Install flexible raceway segments where flexibility is required after installation.  For example, raceways that cross expansion joints or seismic joints, where they are attached to parts of the structure with a potential for differential seismic displacement, and where they connect to equipment with designed anchors (seismic controls) or vibration isolators. Refer to Section << 26 0529 - Hangers and Supports for Electrical Systems>> and Section << 26 0548.16 - Seismic Controls for Electrical Systems>>.  This does not apply to flexible raceways that are installed for the ease of installation, where flexibility after installation is not required.

For raceway systems larger than Trade Size 2 1/2, install a minimum of 4 feet of flexible raceway. Note:  Raceways that are Trade Size 2 1/2 or less are considered flexible for the sake of seismic requirements.

          - **********************************************************************

          - For the installation of flexible raceways for the purpose of seismic considerations, accommodate minimum 4 inches of movement unless seismic analysis indicates a larger seismic differential displacement in any direction. Coordinate with Section << 26 0548.16 - Seismic Controls for Electrical Systems>>. Refer to LANL ESM Chapter 5 - Structural and ASCE 7 Chapter 13.

          - **********************************************************************

For installations due to seismic considerations, arrange the flexible raceway sections to accommodate << 4 inches; or  _______>> inches of movement in all directions.

Use liquid-tight flexible metal conduit outdoors, in wet, damp, or corrosive indoor locations. Use flexible metal conduit in dry indoor locations.

Connection to vibrating equipment (including hydraulic, pneumatic, or electric solenoid or motor-driven equipment): Use a minimum of 24 inches:

Outdoors: Use liquid-tight flexible metal conduit.

Wet, damp, or corrosive indoor locations: Use liquid-tight flexible metal conduit.

Dry indoor locations: Use flexible metal conduit.

Connections to luminaires: Use flexible metal conduit, metal-clad cable, or manufacturer’s whips, for conductors to luminaires above suspended ceilings.

For medium-voltage wiring systems (1 kV or greater but less than 100 kV) use raceway materials according the following:

Underground, both outside and inside the perimeter of the building, red-concrete encased: Use PVC, RTRC, RMC, or IMC for concrete encased underground work. Install with 24-inches-minimum cover from top of encasement to finished grade, paving, or building slab.

Indoors or outdoors, concealed or exposed: Use RMC or IMC.

Use trade size 3/4 or larger raceways to enclose multiple conductors larger than 12 AWG.

Use raceways to enclose fire alarm wiring.  See Section << 28 4600 - Fire Detection and Alarm>>​ for size and type of raceways to be used to enclose fire alarm wiring.

Conceal raceways, unless otherwise indicated on the drawings, with finished walls, floors and ceilings.  Unless otherwise indicated on the drawings, install concealed raceways with a minimum of bends in the shortest practical distance considering the type of building construction and obstructions.

Install expansion fittings where raceways cross building expansion joints, or where needed for thermal expansion and contraction.

For calculating where thermal expansion fittings are needed, use a 100 degrees F temperature difference with 0 degrees as the minimum and 100 degrees as the maximum. The gap must be set on the day of installation, based on the temperature at the time of installation.  For example, if the temperature during installation is 50 degrees F, the gap will be set halfway.  If the temperature is 75 degrees F, the gap will be set three-quarters of the way toward the point where the raceways are the closest to each other.

Use sealing locknuts, hubs, or similar water-resistant fittings on raceways entering the top of switchgear, switchboards, motor control centers, panelboards, cabinets, pull boxes, and similar enclosures that are in damp and/or wet locations.

Install raceways as shown on the drawings or with the following limits of bends and distance between pull points:

Less than 50 feet, follow <<NFPA 70>>.

50 feet to 100 feet, a maximum of 3 equivalent 90-degree bends.

100 feet to 150 feet, a maximum of 2 equivalent 90-degree bends.

150 feet to 200 feet, a maximum of with 1 equivalent 90-degree bend.

Over 200 feet, a straight run with no bend.

Stub-Up Connections:

Extend raceways through concrete floor for entry to freestanding equipment with an adjustable top or coupling threaded inside for plugs.

The use of RTRC for risers negates the requirement to bond the risers to the equipment.

Where equipment connections are not made under this Subcontract, install threaded insert plugs.

      - ***************************************************************************************

      - Raceway Sealing refers to injecting a compound into the raceway that surrounds the conductors/cables, for the purpose of mitigating the transfer of water, air, radiological particles, or other materials.

      - Sealing Fittings are manufactured, listed, components that are specifically made for use in Hazardous (Classified) areas.

      - ***************************************************************************************

Raceway Sealing:

A sealing fitting is not required but may be used.  A type C conduit body may also be used as an access point to install the sealing compound.  The sealing compound must be identified for use with the conductor or cable insulation. Sealing shall be provided where required per <<NFPA 70>> and in the following locations:

Raceways enter or leave radiological "controlled areas.”

Raceways pass between areas where air pressure differential must be maintained.

Raceways enter an enclosure protected by a clean-agent, total-flooding fire suppression system.

Locate raceway fittings used for sealing in a suitable, approved, accessible location to provide access to the interior of the raceway to be filled with sealing compound.

Install sealant in accordance with the manufacturer’s written instructions.

Sealing Fittings

Where raceways enter or leave <<NFPA 70>> hazardous locations, as required.

Install raceway sealing fittings according to the manufacturer's written instructions.  Locate fittings at suitable, approved, accessible locations and fill them with the manufacturer’s  sealing compound required by the sealing fitting listing.

      - ***************************************************************************************

      - RTRC is strongly recommended for risers.  As RTRC is non-metallic, it does not require grounding bushings at the equipment.  The elbows do not burn through during pulling, and the coefficient of friction is lower than that of PVC.  Also, in the case of a fault, the conductor will not weld to the raceway.  Neither will the raceway melt.

      - ***************************************************************************************

Join nonmetallic raceways using cement following manufacturer’s installation instructions.

Do not use PVC 90-degree elbows larger than trade size 2. Use RTRC, tape-wrapped RMC, or tape-wrapped IMC for trade size 2.5 and larger 90-degree elbows.

Maintain the following minimum clearances between raceway and surfaces with temperatures exceeding 104 degrees F (40 degrees C):

6 inches at perpendicular crossings.

12 inches between parallel runs.

For outdoor, above-ground installations in damp or wet locations, avoid moisture trapping in raceway systems by arranging raceways to drain.

        - Note: Drains are often created by using conduit bodies at low points in the raceway system. The opening of the conduit body that is used for the drain can either have a drain fitting attached to it or a drain can be made by drilling a hole in a threaded plug.

Install corrosion protection tape on metal raceways and fittings that are in contact with soil using half-lapped wrappings.

Install grounding bushings where required by <<NFPA 70>>​.

When the conductors will be installed by others, Install raceway measuring tape in empty raceways.  Leave not less than 12 inches of slack at each end of the tape.  Secure each end of tape.

CONCRETE ENCASEMENT

Concrete-encase underground low-voltage (less than 1000 volts) electrical service and feeder raceways outside the perimeter of the building foundation, only if indicated on drawings.

Concrete-encase underground medium-voltage (1 kV or greater but less than 100 kV) electrical raceways outside and inside the perimeter of the building foundation. Use red-colored concrete.

Concrete-encase underground electrical branch circuit, communications, and alarm raceways, only if indicated on the drawings.

Provide not less than 3 inches of concrete coverage on all sides of raceways.

Refer to Section << 03 3053 - Miscellaneous Cast-in-Place Concrete>> for basic material and installation requirements. Concrete finishing is not required for this application.

Use a pre-approved concrete mix design that is suitable for exterior use exposed to freezing and thawing.

Use un-colored concrete to encase raceways for low-voltage wiring systems

Use red-colored concrete to encase raceways for medium voltage.

Use 2.0 lb. of pigment per 94 lb. sack of cement.

Manufacturer: Rockwood Industries/Davis Colors, No. 1117.

Refer to Section << 33 7119 - Electrical Underground Ducts and Manholes>> for requirements pertaining to underground ducts for medium-voltage power, telecommunications, and secure communications.

FIRESTOPPING

Install a firestop system at each electrical penetration in a fire-rated wall, floor, or partition.

Refer to Section << 07 8400 - Firestopping>> for materials and installation requirements.

OUTLET BOX INSTALLATION

Install outlet boxes with centers at the following heights unless noted otherwise on the drawings:

Receptacle, telephone, and data outlets:

Common Areas (such as conference and break rooms): 18 inches above finished floor.

Offices and Workstations: 7 inches above finished floor.

Receptacle, telephone, and data outlets at lab benches and counters - use mounting heights specified in Section << 27 3000 - Voice Communications>>.

Light switches: top of outlet box not more than 48 inches above finished floor and within 6 inches of door frame.

Thermostats: top of outlet box not more than 48 inches above finished floor.

Wall-mounted, cord-and-plug-connected emergency lights: 80 inches above finished floor or 12 inches below the ceiling; whichever is lower (to allow bottom of separately-mounted light to be at least 80 inches above floor).

Fire alarm audible/visible alarm devices and pull stations: Use mounting heights specified in Section << 28 4600 - Fire Detection and Alarm>>.

Coordinate outlet box locations with modular furniture and associated hangers.

Where the drawings show outlets as adjacent, align outlet boxes with each other and group them symmetrically.

Orient boxes to accommodate wiring devices oriented as specified in Section << 26 2726 - Wiring Devices>>.

Install a multi-gang box where more than one device is mounted together. Do not use sectional-type boxes.

Install box with plaster ring for single or multiple device outlets.

Use flush mounted outlet boxes in finished areas.

Install flush outlet boxes and fittings in walls and ceilings so that front edge is flush with the finished surface.  Repair broken wall or ceiling surfaces so no gaps or open spaces exceed 1/8 inch at the edge of boxes or fittings.

Locate flush mounting box in masonry wall to require cutting of masonry unit corner only. Coordinate masonry cutting to achieve neat opening.

Do not install flush mounting boxes back-to-back in walls; install with minimum 6 inches separation. Install with minimum 24 inches separation in acoustic rated walls.

Secure flush mounting boxes to interior wall and partition studs. Accurately position to allow for surface finish thickness.

Install stamped steel bridges to fasten multiple flush mounting outlet boxes between studs.

Install flush mounting box without damaging wall insulation or reducing its effectiveness.

Install adjustable steel channel fasteners for hung ceiling outlet box.

Install partitions in boxes as follows:

Between 277-volt devices

Between 277-volt devices and 120-volt devices.

Between low voltage control switches and both 120 volt and 277-volt devices.

Install a blank cover plate on each outlet box in which no device is installed.

FLOOR BOX INSTALLATION

Install floor boxes at locations indicated on the drawings:

Set height of boxes, before concrete, or flooring material, is placed, so cover will be flush with the finished floor surface.

Determine the type and thickness of flooring materials and set height of boxes accordingly.

In setting box heights, account for structural deflection that will occur when concrete is placed.

Install devices, covers, and carpet flanges after flooring materials are installed; adjust boxes so covers are level and flush with flooring material.

PULL AND JUNCTION BOX INSTALLATION

Install pull and junction boxes as shown on the drawings and as required for splices, taps, wire pulling, and compliance with regulatory requirements.

Install indoor pull and junction boxes in accessible locations above accessible ceilings and in unfinished spaces.  Position boxes such that covers can be removed.  Place boxes to maintain headroom.

Install a concrete collar around handholes not placed in sidewalks or pavement.

WIREWAY INSTALLATION

Install wireways at locations indicated on the drawings.

SURFACE METAL RACEWAY INSTALLATION

Install surface metal raceway at locations indicated on the drawings.

FIELD QUALITY CONTROL

Inspect coatings and finishes to detect damage or deterioration.

Inspection Points – Subcontractor to provide not less than 2 working days advance notice to the LANL STR for the LANL inspection points listed in the subparagraphs below. In the notice, identify the specific areas of the project for which LANL owner inspection is requested. Correct deficiencies identified during inspections. If the requested LANL inspection does not occur within 1 working day of the LANL inspection point, work may proceed.

Underground raceways: After raceways have been installed but before concrete-encasement or trench backfilling commences, inspect for:

Correct raceway material and size.

Correct raceway stub-up locations.

Raceway systems in concrete walls, floors, slabs, and equipment pads: After raceways and boxes have been installed but before concrete placement commences, inspect for:

Correct raceway system materials and sizes.

Correct raceway stub-up locations.

Correct floor box locations and proper height setting,

Correct outlet box locations.

Raceway systems in drywall partitions: After raceways and boxes have been installed but before drywall installation that would cover the raceway system commences, inspect for:

Correct raceway system materials and sizes.

Correct outlet box locations and proper depth setting.

Raceway systems above ceilings: After raceways and boxes have been installed but before ceiling system installation commences, inspect for:

Correct raceway system materials and sizes,

Correct outlet box locations and proper depth setting.

CLEANING

Clean interior of boxes to remove dust, debris, and other material.

Repair damage to galvanized finishes with zinc-rich paint recommended by manufacturer.

Repair damage to paint finishes with matching touch-up coating recommended by the manufacturer.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

  - THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 26 0533, REV. 11, DATED APRIL 15, 2026.