Section 26 0536 
Cable Trays for Electrical Systems

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 6 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Electrical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality Sections.

      - Seismic: If the cable tray is subject to seismic design, prior to attempting to edit this Section to be Project-specific, refer to Sections << 26 0548.16 - Seismic Controls for Electrical Systems>>, and << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>, as applicable.

  - ************************************************************************************************************

PART 1 - GENERAL

Section Includes

Metal cable tray and fittings.

      - ***************************************************************************************

      - Retain the following paragraphs that are part of this project.  Activating these will activate the corresponding articles/paragraphs in PART 2.

      - ***************************************************************************************

Cable Tray Ground Clamps

Cable Tray/Conduit Bonding Clamps

RELATED Requirements

Section ​<< 01 2500 - Substitution Procedures>>​

Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>

Section ​<< 26 0548.16 - Seismic Controls for Electrical Systems>>​

reference standards

ASTM A123/A123M - Standard Specification for Zinc (Hot-Dip Galvanized) Coatings on Iron and Steel Products.

ASTM A1011/A1011M - Standard Specification for Steel, Sheet and Strip, Hot-Rolled, Carbon, Structural, High-Strength Low-Alloy, High-Strength Low-Alloy with Improved Formability, and Ultra-High Strength.

ASTM B633 - Standard Specification for Electrodeposited Coatings of Zinc on Iron and Steel.

ASTM F1136/F1136M - Standard Specification for Zinc/Aluminum Corrosion Protective Coatings for Fasteners.

NECA 1 - Standard for Good Workmanship in Electrical Construction.

NECA/NEMA 105 - Standard for Installing Metal Cable Tray Systems.

NEMA BI 50015 - Metal Cable Tray Systems.

NEMA BI-50016 - Cable Tray Installation Guidelines.

NFPA 70 - National Electrical Code.

ACTION SUBMITTALS

Submit the following in accordance with Project submittal procedures:

Catalog Data:  Submit manufacturer's data on cable tray including, but not limited to, types, materials, finishes, rung spacing, tray dividers, inside depths and fitting radii.

Installation Instructions:  Indicate application conditions and limitations of use stipulated by Product testing agency specified under Regulatory Requirements.  Include instructions for storage, handling, protection, examination, preparation, and installation of Product.

REGULATORY REQUIREMENTS

Conform to requirements of <<NFPA 70>> for installation requirements.

Conform to applicable requirements of <<NEMA BI 50015>>, and <<NEMA BI-50016>>.

Listing requirements.

Cable tray systems are not required to be listed, unless called out in this Section.

COORDINATION

Coordinate cable tray, hangers, and accessories with other construction that penetrates ceilings or floors or is supported by them, including luminaires, HVAC equipment and ductwork, fire-suppression system, and partition assemblies.

Coordinate penetrations through credited firewalls.  Use listed fire stopping systems appropriate for the number of cables/conductors.

DELIVERY, STORAGE, AND HANDLING

Receive, store, and protect, and handle products according to <<NECA 1>>, and <<NECA/NEMA 105>>.

PART 2 - PRODUCTS

    - **********************************************************************************************

      - Retain the following article if substitutions are allowed for this project.

    - **********************************************************************************************

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section << 01 2500 - Substitution Procedures>>.

      - ***************************************************************************************

      - Seismic: See Seismic Specification Section Guide for editing guidance. If either paragraph in Article Seismic Performance Requirements below apply, and there are too many systems/components to list here, then list them in an appendix to this section, and add a reference to that appendix in the applicable paragraph below. Designated Seismic Systems (DSS) are rare at LANL, as the entire utility system will be non-functioning after a design event. A DSS must be fed from a seismically credited generator or UPS. It should be sufficient for Cable Trays to have positional retention (paragraph A) as Cable Trays have no function, other than to support conductors.

      - If this applies, edit it in accordance with content of << 26 0548.16 - Seismic Controls for Electrical Systems>>​ and/or << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>.

      - ***************************************************************************************

SEISMIC PERFORMANCE REQUIREMENTS

The cable tray shall remain in place without separation of any parts when subjected to the design basis earthquake.

Per Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>.

        - *** OR ***

As represented by the seismic forces derived from the criteria indicated ​<< on the drawings; or  in Section  26 0548.16 - Seismic Controls for Electrical Systems>>​.

The cable tray is a Designated Seismic System and, as such, it shall remain in place and be fully operational following the design basis earthquake

Per Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>.

        - *** OR ***

As represented by the seismic forces derived from the criteria indicated << on the drawings; or  in Section  26 0548.16 - Seismic Controls for Electrical Systems>> .

METAL CABLE TRAY

Provide metal cable tray and accessories conforming to <<NEMA BI 50015>>​​​​​​​, <<NFPA 70>>, and this Section.

Cable trays shall be of types, classes and sizes indicated on the Drawings or specified, complete with splice plates, bolts, nuts and washers for connecting units.

      - ***************************************************************************************

      - Edit the following paragraph to match project conditions.

      - Cable trays, under almost all circumstances, will be subject to seismic design. The designer will have to know the load on each cable tray support, due to both the weight of the tray and the contents (cables).

      - ***************************************************************************************

Cable tray shall be capable of carrying not less than the following uniformly distributed and concentrated loads at the rated support span with a safety factor of 1.5 when supported as a simple span and tested per <<NEMA BI 50015>> Section 5.2.  Load and safety factors are applicable to both side rails and rung capacities.

6 and 12 inch widths: 50 lb. per linear foot.

Class 8A with a support span of 8 feet

Class 12A with a support span of 12 feet

Class 16A with a support span of 16 feet

Class 20 A with a support span of 20 feet.

18 and 24 inch widths: 75 lb. per linear foot

Class 8B with a support span of 8 feet

Class 12B with a support span of 12 feet

Class 16B with a support span of 16 feet

Class 20 B with a support span of 20 feet.

30 and 36 inch widths: 100 lb. per linear foot

Class 8C with a support span of 8 feet

Class 12C with a support span of 12 feet

Class 16C with a support span of 16 feet

Class 20 C with a support span of 20 feet.

Materials and Finish:

        - ******************************************************************************

        - Choose the following subparagraphs to match project conditions. If more than one material is needed, the Drawings should clearly indicate material requirements. Aluminum alloy cable tray can be used for most indoor and outdoor applications. Use pre-galvanized steel cable tray for indoor, non-corrosive environments where greater strength or longer spans are required. Use hot-dip galvanized cable tray for non-chemical industrial outdoor and indoor applications. Use stainless steel cable tray for severe chemical environments.

        - ******************************************************************************

Aluminum: Straight section and fitting side rails and rungs extruded from aluminum alloy.

Pre-galvanized Steel: Straight sections, fitting side rails, rungs, and covers made from steel meeting the minimum structural properties and mill galvanized in accordance with coating designation G90.

Hot-dip Galvanized Steel: Straight section and fitting side rails and rungs made from steel meeting the minimum structural properties and hot-dip galvanized after fabrication in accordance with <<ASTM A123/A123M>>. All covers and splice plates must also be hot-dip galvanized after fabrication; mill galvanized covers are not acceptable for hot-dipped galvanized cable tray.  Inspect hot-dip galvanized after fabrication steel cable trays after coating and remove excess zinc.

Stainless Steel: Straight section and fitting side rails and rungs made of Type 304 or Type 316 stainless steel. Transverse members (rungs) or corrugated bottoms welded to the side rails with Type 316 stainless steel welding wire.

Type of tray system:

        - ******************************************************************************

        - The following are designer-choices, based on project conditions. Choose the appropriate subparagraphs for the types of trays present on the project.  Select the appropriate rung spacing. If more than one rung spacing is needed, the Drawings should clearly indicate material requirements. Use 6-inch rung spacing for small telecommunications and control cables. Trays for power cables typically use 12-inch spacing.

        - ******************************************************************************

Ladder type trays shall consist of two longitudinal members (side rails) with transverse members (rungs) welded to the side rails. Rung spacing shall be ​<< 6;  9;  12; or  18>>​ inches on center.

Ventilated trough type trays shall consist of two longitudinal members (side rails) with a corrugated bottom welded to the side rails. To provide ventilation in the tray, the valleys of the corrugated bottom shall have rectangular holes punched along the width of the bottom.

Solid bottom trough type trays shall consist of two longitudinal members (side rails) with a corrugated bottom welded to the side rails.

Tray dimensions:

        - ******************************************************************************

        - Edit the following subparagraphs to match project conditions.  Choose the appropriate sizes for project. If more than one cable size type is needed, the Drawings should clearly indicate requirements.

        - ******************************************************************************

Cable tray usable load depth shall be ​<< 3;  4;  5; or  6>>​ inches minimum, or as noted on the Drawings.

Straight tray sections shall have side rails fabricated as I-beams or C-sections. Supply straight sections in standard << 10;  12;  20; or  24>> feet lengths, except where shorter lengths are needed to facilitate tray assembly lengths shown on Drawings.

Cable tray width shall be << 6;  9;  12;  18;  24;  30; or  36>> inches or as shown on Drawings.

Fittings shall have a minimum inside radius of << 12;  24; or  36>> inches.

Use bolted type splice plates, as indicated below for each tray type.

        - ******************************************************************************

        - Retain the following subparagraphs to match project conditions.

        - ******************************************************************************

Aluminum Tray: Splice plates shall be made of aluminum alloy with four square neck carriage bolts and serrated flange locknuts. Hardware shall be zinc plated in accordance with <<ASTM B633>>, SC1. If aluminum cable tray is to be used outdoors then hardware shall be Type 316 stainless steel.

Steel (including Pre-galvanized and Hot-dip galvanized):  Splice plates shall be manufactured of high strength steel, meeting the minimum mechanical properties of <<ASTM A1011/A1011M>>, Grade 50, Class 1.  Attach each splice plate with four ribbed neck carriage bolts with serrated flange locknuts.  Hardware shall be zinc plated in accordance with <<ASTM B633>> SC1 for pre-galvanized cable trays, or Chromium Zinc in accordance with <<ASTM F1136/F1136M>> for hot-dip galvanized cable trays.

Place cable tray supports so that the support spans do not exceed span ratings of cable tray sections.

Construct trapeze supports from 12 gauge steel formed shape channel members,  1-5/8 inches by 1-5/8 inches with necessary hardware.

Support cable trays installed adjacent to walls on wall mounted brackets.

Use 1/2 inch (minimum) diameter threaded rods to support trapeze hangers and center-hung supports.

Provide barrier strips as indicated on the Drawings. Fasten barrier strips into the tray according to manufacturer's instructions.

Furnish accessories as shown on the Drawings and as required to protect, support, and install a cable tray system and associated cables. Accessories include section splice plates, expansion plates, blind-end plates, ladder dropouts, fittings, bends, and barriers.

Manufacturers: Chalfant, Cooper B-Line, Cope, MP Husky.

      - ***************************************************************************************

      - The following article is automatically activated by the associated paragraph in PART 1.

      - ***************************************************************************************

CABLE TRAY GROUND CLAMPS

Use NRTL listed cable tray ground clamps suitable for use with aluminum cable tray and copper equipment grounding conductor

Manufacturer: O-Z/Gedney “Type CTGC”, Crouse-Hinds “TGC40”

      - ***************************************************************************************

      - The following article is automatically activated by the associated paragraph in PART 1.

      - ***************************************************************************************

CABLE TRAY/CONDUIT BONDING CLAMPS

Use NRTL listed clamps suitable for mechanically connecting and electrically bonding conduit to steel or aluminum cable tray.

Manufacturer: Thomas & Betts “6200 Series”, Crouse-Hinds “LCC Series”

PART 3 - EXECUTION

    - **********************************************************************************************

      - Retain this article when existing construction is affected.

    - **********************************************************************************************

EXISTING WORK

Maintain access to existing cable trays and other installations remaining active and requiring access. Modify installation or provide access panels.

Clean and repair existing cable trays and accessories to remain or to be reinstalled, if needed to facilitate connection to new systems.

EXAMINATION

Examine spaces to receive cable tray for compliance with installation tolerances and other conditions affecting performance of the raceway system.  Do not proceed with installation until unsatisfactory conditions have been corrected.

Cable Tray INSTALLATION

Install cable tray where indicated on the Drawings and according to manufacturer's instructions, <<NECA/NEMA 105>>, and <<NFPA 70>>. Have the manufacturer’s instructions available at the construction site.

Provide not less than 12 inches of clear space above and to one side of cable trays to permit access for installing and maintaining cables.

Install supports for cable tray as shown on drawings.

Support cable tray independent of supports for other elements such as pipes, conduits, ceilings, ducts, and equipment enclosures, unless indicated on drawings.

Use minimum 1/2-inch threaded rods to support cable tray, unless otherwise shown on drawings.

Locate cable tray fitting supports so they meet the strength requirements of straight sections. Install fitting supports per <<NECA/NEMA 105>> and in accordance with manufacturer's instructions.

Splice plates and expansion plates, where used, shall be placed within 5 inches from quarter span between supports.

Install expansion splice plates and flexible bonding jumpers for thermal expansion, as well as at locations where cable trays cross building expansion joints.  Calculate distance between expansion joints based on a temperature difference of 100 degrees F and the allowable expansion of the plate.  The gap must be set on the day of installation, based on the temperature at the time of installation.  Use 0 degrees F as the coldest day and use 100 degrees F as the hottest day.

Install a waterproof concrete curb at least 4 inches high around floor penetrations.

Fasten cable tray supports to building structure.

      - ***************************************************************************************

      - Seismic:  Cable trays are rarely connected to other equipment.  The gap between the tray and the associated equipment satisfies the concern for cascade failure, which this paragraph is meant to address.  Retain the following if either of the two conditions below exist on the project.

      - Where cable tray is connected to associated equipment, the possibility of cascade failure will have to be taken into account. Ensure flexible connections are indicated on the drawings in the applicable locations.

      - Regardless of whether the cable tray is subject to seismic design or not, flexible connections shall be used at seismic-control joints.

      - ***************************************************************************************

Install flexible connections for cable tray where shown on drawings.

Grounding and Bonding

Ground and bond cable tray as shown on drawings.

Provide electrical continuity between conductive tray components.

Use anti-oxidant compound, if required by the manufacturer, to prepare aluminum contact surfaces before assembly.

        - ******************************************************************************

        - The following subparagraph is automatically activated when the associated paragraph is activated in PART 1.

        - ******************************************************************************

Make mechanical and electrical bond connection between conduits and cable tray using NRTL-listed cable tray/conduit bonding clamps.

LABELING

      - ***************************************************************************************

      - Retain the following paragraph if the cable tray is installed in a plenum or in an environmental air space.  If this is a NFPA 75 room and under the floor has fire suppression, this may not be required.

      - ***************************************************************************************

Install red warning labels with 1/2-inch white letters and the following message at visible locations 50 foot on centers on all cable trays in environmental air spaces or return air plenums:

        - USE ONLY PLENUM RATED CABLES IN THIS CABLE TRAY

Install white labels with 1/2-inch black letters and the following information at visible locations 50 foot on centers on all cable trays:

Maximum cable tray loading depth.

Allowable cable load in pounds per foot based on the as-installed support span spacing and structural support capability.

FIELD QUALITY CONTROL

Inspect accessible components for cleanliness, mechanical, and electrical integrity, and for presence of damage or deterioration before energizing.

After completing installation, cleaning, and testing: touch up scratches and mars on finish to match original finish.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 26 0536, REV. 6, DATED APRIL 15, 2026.