Section 26 0700 
Induction Motors - 500HP and Smaller

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 5 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Electrical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable Sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality Requirements.

      - Seismic: If the motor isn’t exempt from seismic design per ASCE 7 paragraph 13.1.4 then, prior to attempting to edit this Section to be Project-specific, refer to Sections << 26 0548.16 - Seismic Controls for Electrical Systems>>, and << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>, as applicable.

  - *************************************************************************************************************

PART 1 - GENERAL

Section Includes

Section includes single- and three-phase induction motors rated 500 horsepower and smaller and 600 volts and less, for application on equipment provided under other sections, and motors furnished loose to Project.

Section does not address motors intended for use in hazardous locations as defined in <<NFPA 70>>, or as required by <<DOE-STD-1212>>.

Section does not address sealed (hermetic-type) motor-compressor parts.

Section does not address special-purpose motors such as for submersible pumps.

RELATED Requirements

Section << 01 2500 - Substitution Procedures>>

Section << 01 3300 - Submittal Procedures>>

Section ​<< 01 7839 - Project Record Documents>>​

Section ​<< 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>​

Section ​<< 26 0519 - Low Voltage Electrical Power Conductors and Cables>>​

Section << 26 0533 - Raceways and Boxes for Electrical Systems>>

Section << 26 0548.16 - Seismic Controls for Electrical Systems>>​​

Section << 26 0813 - Electrical Acceptance Testing>>

REFERENCE STANDARDS

ABMA STD 9 - Load Ratings and Fatigue Life for Ball Bearings.

DOE-STD-1212 - Explosives Safety.

IEEE 112 - IEEE Standard Test Procedure for Polyphase Induction Motors and Generators.

IEEE 841 - IEEE Standard for Petroleum and Chemical Industry--Premium-Efficiency, Severe-Duty, Totally Enclosed Squirrel Cage Induction Motors from 0.75 kW to 370 kW (1 hp to 500 hp).

NECA 1 - Standard for Good Workmanship in Electrical Construction.

NECA 230 - Standard For Selecting, Installing, And Maintaining Electric Motors And Motor Controllers (ANSI).

NEMA MG 00001 - Motors and Generators.

NFPA 70 - National Electrical Code.

UL 1004 - Standard for Electric Motors.

SUBMITTALS

Submit the following in accordance with Section ​<< 01 3300 - Submittal Procedures>>​.

Action Submittals

Catalog Data: Submit catalog data for each motor furnished loose. Indicate nameplate data, standard compliance, electrical ratings and characteristics, and physical dimensions, weights, mechanical performance data, and support points.

Installation instructions including handling, storage, setting, mechanical connections, lubrication, wiring, and testing.

Informational Submittals at Closeout:

Operation and maintenance data:

Operation data including instructions for safe operating procedures.

Maintenance data including assembly drawings, bearing data with replacement sizes, and lubrication instructions.

Test reports from PART 3.

QUALITY ASSURANCE

Comply with <<NFPA 70>> for installation requirements

Motors Shall be listed and labeled by a Nationally Recognized Testing Laboratory (NRTL)

<<UL 1004>>​-1, Standard for Rotating Electrical Machine - General Requirements

<<UL 1004>>-2, Standard for Impedance Protected Motors

<<UL 1004>>-3, Standard for Thermally Protected Motors

<<UL 1004>>-5, Standard for Fire Pump Motors

<<UL 1004>>-8, Standard for Inverter Duty Motors

DELIVERY, STORAGE, AND HANDLING

Receive, store, and protect, and handle products according to <<NECA 1>>, and <<NECA 230>>.

Upon delivery of motors to site, inspect thoroughly for damage.

Store, protect and handle motors following manufacturer’s instructions.  Provide slings and spreader bars as required.  Lift only with lugs provided. Do not lift motors using shaft as an attachment point.

Protect products from weather and moisture by covering with plastic or canvas and by maintaining temperature within enclosure.

PART 2 - PRODUCTS

MANUFACTURERS

Baldor.

Marathon.

Emerson Motors.

GE Motors.

Siemens.

TECO-Westinghouse.

      - ***************************************************************************************

      - The following is a designer-choice, depending on if substitutions are allowed on the project.

      - ***************************************************************************************

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted, follow Section << 01 2500 - Substitution Procedures>>.

PERFORMANCE REQUIREMENTS

Motors shall perform satisfactorily in the following service conditions:

Elevation: 7,500 feet above sea level.

Maximum ambient temperature: 104 degrees F.

Minimum ambient temperature: -20 degrees F.

        - ******************************************************************************

        - The following is a designer-choice, based on outdoor equipment.

        - ******************************************************************************

Maximum solar heat gain: 110 W/sq. ft.

      - ***************************************************************************************

      - Seismic: Retain the following paragraphs in the following Article as applicable to project. If motors are not subject to seismic design, omit article below.

      - - 1st paragraph is for motors that do not have to operate/ function post-seismic-event.

      - - 2nd paragraph is for motors that must operate/ function after a seismic event (i.e., a Designated Seismic System, or DSS).

      - If paragraph applies, the “E” drawings for the motors shall also state that the motors are Designated Seismic Systems

      - If paragraph applies, edit it in accordance with content of Section ​<< 26 0548.16 - Seismic Controls for Electrical Systems>>​ and/or ​<< 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>​.

      - ***************************************************************************************

SEismic Performance requirements

The motors shall remain in place without separation of any parts when subjected to the design basis earthquake

Per Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>

        - *** OR ***

As represented by the seismic forces derived from the criteria indicated ​<< on the drawings; or  in Section 26 0548.16 - Seismic Controls for Electrical Systems>>​

The motors are Designated Seismic Systems and, as such, shall remain in place and be fully operational following the design basis earthquake

Per Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>

        - *** OR ***

As represented by the seismic forces derived from the criteria indicated ​<< on the drawings; or  in Section 26 0548.16 - Seismic Controls for Electrical Systems>>​

GENERAL CONSTRUCTION AND REQUIREMENTS

Motors less than 1/4 HP, for general applications, may be equipment manufacturer's standard product and need not conform to these specifications, unless otherwise required.

Provide motors with electrical and mechanical performance in accordance with <<NEMA MG 00001>>, unless specified otherwise in this Section.

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements.

      - ***************************************************************************************

Enclosure

For NEMA frame motors, provide motors that conform to <<IEEE 841>>.  In the event that any part of this Section is in conflict with <<IEEE 841>>, <<IEEE 841>> shall prevail.

For non-NEMA frame motors, provide type as shown on drawings.

Provide 240 volt space heaters in motors, if indicated on the Drawings.

Rating

Motors shall be rated for continuous-duty, unless otherwise specified.

De-rate motors for operation at 7500 feet altitude in accordance with <<NEMA MG 00001>>. Do not use motor service factor to compensate for altitude. Refer to motor selection table in “Three Phase Power – Squirrel Cage Motor” in this Section.

Nameplates:

Each motor shall have a stainless steel nameplate indicating information required by <<NFPA 70>> and <<NEMA MG 00001>>.

Additional nameplate information may be required by other sections in this Specification.

Attach nameplates to motor frame with stainless steel fasteners.

Wiring Terminations:

Terminal lugs shall match branch circuit conductor quantities, sizes, and materials indicated.

For fractional horsepower motors where connection is made directly, provide conduit connection in end frame.

Provide a screw or lug inside terminal cover or terminal box for connection to an Equipment Grounding Conductor.

Motors shall meet <<NEMA MG 00001>> noise level standards.

      - ***************************************************************************************

      - The following is a designer-choice, based on if single-phase split phase motors are on the project.

      - ***************************************************************************************

SINGLE PHASE POWER – SPLIT PHASE MOTORS

Use single-phase power, split-phase motors where shown on approved construction documents.

Split-phase motors shall have the following characteristics:

Starting Torque: Less than 150 percent of full load torque.

Breakdown Torque: Approximately 200 percent of full load torque.

Insulation: Class A (60 degrees C temperature rise) or better.

Service Factor: Minimum of 1.35 for drip-proof motors and 1.0 for enclosed motors.

Bearings: Pre-lubricated ball bearings.

      - ***************************************************************************************

      - The following is a designer-choice, based on if single-phase permanent split capacitor motors are on the project.

      - ***************************************************************************************

SINGLE PHASE POWER – PERMANENT-SPLIT CAPACITOR MOTORS

Use single-phase power, permanent split capacitor motors where shown on approved construction documents.

Permanent split capacitor motors shall have the following characteristics:

Starting Torque: Exceeding 1/4 of full load torque.

Multiple Speed: Through tapped windings.

Insulation: Class A (60 deg C temperature rise) or better.

Service Factor: 1.0

Bearings: Pre-lubricated ball or sleeve bearings.

Integral Protection: Automatic reset overload protector.

      - ***************************************************************************************

      - The following is a designer-choice, based on if capacitor start motors are on the project.

      - ***************************************************************************************

SINGLE PHASE POWER – CAPACITOR-START MOTORS

Use single-phase power, capacitor-start motors where shown on approved construction documents.

Capacitor-start motors shall have the following characteristics:

Starting Torque: 3 times full load torque.

Pull-up Torque: Up to 350 percent of full load torque.

Breakdown Torque: Approximately 250 percent of full load torque.

Motors: Capacitor in series with starting winding. Provide capacitor-start/ capacitor-run motors with 2 capacitors in parallel with run capacitor remaining in circuit at operating speeds.

Insulation: Class A (60 deg C temperature rise) or better.

Service Factor: Minimum of 1.25 for drip-proof motors and 1.0 for enclosed motors.

Bearings: Pre-lubricated ball bearings.

      - ***************************************************************************************

      - The following is a designer-choice, based on if three-phase squirrel cage motors are on the project.

      - ***************************************************************************************

THREE PHASE POWER – SQUIRREL CAGE MOTORS

Use 3-phase power, squirrel-cage, induction motors for applications where shown on approved construction documents.

3-phase power, squirrel-cage motors shall have the following characteristics:

Starting Torque:  NEMA Design B characteristics.

Locked Rotor Current: NEMA Design B characteristics.

Power Output, Locked Rotor Torque, Breakdown or Pull-Out Torque: NEMA Design B characteristics.

Design, Construction, Testing, and Performance: Conform to <<NEMA MG 00001>> for Design B motors.

Insulation System: NEMA Class F or better.

Service Factor: 1.15 minimum.

Motors shall be NEMA Standard T-Frames of steel, aluminum, or cast iron with end brackets of cast iron or aluminum with steel inserts.

Motors shall have grease lubricated anti-friction ball bearings, with housings equipped with provision for re-lubrication.

The bearings shall have a rated L-10 fatigue life per ANSI/<<ABMA STD 9>> of 150,000 hours for direct-coupled applications and 50,000 hours for belted applications minimum. Belted rating shall be based on radial loads and pulley sizes called out in <<NEMA MG 00001>>. The calculation will be determined from the pulley centerline being at the end of the motor shaft.

Bearing cavities and greasing passages shall be thoroughly cleaned of all debris before lubricating. Motors shall be lubricated at the factory with Exxon Mobil Polyrex™ EM grease, or equal.

Stamp ANSI/ABMA bearing identification number on motor nameplate.

For belted applications, provide an adjustable sliding base; for applications above 10 horsepower, sliding base shall have 2 adjusting bolts.

General purpose, single-speed motors shall be NEMA PremiumTM labeled motors or motors with full-load nominal efficiency not less than that tabulated below when tested in accordance with <<IEEE 112>>, subclause 6.4, Method B.

| NOMINAL FULL-LOAD EFFICIENCY |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | NUMBER OF POLES/ SYNCHRONOUS SPEED, RPM |  |  |  |  |  |
| MOTOR HP | ODP MOTORS |  |  | TEFC MOTORS |  |  |
|  | 2 3600 | 4 1800 | 6 1200 | 2 3600 | 4 1800 | 6 1200 |
| 1 | 77.0 | 85.5 | 82.5 | 77.0 | 85.5 | 82.5 |
| 1.5 | 84.0 | 86.5 | 86.5 | 84.0 | 86.5 | 87.5 |
| 2 | 85.5 | 86.5 | 87.5 | 85.5 | 86.5 | 88.5 |
| 3 | 85.5 | 89.5 | 88.5 | 86.5 | 89.5 | 89.5 |
| 5 | 86.5 | 89.5 | 89.5 | 88.5 | 89.5 | 89.5 |
| 7.5 | 88.5 | 91.0 | 90.2 | 89.5 | 91.7 | 91.0 |
| 10 | 89.5 | 91.7 | 91.7 | 90.2 | 91.7 | 91.0 |
| 15 | 90.2 | 93.0 | 91.7 | 91.0 | 92.4 | 91.7 |
| 20 | 91.0 | 93.0 | 92.4 | 91.0 | 93.0 | 91.7 |
| 25 | 91.7 | 93.6 | 93.0 | 91.7 | 93.6 | 93.0 |
| 30 | 91.7 | 94.1 | 93.6 | 91.7 | 93.6 | 93.0 |
| 40 | 92.4 | 94.1 | 94.1 | 92.4 | 94.1 | 94.1 |
| 50 | 93.0 | 94.5 | 94.1 | 93.0 | 94.5 | 94.1 |
| 60 | 93.6 | 95.0 | 94.5 | 93.6 | 95.0 | 94.5 |
| 75 | 93.6 | 95.0 | 94.5 | 93.6 | 95.4 | 94.5 |
| 100 | 93.6 | 95.4 | 95.0 | 94.1 | 95.4 | 95.0 |
| 125 | 94.1 | 95.4 | 95.0 | 95.0 | 95.4 | 95.0 |
| 150 | 94.1 | 95.8 | 95.4 | 95.0 | 95.8 | 95.8 |
| 200 | 95.0 | 95.8 | 95.4 | 95.4 | 96.2 | 95.8 |
| 250 | 95.0 | 95.8 | 95.4 | 95.8 | 96.2 | 95.8 |
| 300 | 95.4 | 95.8 | 95.4 | 95.8 | 96.2 | 95.8 |
| 350 | 95.4 | 95.8 | 95.4 | 95.8 | 96.2 | 95.8 |
| 400 | 95.8 | 95.8 | 95.8 | 95.8 | 96.2 | 95.8 |
| 450 | 95.8 | 96.2 | 96.2 | 95.8 | 96.2 | 95.8 |
| 500 | 95.8 | 96.2 | 96.2 | 95.8 | 96.2 | 95.8 |

Do not select motors to operate continuously above rated load in the service factor area.

De-rate motors for operation at 7500 ft. altitude in accordance with the following table, taking into consideration the ambient temperature of the motor environment. Select motor based on 104 degrees F ambient temperature, unless motor is in a moving air stream when operating.

| MAXIMUM MOTOR SHAFT LOAD e (bhp) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Motor Nameplate (hp) |  | Ambient Temperature a, b, c (degrees F) |  |  |  |  |  |
|  |  | 81.1 | 85 | 90 | 95 | 100 | 104d |
| 1 |  | 1.00 | 0.98 | 0.95 | 0.92 | 0.89 | 0.87 |
| 1.5 |  | 1.50 | 1.47 | 1.43 | 1.38 | 1.34 | 1.31 |
| 2 |  | 2.00 | 1.96 | 1.90 | 1.85 | 1.79 | 1.75 |
| 3 |  | 3.00 | 2.93 | 2.85 | 2.77 | 2.68 | 2.62 |
| 5 |  | 5.00 | 4.89 | 4.75 | 4.61 | 4.47 | 4.36 |
| 7.5 |  | 7.50 | 7.34 | 7.13 | 6.92 | 6.71 | 6.55 |
| 10 |  | 10.0 | 9.78 | 9.51 | 9.23 | 8.95 | 8.73 |
| 15 |  | 15.0 | 14.7 | 14.3 | 13.8 | 13.4 | 13.1 |
| 20 |  | 20.0 | 19.6 | 19.0 | 18.5 | 17.9 | 17.5 |
| 25 |  | 25.0 | 24.5 | 23.8 | 23.1 | 22.4 | 21.8 |
| 30 |  | 30.0 | 29.3 | 28.5 | 27.7 | 26.8 | 26.2 |
| 40 |  | 40.0 | 39.1 | 38.0 | 36.9 | 35.8 | 34.9 |
| 50 |  | 50.0 | 48.9 | 47.5 | 46.1 | 44.7 | 43.6 |
| 60 |  | 60.0 | 58.7 | 57.0 | 55.4 | 53.7 | 52.4 |
| 75 |  | 75.0 | 73.4 | 71.3 | 69.2 | 67.1 | 65.5 |
| 100 |  | 100 | 97.8 | 95.1 | 92.3 | 89.5 | 87.3 |
| 125 |  | 125 | 122 | 119 | 115 | 112 | 109 |
| 150 |  | 150 | 147 | 143 | 138 | 134 | 131 |
| 200 |  | 200 | 196 | 190 | 185 | 179 | 175 |
| 250 |  | 250 | 245 | 238 | 231 | 224 | 218 |
| 300 |  | 300 | 293 | 285 | 277 | 268 | 262 |
| 350 |  | 350 | 342 | 333 | 323 | 313 | 305 |
| 400 |  | 400 | 391 | 380 | 369 | 358 | 349 |
| 450 |  | 450 | 440 | 428 | 415 | 403 | 393 |
| 500 |  | 500 | 489 | 475 | 461 | 447 | 436 |
| Notes: |  |  |  |  |  |  |  |
| a. | Select motor based on 104 degrees F ambient temperature unless motor is in a moving air stream when operating. |  |  |  |  |  |  |
| b. | Document selection of an ambient temperature lower than 90 degrees F. |  |  |  |  |  |  |
| c. | Do not extrapolate to ambient temperatures below 81.1 or above 104 degrees F. If the ambient temperature is outside the 81.1 degrees F to 104 degrees F range, refer to <<NEMA MG 00001>> and/or the motor manufacturer for guidance. |  |  |  |  |  |  |
| d. | If ambient temperature exceeds 104 degrees F, select motor with greater nameplate hp rating in accordance with <<NEMA MG 00001>>. |  |  |  |  |  |  |
| e. | Motor selection criteria developed from temperature rise considerations in <<NEMA MG 00001>>, clauses 12.43, 12.51, and 14.4. |  |  |  |  |  |  |

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements. Coordinate with equipment schedules on the Drawings. Retain if motors are controlled by part-winding starters.

      - ***************************************************************************************

Where indicated on Drawings, provide motors suitable for use with part winding starting systems to reduce locked rotor current to approximately 60 percent of full winding locked rotor current while providing approximately 50 percent of full winding locked rotor torque.

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements. Coordinate with equipment schedules on the Drawings. Retain if there are 2-speed motors included in the project.

      - ***************************************************************************************

Where indicated on Drawings, provide motors suitable for use in a single winding, variable torque connection for 2 speed fan and centrifugal pump applications.

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements. Coordinate with equipment schedules on the Drawings. Retain if motors are on adjustable frequency controllers.

      - ***************************************************************************************

Where indicated on Drawings, provide motors suitable for use with adjustable frequency controllers as follows:

Provide motors that comply with Part 31 of <<NEMA MG 00001>> for use with pulse width modulation (PWM) adjustable frequency AC controllers.

Provide motors that comply with Part 30 or 31 of <<NEMA MG 00001>> for use with six step adjustable frequency controllers.

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements. Coordinate with equipment schedules on the Drawings. Retain if required. Only critical motors warrant winding thermistors.

      - ***************************************************************************************

Where indicated on approved construction documents, provide three positive thermal coefficient (PTC) thermistors imbedded in motor windings (one per phase) and solid state control relay for wiring into motor starter.

PART 3 - EXECUTION

    - **********************************************************************************************

      - Retain the following if existing work will be affected.

    - **********************************************************************************************

EXISTING WORK

Maintain access to existing motors and other installations remaining active and requiring access. Modify installation or provide access panel.

If part of the project scope, clean and repair existing motors that are to remain or are to be reinstalled.

EXAMINATION

Examine surfaces to receive motors for compliance with installation tolerances and other conditions affecting performance of the control system.  Do not proceed with installation until unsatisfactory conditions have been corrected.

INSTALLATION

Install motors and accessories in accordance with manufacturer's instructions, <<NFPA 70>> , and <<NECA 230>>; have manufacturer’s installation instructions available at the construction site.

Remove any slushing compound on shaft or other parts using a petroleum-type solvent.

Remove shaft shipping braces after motor is placed in its final location.

Connections to motor: Use motor lead splicing kits to insulate and seal connections to leads. Make electrical connections to motors using materials and methods specified in Sections ​<< 26 0519 - Low Voltage Electrical Power Conductors and Cables>>​ and Section ​<< 26 0533 - Raceways and Boxes for Electrical Systems>>​. Use flexible conduits for connection.

      - ***************************************************************************************

      - Retain the following three paragraphs only for when the electrical subcontractor is responsible for the finished installation. In most cases, it is the responsibility of the mechanical discipline to install the coupling.

      - ***************************************************************************************

Install shaft coupling or sheave in accordance with manufacturer’s instructions.  Do not modify motor shaft to accommodate coupling or sheave.

Align the motor shaft with the load shaft. Meet the most stringent of the motor manufacturer’s requirements for shaft alignment, the driven equipment manufacturer’s requirements for shaft alignment, or the following requirements for shaft alignment. The minimum acceptable criteria for motor installation and shaft alignment for motors 10 hp and larger are as follows:

Load and motor casing distortion (soft foot): Not more than 0.002 inch (0.0508 mm) at each foot. Use stainless steel pre-stamped shims as required in bringing soft foot within acceptable limits.

Load and motor shaft runout: Not more than 0.001 inch.  If load shaft exceeds criteria contact the LANL Subcontract Technical Representative (STR). If motor shaft runout exceeds criteria, replace the motor.

Alignment tolerances for coupled shafts with short couplings:

| Speed, rpm | SHAFT OFFSET At center, inch (mm) | ANGULARITY/GAP Inch/10 inches (mm/254 mm) |
| --- | --- | --- |
| 600 | 0.005 (0.1270) | 0.010 (0.2540) |
| 900 | 0.003 (0.0762) | 0.007 (0.1778) |
| 1200 | 0.0025 (0.0635) | 0.005 (0.1270) |
| 1800 | 0.002 (0.0508) | 0.003 (0.0762) |
| 3600 | 0.001 (0.0254) | 0.002 (0.0508) |
| 7200 | 0.0005 (0.0127) | 0.001 (0.0254) |

Alignment tolerances for coupled shafts having couplings with spacers:

| Speed, rpm | SHAFT OFFSET Per inch (25.4 mm) of spacer length |
| --- | --- |
| 600 | 0.0018 (0.0457) |
| 900 | 0.0012 (0.0305) |
| 1200 | 0.0009 (0.0229) |
| 1800 | 0.0006 (0.0152) |
| 3600 | 0.0003 (0.0076) |
| 7200 | 0.00015 (0.0038) |

For belt-driven loads, use string or straight edge alignment of pulley grooves to minimize offset, angle, and twist so belts are not distorted. Verify roundness of pulleys; replace pulleys with total indicator runout exceeding 0.005 inch. Set belt tension as low as possible.

FIELD Quality Control

Perform the following inspections for all field installed motors:

Verify that motor nameplate data agrees with Drawings and Specifications.

Inspect physical and mechanical condition of motor.

Verify that motor is properly anchored.

Verify that motor is lubricated in accordance with manufacturer’s instructions.

Perform and document the following inspections and tests for all field installed motors that are indicated on the approved construction documents to be driving critical loads:

Witness the torquing of accessible bolted electrical connections.

Before energizing motor with driven equipment, verify proper alignment of motor shaft with load shaft.

Verify proper rotation direction as required by the load.

Maintain and submit records of inspections and tests for each motor.

      - ***************************************************************************************

      - Retain the following if formal electrical acceptance testing is required; refer to Section << 26 0813 - Electrical Acceptance Testing>>.  For squirral cage motors, testing is only required for motors greater than 100 hp.

      - ***************************************************************************************

Coordinate inspections and tests with those required by Section << 26 0813 - Electrical Acceptance Testing>>.

      - ***************************************************************************************

      - The following is a designer-choice, based on if manufacturer's start up services are required for the project. Balance the benefits of start-up services against the cost of the motor and the importance of the load it drives. Omit the following Article if the cost of the manufacturer’s start-up service is not warranted. Generally, only motors that drive critical loads will require start-up services.

      - ***************************************************************************************

manufacturer’s Start-up Services

For motors driving critical loads, provide services of a factory-trained manufacturer’s service representative to verify proper installation and start-up of equipment.

Submit certification that motors have been installed, adjusted, and tested in accordance with manufacturer’s recommendations.

project Record Documents

Submit the following in accordance with Section << 01 7839 - Project Record Documents>>​:

Report of field tests showing compliance with and field quality control specified in PART 3 of this Section.

        - ******************************************************************************

        - The following subparagraph will be automatically selected if manufacturer's start-up services is activated above.

        - ******************************************************************************

Start-up report from motor manufacturer’s start-up service to certify that motors have been installed, adjusted, and tested in accordance with manufacturer’s recommendations.

  - END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 26 0700, REV. 5, DATED APRIL 15, 2026.