Section 26 2213 
Low Voltage Distribution Transformers

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 5 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Electrical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality Sections.

      - ==========================================================

      - Seismic Design: This template can’t be properly edited for job-specific seismic requirements without the following three (3) decisions having been made first:

      - - Whether the transformer(s) is exempt from ASCE 7 Ch. 13.

      - - How ASCE 7 paragraph 13.2.1 is going to be complied with.

      - - Whether the transformer is a Designated Seismic System (DSS).

      - I) If the transformer(s) is exempt per ASCE 7 paragraph 13.1.4 then the seismic-related requirements herein are not applicable, and the same goes for the remaining two decisions (i.e., II and III).

      - II) There are two (2) options for complying w/ ASCE 7 paragraph 13.2.1:

      - -Project-specific design and documentation, prepared by the Engineer of Record (EOR) or the construction subcontractor (i.e., Delegated Design); or

      - - Manufacturer certification.

      - If the latter option applies then this Section shall reference Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>, and a project-specific version of Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>shall be created and included in the Project Spec.

      - III) DSS: If a transformer must function after the design-basis earthquake, it is assigned an Importance Factor (Ip) of 1.5 and, as a result of this, and the fact that transformers are “active,” it is a DSS that requires Special Certification. If this applies then, regardless of the previous decision (i.e., II), this Section shall reference Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>, and a project-specific version of Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>> shall be created and included in the Project Spec.

      - If II.A applies, and will be accomplished via Delegated Design, then this Section shall reference Section << 26 0548.16 - Seismic Controls for Electrical Systems>>, and a project-specific version of Section << 26 0548.16 - Seismic Controls for Electrical Systems>>​ 2shall be created and included in the Project Spec. The seismic design criteria will be included therein.

      - Finally, another reason to include Sect. << 26 0548.16 - Seismic Controls for Electrical Systems>> in a Project Spec is to specify seismic control/ restraint. Such use of Section << 26 0548.16 - Seismic Controls for Electrical Systems>> is not applicable only for projects in which transformers are exempt and those in which compliance w/ ASCE 7 paragraph 13.2.1 is achieved via II.B. Seismic control/ restraint is achieved by devices (e.g., supports and attachments) that provide restraint against excessive movement during an earthquake without compromising the effectiveness of vibration isolators. Since these devices are included in Sect. << 26 0548.16 - Seismic Controls for Electrical Systems>>, if a Project Spec includes it then only devices that differ from those therein (that are required for use) need be included herein.

  - *************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

General-purpose dry-type low-voltage transformers.

      - ***************************************************************************************

      - The following is a designer-choice.  Use low temperature rise dry-type transformers where the average daily load will be 90% or more of the transformer nameplate rating. On the Drawings clearly indicate which transformers shall be low temperature rise; this will typically be for continuous loads (e.g., 24-hour-per-day loads in laboratory buildings and computer centers). Omit this paragraph if low temperature rise transformers are not required.

      - ***************************************************************************************

Low-temperature rise dry-type low-voltage transformers.

      - ***************************************************************************************

      - The following is a designer-choice, based on the need to use K-factor transformers.  Use K-factor rated dry-type transformers for separately derived systems that only supply computer or other high harmonic loads. On the Drawings clearly indicate which transformers shall be K-Factor rated.

      - ***************************************************************************************

K-Factor rated dry type transformers

Related Requirements

Section ​<< 01 2500 - Substitution Procedures>>​

Section << 01 3300 - Submittal Procedures>>

Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>

Section << 26 0526 - Grounding and Bonding for Electrical Systems>>

Section << 26 0553 - Identification for Electrical Systems>>

Section << 26 0548.16 - Seismic Controls for Electrical Systems>>

REFERENCE STANDARDS

10 CFR 431 - Energy Efficiency Program for Certain Commercial and Industrial Equipment - Distribution Transformers.

IEEE C57.12.91 - IEEE Standard Test Code for Dry-Type Distribution and Power Transformers.

NECA 1 - Standard for Good Workmanship in Electrical Construction.

NECA 409 - Standard for Installing and Maintaining Dry-Type Transformers.

NFPA 70 - National Electrical Code.

UL 486A-486B - Wire Connectors.

UL 1561 - Standard for Dry-Type General Purpose and Power Transformers.

      - ***************************************************************************************

      - Edit the following article to match project conditions.

      - ***************************************************************************************

ACTION SUBMITTALS

Submit the following in accordance with Section << 01 3300 - Submittal Procedures>>, for transformers greater than 10 kVA:

Catalog Data. Include outline and support point dimensions of transformer enclosures and accessories, unit weight, voltages, kVA, percent impedance, sound level, tap configurations, insulation system type, rated temperature rise, shipping bolt instructions.

Operation and maintenance instructions.

QUALITY ASSURANCE

Provide products that are listed and labeled by a Nationally Recognized Testing Laboratory (NRTL), where such products are required by <<NFPA 70>> to be listed, or such products contain an electrical hazard as follows:

For AC circuits – Greater than 50 volts.

For DC circuits including batteries – Greater than 100 volts.

Provide products that comply with the following industry standards:

<<10 CFR 431>>​​, Subpart K

<<UL 1561>>

DELIVERY, STORAGE, AND HANDLING

Receive, store, and protect, and handle products according to Chapter 2 of <<NECA 1>>​ and Chapter 4 of <<NECA 409>>.

PART 2 - PRODUCTS

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section << 01 2500 - Substitution Procedures>>.

PERFORMANCE REQUIREMENTS

Provide transformers and accessories that will perform satisfactorily in the following service conditions:

Elevation of 7,500 feet above sea level.

Maximum ambient temperature of 104 degrees F.

Load current harmonic factor not exceeding 5 percent THD.

        - ******************************************************************************

        - The following is a designer-choice, depending on if the equipment will be outdoors in the sun.

        - ******************************************************************************

Maximum solar heat gain: 110 W/sq ft.

      - ***************************************************************************************

      - Seismic: Retain the paragraphs in the following Article based on project requirements and guidance in the first author note. Omit the following Article if transformer(s) is exempt from seismic design.

      - For transformer(s) that aren’t exempt from seismic, if Project Spec includes Section << 26 0548.16 - Seismic Controls for Electrical Systems>>, and if mounting and/or anchorage devices are to be used that differ from those specified in Section << 26 0548.16 - Seismic Controls for Electrical Systems>>, they must be described herein (in PART 2).

      - If transformer is a Designated Seismic System, this shall (also) be indicated on the drawings (i.e., as a minimum, on the sheet where the component is first shown/indicated.).

      - ***************************************************************************************

SEISMIC PERFORMANCE REQUIREMENTS

The transformer(s) shall remain in place without separation of any parts when subjected to the design basis earthquake

Per Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>

        - *** OR ***

As represented by the seismic forces derived from the criteria indicated << on the drawings; or  in Section 26 0548.16 - Seismic Controls for Electrical Systems>>

The transformer is a Designated Seismic System and, as such, it shall remain in place and be fully operational following the design basis earthquake

Per Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>

        - *** OR ***

As represented by the seismic forces derived from the criteria indicated << on the drawings; or  in Section 26 0548.16 - Seismic Controls for Electrical Systems>>

GENERAL

Transformers shall be NRTL listed to <<UL 1561>>.

Transformers rated 10 kVA and larger.

Comply with <<10 CFR 431>>, Subpart K  (DOE 2016 Efficiency Standards)

Marked as compliant with DOE 2016 Efficiency Standards, by manufacturer.

Transformer coils may be aluminum or copper with continuous wound construction and shall be impregnated with non-hygroscopic, thermosetting varnish.

Insulating materials shall be rated as a 220 degree-C UL-component-recognized insulation system.

Transformers 25 kVA and larger shall have a minimum of two 2.5 percent full capacity above normal and four 2.5 percent full capacity below normal primary taps.

The core and coil shall be bolted to the base of the enclosure, isolated by means of vibration-absorbing mounts. Sound isolation systems requiring the complete removal of all fastening devices will not be acceptable.

The core of the transformer shall be visibly bonded to the enclosure by a flexible conductor or strap.

      - ***************************************************************************************

      - Edit the following paragraph to match Project requirements; some installations may require lower sound levels. Transformers designed to have a 3 dB reduction below the sound levels specified below are available from several manufacturers as a premium special order item; proper design of transformer installations is usually a more cost-effective approach than specifying low-sound transformers.

      - ***************************************************************************************

Maximum sound levels shall not exceed the following when tested, according to <<IEEE C57.12.91>>

10 – 50 kVA: 45 dB

51 – 150 kVA: 50 dB

151 – 300 kVA: 55 dB

301 – 500 kVA: 60 dB.

Transformers 45 kVA and less shall be suitable for wall, floor, or trapeze mounting; transformers larger than 45 kVA shall be suitable for floor or trapeze mounting.  Provide mounting accessories required for installation.

Grounding:  Manufacturer shall provide ground bar kit or a ground bar installed on the inside of the transformer enclosure, per <<NFPA 70>> Section 450.10.

      - ***************************************************************************************

      - The following Article applies if flexible connections will have to be installed for “seismic purposes” per the author note for the Article, “Flexible Connections” in PART 3. Note: Raceways smaller than 3 inch are considered flexible for seismic purposes. If all raceways connecting to the transformer are less than 3 inches, This Article is not needed.

      - ***************************************************************************************

FLEXIBLE CONNECTIONS

Permissible products include those that permit rotational and or translational movement without degradation of performance.  Examples include flexible metallic conduit.

General-Purpose DRY-TYPE TRANSFORMERS

Provide factory assembled and tested, energy-efficient, general-purpose, air cooled, dry-type transformers with voltage and kVA ratings as indicated on the Drawings.

General-purpose transformers 15 kVA and larger shall be 150 degree-C temperature rise above 40 degree-C ambient.  The maximum temperature of the top of the enclosure shall not exceed 50 degrees-C rise above a 40 degree-C ambient.

Manufacturers:

Square D Type “EE”

Eaton/Cutler-Hammer “DS-3”and “DT-3”

Sola/Hevi-Duty “ES” and “ET.”

Low Temperature Rise DRY TYPE TRANSFORMERS

Provide factory assembled and tested energy-efficient, low temperature rise air cooled, dry-type transformers with voltage and kVA ratings as indicated on the Drawings.

Low temperature rise transformers 15 kVA and larger shall be 115 degrees-C temperature rise above 40 degrees-C ambient and shall be capable of carrying a 15 percent continuous overload without exceeding a 150 degrees-C rise in a 40 degrees-C ambient at sea level.

Manufacturers:

Square D “EE Watchdog”

Eaton/Cutler-Hammer “DS-3” and “DT-3”

Sola/Hevi-Duty “ES” and “ET.”

K-Factor Rated DRY TYPE TRANSFORMERS

Provide K rated transformers to supply high harmonic loads, as indicated on the drawings.

Manufacturer:

Square D “EE NL and EE NLP Series”

Eaton/Cutler-Hammer “KT”

Sola/Hevi-Duty 3H”.

PART 3 - EXECUTION

    - **********************************************************************************************

      - For transformer(s) that aren’t exempt from seismic, if Project Spec includes Section << 26 0548.16 - Seismic Controls for Electrical Systems>>, and if requirements associated with installation, testing, and inspection of mounting and/or anchorage devices differ from those requirements in Section << 26 0548.16 - Seismic Controls for Electrical Systems>> 26 0548., they must be described herein (in PART 3). Also, if this is applicable, identify special types of seismic-control devices required for each application using the same terminology used for those devices in PART 2.

      - The following article "Existing Work," is a designer-choice, depending if there is existing work that will be affected.

    - **********************************************************************************************

EXISTING WORK

Maintain access to existing dry-type transformers and other installations that are to remain active and to require access. Modify installation or provide access panel.

EXAMINATION

Examine surfaces to receive transformers for compliance with installation tolerances. Do not proceed with installation until unsatisfactory conditions have been corrected.

INSTALLATION

Install dry-type transformers where indicated on the drawings and according to manufacturer's instructions. Manufacturer’s installation instructions shall be available at the construction site.

Install transformers according to <<NECA 409>>, Chapter 5.

      - ***************************************************************************************

      - Mechanical: Space limitations sometimes necessitate wall-mounting a dry-type transformer above a floor mounted transformer. Each such proposed design must be analyzed by a mechanical engineer to determine the necessary vertical separation or other reliable means (e.g., redundant fans) to ensure adequate cooling for both transformers.

      - Structural: Also, each such proposed design must be analyzed and detailed by a structural engineer, and this paragraph (Installation) should be edited to require coordination of installation of wall-mounted and structure-hanging supports with actual transformer provided.

      - Seismic: If wall-mounted, suspended, or platform-mounted transformers aren’t seismically exempt, and Project Spec includes Section << 26 0548.16 - Seismic Controls for Electrical Systems>>, this paragraph should be edited with a reference to Section << 26 0548.16 - Seismic Controls for Electrical Systems>> for the bracing.

      - ***************************************************************************************

Arrange equipment to provide adequate spacing for access, replacement, and for cooling air circulation. Locate the front and rear of each ventilated transformer at least 6 inches, or as per manufacturer’s specifications, from the wall or any obstruction to allow proper air circulation.

Connect conductors to transformer terminals according to manufacturer's published torque-tightening values. Where manufacturer's torque values are not furnished, use those specified in <<UL 486A-486B>>.

Bond transformers and ground systems supplied by transformers according to Section ​​<< 26 0526 - Grounding and Bonding for Electrical Systems>>​​.

Identify transformers and install warning signs according to Section ​​<< 26 0553 - Identification for Electrical Systems>>​​.

      - ***************************************************************************************

      - Seismic: The following Article, "flexible connections," is a designer-choice depending on if flexible connections are necessary.

      - Note: Raceways smaller than 3 inch are considered flexible for seismic purposes. If all raceways connecting to the transformer are less than 3 inches, the following Article is not needed.

      - ***************************************************************************************

FLEXIBLE CONNECTIONS

Install flexible connections for transformer where shown on drawings.

FIELD QUALITY CONTROL

Clean, inspect, test, adjust, and energize transformers in accordance with chapter 6 of <<NECA 409>>.

Inspect each transformer for physical damage, proper connection, grounding, and proper anchorage.

Keep records of inspections, tests, and adjustments; submit them to the LANL STR or PIC.

After completing installation, cleaning, and testing, touch up scratches and mars on finish to match original finish.

Measure primary and secondary voltages, check phase rotation, and make preliminary tap adjustments. Adjust taps to provide the following voltage. Record voltages and tap settings.

        - System Nominal Voltage

          - 480Y/277

          - 208Y/120.

          - 120/240.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 26 2213, REV. 5, DATED APRIL 15, 2026.