Section 26 2300 
Low-Voltage Switchgear

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 4 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Electrical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality Sections.

      - ==========================================================

      - Seismic Design: This template cannot be properly edited for job-specific seismic requirements without the following three (3) decisions having been made first:

      - Whether the switchgear is subject to Seismic design

      - How to comply with ASCE 7 paragraph 13.2.1.

      - Whether the switchgear is a Designated Seismic System (DSS).  In other words, must it be operational after a seismic event.  It can only be a DSS if it is fed from a seismically credited generator or UPS, and if it feeds a load that has been designated a DSS.

      - I) If the switchgear is exempt per ASCE 7 paragraph 13.1.4 then the seismic-related requirements herein are not applicable, and the same goes for the remaining two decisions (i.e., II and III).

      - II) There are two (2) options for complying with ASCE 7 paragraph 13.2.1:

      - Project-specific design and documentation, prepared by the Engineer of Record (EOR) or the construction subcontractor (i.e., Delegated Design); or

      - Manufacturer certification

      - If the latter option applies then this Section shall reference Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>, and a project-specific version of Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>​​​ shall be created and included in the Project Spec.

      - III) DSS: If switchgear must function after the design-basis earthquake, it is assigned an Importance Factor (Ip) of 1.5 and, as a result of this, and the fact that switchgear is “active,” it is a DSS that requires Special Certification. If this applies then, regardless of the previous decision (i.e., II), this section shall reference Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>, and a project-specific version of Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>> shall be created and included in the Project Spec.

      - If II.A applies, and will be accomplished via Delegated Design, then this Section shall reference Section << 26 0548.16 - Seismic Controls for Electrical Systems>>, and a project-specific version of Section << 26 0548.16 - Seismic Controls for Electrical Systems>> shall be created and included in the Project Spec. The seismic design criteria will be included therein.

      - Finally, another reason to include Sect. << 26 0548.16 - Seismic Controls for Electrical Systems>> in a Project Spec is to specify seismic control/ restraint. Such use of Section << 26 0548.16 - Seismic Controls for Electrical Systems>> is not applicable only for projects in which switchgear is exempt and those in which compliance with ASCE 7 paragraph 13.2.1 is achieved via II.B.

      - Refer to LANL ESM Chapter 7 - Electrical, Section D5010 for requirements applicable to using a “low-voltage power circuit breaker switchgear assembly” as opposed to using a “power panelboard” or a “switchboard.” Refer to LANL Master Specification Sections << 26 2413 - Switchboards>>, and << 26 2416 - Panelboards>>.

      - Switchgear is rarely used at LANL, due to its space requirements and expense.

      - ==========================================================

      - The electrical drawings pertaining to the low-voltage switchgear should include the following information:

      - 1.  One-line diagram; refer to Drawing ST7002 in the LANL ESM Chapter 7 - Electrical.

      - 2.  Grounding one-line diagram; refer to Drawing ST7003 in the LANL ESM Chapter 7 - Electrical.

      - 3. Breaker trip unit setting table based on fault current and coordination studies:

      - a.  Circuit number.

      - b.  Load name.

      - c.  Sensor rating (amps) “S”.

      - d.  Rating plug (amps) “P”.

      - e.  Long time pickup (xP)

      - f.  Long time delay (sec).

      - g.  Short time pickup (xP) (if used).

      - h.  Short time delay (sec) (if used).

      - i.  Instantaneous pickup (xP) (if used)

      - j.  Ground fault pickup (xP)

      - k.  Ground fault delay (sec)

      - l.  Remarks

      - 4. Switchgear plan and elevation.

      - 5.  Seismic anchoring details.

      - 6.  Communications network diagram showing connection to other equipment and to a facilities operations computer. (If applicable)

  - *************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

Low-voltage arc-resistant switchgear which consists of an enclosure, power circuit breakers, instruments, metering equipment, monitoring equipment or control equipment, with associated interconnections and supporting structures.

RELATED requirements

Section << 01 2500 - Substitution Procedures>>

Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>

Section << 26 0519 - Low Voltage Electrical Power Conductors and Cables>>

Section << 26 0526 - Grounding and Bonding for Electrical Systems>>

Section << 26 0533 - Raceways and Boxes for Electrical Systems>>

Section << 26 0548.16 - Seismic Controls for Electrical Systems>>

Section << 26 0553 - Identification for Electrical Systems>>

Section << 26 0813 - Electrical Acceptance Testing>>

Section ​<< 26 2500 - Enclosed Bus Assemblies>>​

Section << 26 2713 - Electricity Metering>>

Section << 26 4300 - Surge Protective Devices>>

Section ​<< 26 5100 - Interior Lighting>>​

REFERENCE STANDARDS

ANSI C37.16 - Low-Voltage Power Circuit Breakers and AC Power Circuit Protectors Preferred Ratings, Related Requirements, and Application Recommendations.

ANSI C37.17 - American National Standard for Trip Devices for AC and General Purpose DC Low Voltage Power Circuit Breakers.

ANSI C37.50 - American National Standard for Switchgear - Low Voltage AC Power Circuit Breakers Used In Enclosures - Test Procedures.

ANSI C37.51 - American National Standard for Switchgear - Metal-Enclosed Low Voltage AC Power Circuit Breaker Switchgear Assemblies - Conformance Test Procedures.

IEEE C37.13 - IEEE Standard for Low-Voltage AC (1058 V and Below) Power Circuit Breakers Used in Enclosures.

IEEE C37.20.1 - IEEE Standard for Metal-Enclosed Low-Voltage (1000 Vac and Below, 3200 Vdc and Below) Power Circuit Breaker Switchgear.

IEEE C37.20.2 - IEEE Standard for Metal-Clad Switchgear.

IEEE C37.90 - IEEE Standard for Relays and Relay Systems Associated with Electric Power Apparatus.

IEEE C62.11 - Standard for Metal-Oxide Surge Arresters for AC Power Circuits (>1 kV).

IEEE C62.41 - IEEE Recommended Practice for Surge Voltages in Low-Voltage AC Power Circuits.

NECA 1 - Standard for Good Workmanship in Electrical Construction.

NEMA IM 60000 - Industrial Laminating Thermosetting Products.

NEMA PE 1 - Uninterruptible Power Systems (UPS) - Specification and Performance Verification.

NFPA 70 - National Electrical Code.

UL 486A-486B - Wire Connectors.

UL 746C - Polymeric Materials – Use in Electrical Equipment Evaluations.

UL 1066 - Low-Voltage AC and DC Power Circuit Breakers Used in Enclosures.

UL 1558 - Switchgear.

UL 1581 - Reference Standard for Electrical Wires, Cables, and Flexible Cords.

DEFINITIONS

For definitions and acronyms, refer to COE Glossary of Terms.

Arc-resistant: Designed to withstand the effects of an internal arcing fault and to direct the internally released energy away from personnel performing normal operating duties in close proximity to the equipment while the equipment is operating under normal conditions.

Normal operating duties: Operations such as opening or closing switching devices, connecting and disconnecting withdrawable parts, reading of measuring instruments and monitoring equipment, and so forth. Removing or replacing active components (e.g., fuses or any other removable primary component) and activities required to carry out maintenance work are not considered to be normal operations.

ACTION SUBMITTALS

Provide the following submittals according to the provisions of Project submittal procedures.

Catalog Data describing each type low-voltage switchgear, circuit breaker, accessory item, and component specified. Include data substantiating that materials comply with specified requirements.

Installation Instructions indicating application conditions and limitations of use stipulated by Product testing agency specified under Quality Assurance. Include instructions for storage, handling, protection, examination, installation, and starting of Product.

Performance Data/Curves including time-current curves for each circuit breaker.

Shop Drawings for each low-voltage switchgear assembly including dimensioned plans and elevations and component lists. Include front and side views of enclosure showing overall dimensions, enclosure type, enclosure finish, unit locations, and conduit entrances. Include the following:

Master drawing index

Front, side, and plan view of the switchgear

Single line or three line diagrams

Nameplate schedule

Component lists

Raceway entry locations

        - ******************************************************************************

        - Retain the following if Bus will be used on the project

        - ******************************************************************************

Busway entry locations and details

Assembly ratings including short circuit, voltage, and current

Major component ratings including voltage, current, and interrupting

Cable terminal sizes and types

Shipping splits

Enclosure type with details for types other than NEMA Type 1

Bus configuration and current ratings

Features, characteristics, ratings, and factory settings of individual protective devices and auxiliary components.

        - ******************************************************************************

        - Retain the following subparagraphs to match project requirements.

        - Activating Key Interlocks will activate articles/paragraphs below

        - Activating M-T-M will activate articles/paragraphs below

        - ******************************************************************************

Key interlock scheme drawing and sequence of operations.

Connection details between close-coupled assemblies.

Composite front view and plan of close-coupled assemblies.

Description of the main-tie-main automatic throw-over system to include components and operating sequences.

      - ***************************************************************************************

      - Omit the following paragraph if not required. Coordinate with Structural to make the choice below.

      - ***************************************************************************************

Additional information for seismic:

Include dimensioned plans and elevations that identify the weight, and the locations of the horizontal and vertical centers or gravity.

Indicate field anchorage or mounting provisions to hold the equipment in place and resist forces derived from the criteria specified in Section ​<< 01 8734 - Seismic Qualification of Nonstructural Components (IBC); or  26 0548.16 - Seismic Controls for Electrical Systems>>​.

Identify anchors and other mounting devices.

Include information on the size, type, and spacing of factory-installed mounting brackets, holes, and other mounting provisions

      - ***************************************************************************************

      - Edit the following paragraphs to match project requirements.  A Modified Differential Ground-Fault Detection System is sometimes installed on systems that have multiple sources, like double-ended switchgear.  The system if for the purpose of distinguishing fault current from normal neutral current.  In a system with multiple sources, neutral current can take multiple paths due to there being more than one bonding jumper.

      - **************************************************************************************

Wiring Diagrams including detailed schematic wiring diagrams including device identifications and numbered terminals for power, control, communications and instrumentation systems, and differentiating between manufacturer-installed and field-installed wiring. ​​<< Include a wiring diagram of the modified differential ground fault system.; or  None - N/A>>​​

Test Reports including results of factory production tests specified in and <<IEEE C37.20.1>> field inspections and tests required by this Section.

Operation and Maintenance Instructions including step-by-step inspection and maintenance test procedures and a listing of recommended spare parts. Include instructions for testing circuit breakers. ​<< Include a test procedure for the modified differential ground fault system using high current injection equipment.; or  None - N/A>>​

MAINTENANCE MATERIALS

For each switchgear assembly furnish one set of any special tools required to operate and maintain the equipment.

      - ***************************************************************************************

      - The following is automatically activated if keyed interlocks (kirk keys) are activated in Part 1, under "Action Submittals"

      - **************************************************************************************

For each switchgear assembly furnish two sets of keys for key interlocks.

Furnish one spray can of touch-up paint that matches finish for each switchgear assembly. Provide Material Safety Data Sheet (MSDS) for touch-up paint.

      - ***************************************************************************************

      - The following paragraph is automatically activated if M-T-M throw-over scheme is activated in Part 1, under "Action Submittals."  Automatic throw-over systems are only used on double-ended switchgear with a main-tie-main configuration.

      - ***************************************************************************************

Supply backup copies of automatic throw-over system PLC programming plus software, interface hardware, and passwords required to modify programming or re-load programming.

EXTRA MATERIALS

Furnish a total of three (3) of each size and type power and control fuse installed in the low-voltage switchgear.

Furnish one of each type circuit breaker electronic trip unit installed in the low-voltage switchgear.

For each size and type power circuit breaker in the switchgear furnish the following:

Four spare blank nameplates for circuit breaker cell doors.

      - ***************************************************************************************

      - The following paragraph is automatically activated if M-T-M throw-over scheme is activated in Part 1, under "Action Submittals."  Automatic throw-over systems are only used on double-ended switchgear with a main-tie-main configuration.

      - ***************************************************************************************

Furnish one of each type digital input module and one of each type digital output module for the programmable logic controller (PLC) associated with the automatic throw-over system.

QUALITY ASSURANCE

Comply with <<NFPA 70>>​  for installation requirements.

Furnish products that are listed and labeled by a Nationally Recognized Testing Laboratory (NRTL).

Comply with the following ANSI/IEEE standards:

<<IEEE C37.13>> / <<ANSI C37.50>>

<<ANSI C37.16>>.

<<ANSI C37.17>>

<<IEEE C37.20.1>>

Comply with <<NEMA C37.50>> and <<NEMA C37.51>>.

Comply with <<UL 1066>> and <<UL 1558>>.

DELIVERY, STORAGE, AND HANDLING

Receive, inspect, handle, and store low-voltage switchgear according to the following:

Manufacturer's written instructions.

ANSI/<<IEEE C37.20.1>>

<<NECA 1>>.

FIELD MEASUREMENTS

Make field measurements to ensure that the low voltage switchgear will fit in allocated space in full compliance with minimum clearances recommended by the manufacturer, required by <<NFPA 70>>, and the following minimum clearances:

Each end: 3’-0” plus space to add one switchgear section at one end.

Verify field measurements against manufacturer’s shop drawings prior to fabrication.

Notify the LANL STR if the allocated space is inadequate for the switchgear.

PART 2 - PRODUCTS

    - ****************************************************************************************

      - Retain the following article if substitutions are allowed on the project.

    - ****************************************************************************************

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section << 01 2500 - Substitution Procedures>>.

PERFORMANCE REQUIREMENTS

Furnish low-voltage switchgear that will perform satisfactorily in the following service conditions without mechanical or electrical damage or degradation of operating characteristics:

Operating elevation of 7500 feet above sea level.

Operating ambient temperature extremes of 32 to 104 degrees F.

Operating relative humidity: 0 to 80 percent, without condensation.

        - ******************************************************************************

        - Retain the following subparagraph to match project requirements; use only for outdoor equipment.

        - ******************************************************************************

Maximum solar heat gain: 110 W/sq ft.

      - ***************************************************************************************

      - Retain the paragraphs in the following article when the switchgear is subject to seismic design. May not be needed for seismic design category C.

      - Edit the article in accordance with project requirements. The first paragraph under 'seismic performance requirements' is for switchgear that must remain in place during and after a seismic event, but is not required to operate. The second paragraph is for equipment that must stay in place And operate. This makes it a designated seismic system, or DSS.

      - If DSS applies, this shall (also) be indicated on the drawings (i.e., as a minimum, on the sheet where the component is first shown/ indicated.).

      - ***************************************************************************************

SEISMIC PERFORMANCE REQUIREMENTS

The switchgear shall remain in place without separation of any parts when subjected to the design basis earthquake

Per Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>

        - *** OR ***

As represented by the seismic forces derived from the criteria indicated << on the drawings; or  in Section 26 0548.16 - Seismic Controls for Electrical Systems>>

The switchgear is a Designated Seismic System and, as such, it shall remain in place and be fully operational following the design basis earthquake

Per Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>

        - *** OR ***

As represented by the seismic forces derived from the criteria indicated << on the drawings; or  in Section 26 0548.16 - Seismic Controls for Electrical Systems>>

LOW-VOLTAGE SWITCHGEAR

Manufacturers:

Square D Company, “POWER ZONE 4”

Eaton, “Magnum DS”

Siemens Energy & Automation, Inc., “Type WL”

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements.

      - ***************************************************************************************

Furnish NRTL-listed << indoor; or  outdoor, walk-in>>, low-voltage switchgear that meets the requirements of ANSI/<<IEEE C37.20.1>> and <<UL 1558>> and has the following ratings:

Operating Voltage: 480Y/277 volts.

Rated Maximum Voltage: 635 volts (RMS).

Rated Frequency: 60 Hz.

Rated Insulation Level: 2.2 kV (RMS).

        - ******************************************************************************

        - Edit the following subparagraph to match project requirements; main bus rating need not exceed main breaker frame size.

        - ******************************************************************************

Main Bus Rated Current: ​<< 1600;  2000;  3200;  4000; or  5000>>​​ amperes. ​<< As scheduled on the Drawings.; or  None - N/A>>​

Neutral Bus Rated Current: 100% of the main bus rating.

        - ******************************************************************************

        - Edit the following subparagraph to match project requirements; rated short time current need not be greater than the corresponding rating of the main circuit breaker.

        - ******************************************************************************

Rated Short Time Current: ​<< 50,000;  65,000; or  85,000>>​ amperes (RMS symmetrical). ​<< As scheduled on the Drawings.; or  None - N/A>>​​

        - ******************************************************************************

        - Edit the following subparagraph to match project requirements; rated short circuit current need not be more than the corresponding rating of the main circuit breaker.

        - ******************************************************************************

Rated Short Circuit Current (SCCR): ​<< 50,000;  65,000; or  85,000>>​ amperes (RMS symmetrical). ​<< As scheduled on the Drawings.; or  None - N/A>>​

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements.

      - ***************************************************************************************

Low-voltage switchgear assembly shall be suitable for use as service equipment and be so labeled according to UL requirements.

Fabricate enclosure frame, internal barriers and outer panels following ANSI/<<IEEE C37.20.1>>

Finish interior panels and barriers with light or medium gray paint, or powder coat that is applied using an electro-deposition process over rust-inhibiting phosphate primer.

Enclosure construction shall prevent entry of rodents and reptiles into the switchgear interior.

Each circuit breaker cell shall have a hinged outer steel door with padlocking provisions. Circuit breaker cell doors shall be free of any ventilation openings.

Use Type SIS flexible stranded 90 degree C wire that is VW-1 flame test rated per <<UL 1581>> for control and communications wiring.

Secure wires in bundles using nylon ties; secure bundles to the switchgear assembly.

Connect current transformer secondary leads to accessible short-circuiting terminal blocks before connecting to any other device.

Terminate control and communications conductors on terminal blocks with suitable numbering strips; use crimp-on ring-type lugs.

Install wire markers at each end of all control and communications wiring.

Mount prominent nameplates on the front of the low-voltage switchgear assembly showing equipment designation, ratings, manufacturer identification, reference serial numbers, and special operations instructions such as for key interlocks.

Fabricate main, riser, run-back, neutral, and ground busses from silver-plated copper, with joints made up with SAE grade 5 bolts and Belleville-type spring washers.

Silver plating shall be a minimum of 0.0002 inch thick and cover the entire length of each bus bar.

The through-bus shall be rated at the full ampacity of the main throughout the switchgear.

A minimum one quarter by 2 inches ground bus shall be firmly secured to each vertical section structure and shall extend the entire length of the switchgear.

The neutral bus shall be rated at 100 percent of the main bus continuous current rating.

Phase bus bars shall be insulated with a factory applied fire retardant NRTL-recognized insulation system.  Bolted bus joints shall be insulated with secure joint covers that can be removed and reinstalled.

Insulating barriers shall separate the main bus from the rear cable compartment, separate the rear cable compartments in adjacent sections, and isolate the incoming line connections from the main horizontal and vertical bus. Insulating material shall comply with <<NEMA IM 60000>>, Grade GPO-3.

Switchgear with calculated short circuit current exceeding 65,000 amperes shall have means for cable/conductor bracing.

POWER CIRCUIT BREAKERS

      - ***************************************************************************************

      - Edit the following paragraphs to match project requirements.

      - ***************************************************************************************

All overcurrent devices; Main, Tie, and Feeder, shall be NRTL labeled, 100 percent rated, draw-out type, low voltage AC power circuit breakers. Each circuit breaker shall meet the requirements of ANSI/<<IEEE C37.13>>, <<ANSI C37.16>>, and <<UL 1066>>.

Circuit breakers shall have the following ratings:

Operating Voltage: 480Y/277 volts

Contact ratings of 600 volts

Rated Maximum Voltage: 635 volts (RMS)

Rated Frequency: 60 Hz

Rated Continuous Current: as scheduled on Drawings.

        - ******************************************************************************

        - Edit the following subparagraph to match project requirements. Include all circuit breaker frames that will be furnished. Circuit breaker short time interrupting ratings must exceed the calculated bolted fault current based on an infinite source at the primary of the immediate upstream transformer.

        - ******************************************************************************

Short Time Trip Interrupting Rating at 480 volts:

800 amp frame, << 42,000;  65,000; or  85,000>> amperes (RMS symmetrical)

1600 amp frame, << 42,000;  65,000; or  85,000>> amperes (RMS symmetrical)

2000 amp frame, << 65,000; or  85,000>> amperes (RMS symmetrical)

3200 amp frame, << 65,000; or  85,000>> amperes (RMS symmetrical)

4000 amp frame, 85,000 amperes (RMS symmetrical)

5000 amp frame, 85,000 amperes (RMS symmetrical)

        - ******************************************************************************

        - Edit the following subparagraph to match project requirements. Include all circuit breaker frames that will be furnished. Circuit breaker short time interrupting ratings must exceed the calculated bolted fault current based on an infinite source at the primary of the immediate upstream transformer.

        - ******************************************************************************

Instantaneous Trip Interrupting Rating at 480 volts:

800 amp frame, << 42,000;  65,000; or  85,000>> amperes (RMS symmetrical)

1600 amp frame, << 42,000;  65,000; or  85,000>>​ amperes (RMS symmetrical)

2000 amp frame, << 65,000; or  85,000>>​ amperes (RMS symmetrical)

3200 amp frame, << 65,000; or  85,000>> amperes (RMS symmetrical)

4000 amp frame, 85,000 amperes (RMS symmetrical)

5000 amp frame, 85,000 amperes (RMS symmetrical)

        - ******************************************************************************

        - Edit the following subparagraph to match project requirements. Some systems may require the dead bus control capability provided by station batteries; the use of station batteries must be approved by the LANL ESM Electrical POC due to the higher installation and maintenance costs.

        - ******************************************************************************

Rated Control Voltage: ​​<< 120 VAC;  125 VDC; or  48 VDC>>​​.

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements; coordinate with Drawings.

      - ***************************************************************************************

Electrically operated circuit breakers shall comply with the following:

125 vdc controls, operated by a remote battery system

48 vdc controls, operated by a remote battery system

120 volt ac controls, operated by a remote system

120 volt ac controls, derived from control power transformers internal to the switchgear

​Open/Close pushbuttons

Control Switch

Red and Green indicator lights to indicate breaker position

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements; coordinate with Drawings. Retain if needed. Specify fused circuit breakers only where available short circuit current exceeds the interrupting rating of the switchgear or down-stream equipment. Fused circuit breakers should only be needed on some renovation projects; new projects should be designed to keep the available short circuit current as low as practicable.

      - ***************************************************************************************

Fused power circuit breakers shall contain integral current-limiting fuses as indicated on the Drawings. Coordination of the circuit breaker and the integral fuses shall be such that on overloads or low magnitude short-circuits the circuit breaker will operate to clear the fault. For high magnitude short circuits the current-limiting fuses will clear the fault and then the circuit breaker shall trip open.

It shall be possible to rack each circuit breaker from the connected to the disconnected position with the cubicle door closed. Interlocks shall prevent racking the circuit breaker unless the breaker is open

Each circuit breaker shall have means for padlocking open to prevent manual or electric closing.  The padlocking shall also secure the breaker in the connected, test, or disconnected position.

Identify each circuit breaker with a unique serial number visible from the front.

Circuit breaker manual trip devices shall be recessed or otherwise protected to prevent accidental operation.

      - ***************************************************************************************

      - Retain the following paragraph to match project requirements; coordinate with Utilities to determine if this is needed on the project.

      - ***************************************************************************************

Main and tie circuit breaker cubicles shall have auxiliary switches for remote monitoring of OPEN or CLOSED position by the utility SCADA system.

Main and tie circuit breakers, and any circuit breaker that has in incident energy over 40 cal/cm2 on the line side, shall have remote, umbilical, control devices.

      - ***************************************************************************************

      - Retain the following in critical situations where the switchgear cannot be completely taken down for maintenance.  Having two ties is the only way to isolate each tie breaker in order to test it.

      - ***************************************************************************************

Supply two tie circuit breakers for double-ended equipment, such that the configuration is Main-Tie-Tie-Main.

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements.

      - ***************************************************************************************

All circuit breaker trip units shall be NRTL listed, true RMS sensing, microprocessor based devices capable of being remotely monitoring and controlled over a communications network. Each circuit breaker trip unit shall meet the requirements of <<ANSI C37.17>>, and shall have the following functions as indicated on the Drawings:

Protection: Long time, short time (with and without I2T, field selectable), instantaneous and ground fault (with and without I2T, field selectable). Instantaneous pickup setting shall have an OFF position.

LED Indications: Mode of trip and unit status.

Display: Alphanumeric display of phase and ground amperes, cause of trip, fault current, peak demand, present demand, energy consumption, and service messages.

Testing: Simulated testing of all protection functions

Communications: Breaker status (open/closed/tripped), cause of trip, time of trip, current at time of trip, RMS currents per  phase and ground, peak demand, present demand, energy consumption.

Metering: Minimum metering display accuracy of the complete system shall be +/- 2% of full scale for current values, +/- 3% of full scale for power values, +/- 4% of full scale for energy values.

        - ******************************************************************************

        - Retain the following subparagraph for systems that require selective coordination. This is only for ML-1, ML-2, and for systems required by NFPA 70 (e.g. emergency) to be selectively coordinated.

        - ******************************************************************************

Zone Selective Interlocking: Implement zone selective interlocking between circuit breakers that are required to be selectively coordinated.  Interlock both short-time and ground-fault time delays with upstream and downstream devices so the circuit breaker closest to the fault trips with no delay.

Each circuit breaker shall have means to be individually set to a maintenance mode that will reduce arc-flash incident energy by providing fast tripping in response to an arc fault even when Instantaneous on the trip unit is set to OFF.

A simple operator action shall set the circuit breaker to trip without delay at a predetermined arc fault current value; the reverse operator action shall restore the circuit breaker to its normal selective coordination settings.

The operator action shall not require adjustment of the trip unit selective coordination settings. The operator interface may be either through the switchgear communications network or by operating a two-position switch located on the circuit breaker trip unit, or above the circuit breaker cell door.

A blue light located either on the circuit breaker trip unit or above the circuit breaker cell door shall indicate that the circuit breaker is in the maintenance mode; provide a similar indication through the switchgear communications network.

Each circuit breaker cell shall have shutters that will automatically cover live parts when the circuit breaker is in disconnect, test, or remove position.

Furnish means to prevent insertion of an incorrect circuit breaker into a cell.

Completely equip breaker cells indicated as SPACE on the Drawings for the future insertion of circuit breakers with features specified in this Section.

ACCESSORIES

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements; coordinate with Drawings. It is automatically activated when Key Interlocks are activated in Part 1 under "Action Submittals." Some double-ended switchgear arrangements will be divided into two physically separated assemblies connected with a tie bus; there will be a tie circuit breaker in each assembly.

      - ***************************************************************************************

Key interlock systems shall accomplish the following functions:

Prevent closing tie circuit breaker if both main circuit breakers are closed.

Prevent closing both main circuit breakers unless tie circuit breaker is open.

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements; coordinate with Drawings; usually needed for main-tie-main automatic throw-over systems; retain if needed.

      - ***************************************************************************************

Cells shall have truck operated cell switches to indicate racking position of all draw-out circuit breakers.

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements; coordinate with Drawings; retain if needed.

      - ***************************************************************************************

Each switchgear assembly shall include a rail-mounted, traveling circuit breaker hoist and lifter bar.

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements; coordinate with Drawings.

      - ***************************************************************************************

Transformers with 220 degrees F insulation and primary plus secondary fuses shall provide 120 volt control power as required by: metering and monitoring system; ​​<< outdoor enclosure lights, receptacles and strip heaters; and  adequate power for transformer cooling fans>>​​. Use fuses with blown-fuse indicators while fuse is installed in the fuse mounting.

      - ***************************************************************************************

      - Edit the following paragraph to match renovation project requirements; coordinate with Drawings; retain if needed.

      - ***************************************************************************************

A bus transition section shall interface with the existing << _______>> / << _______>> kVA (AA/FA) << liquid filled; or  dry-type>> transformer<< s; or  None - N/A>>. Transformer<< s; or  None - N/A>> was << were; or  None - N/A>> manufactured by << _______>> and is << are; or  None - N/A>> shown on manufacturer's shop drawing number << _______>><< _______>>, dated << _______>>.

Install a mimic bus, showing bussing, connections and circuit breakers on the front panels of the switchgear. Use 0.75 inch wide, 7 mil thick white vinyl plastic tape with rubber-based adhesive.

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements; include for double ended switchgear and switchgear with multiple sources; retain if needed.

      - ***************************************************************************************

480Y/277V, 4-wire, connected switchgear having multiple sources shall have a modified differential ground fault system. The manufacturer shall complete the modified differential ground fault system design prior to building the switchgear and shall supply all components to ensure that the proper main or tie breaker(s) operate properly during the following occurrences on the main bus.

Ensure the system will trip with the occurrence of a ground fault at any location in the switchgear.

Ensure system will not trip without ground fault and with normal current flow.

Rear cable compartment doors shall have viewing ports on to allow closed-door thermographic inspection of all cable and bus connections in the rear cable compartment using a generic infrared (IR) camera with a 45 degree lens.

Each viewing port shall consist of a frame, a reinforced infrared transmitting window, and a captive cover.

Window material shall not be affected by moisture and shall have minimum infrared transmittance of 68 percent at 9 microns and 55 percent at 4 microns.

Select window diameters and place windows so all connections can be viewed with the camera at an angle not more than 30 degrees from perpendicular to the window.

Viewing windows shall comply with <<IEEE C37.20.2>> and <<UL 746C>>​.

      - ***************************************************************************************

      - Edit the following article to match project requirements; use for switchgear in unit-substations; retain if needed.

      - ***************************************************************************************

METERING

Each main circuit breaker shall have an electronic meter and associated instrument transformers, test switches and plugs, and fuses in a dedicated, barriered instrument compartment.

Mount top of meter readout approximately 60 inches above the floor.

Current transformers shall be appropriately sized for use on the main.

Furnish potential transformers if required by the meter.

Refer to Section << 26 2713 - Electricity Metering>> for metering system materials.

COMMUNICATIONS NETWORK

Each low-voltage switchgear shall have a communications network connecting the following:

Addressable trip unit in each draw-out circuit breaker to communicate:

Circuit breaker position in cradle (connected/test/disconnected).

Breaker status (open/closed/tripped).

Cause of trip, time of trip, current at time of trip.

RMS currents per phase and ground, peak demand, present demand, energy consumption.

Addressable microprocessor-based device(s) for switchgear metering.

        - ******************************************************************************

        - Edit the following to match project requirements; use for switchgear in unit-substations; retain if needed.

        - ******************************************************************************

Addressable unit substation transformer fan control devices.

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements; use the first option for single-ended switchgear; use the second option for double ended switchgear with an automatic throw-over system.

      - ***************************************************************************************

Install network interface hardware so that the communications network in the switchgear is prepared to communicate << over a 100 Mbps fiber optic or 10/100 Mbps UTP Ethernet communications network to remote PCs.; or  over an RS-485 communications network to the PLC in the switchgear.>>

      - ***************************************************************************************

      - Edit the following article to match project requirements; coordinate with Drawings; retain the entire article if needed.

      - This article describes a two-source, three breaker, closed-transition re-transfer system used in double-ended switchgear for a facility that requires the highest level of power continuity, such as a computing center.

      - Less critical facilities (e.g. typical nuclear facilities) do not require the closed transition operating sequence described in this article; for such facilities use the “open transition” re-transfer scheme described in the next article.

      - Other switchgear configurations, such as those with secondary tie circuits to separate switchgear, will require different automatic throw-over system specifications.

      - ***************************************************************************************

AUTOMATIC THROW-OVER SYSTEM  (Closed-Transition)

The double-ended low-voltage switchgear shall include a two-source, three-breaker automatic throw-over control system for the automatic operation of the main and tie circuit breakers. This system shall also provide a closed-transition operating sequence to minimize disruption of power to loads during maintenance operations and when restoring the system to its normal configuration.

The control system shall be complete with programmable logic controller (PLC), two uninterruptible power supplies (UPS), control power transfer relays, control switches and indicator lights, and other components as required to accomplish the specified functions.

Install a control panel on a cell door located away from the main or tie circuit breakers, with the following features:

A control switch for each main and tie circuit breaker for manual tripping and closing.

Three indicator lights with legend plates above each circuit breaker control switch to indicate open (green), closed (red), and tripped on overcurrent (yellow).

Key-operated, manual-maintenance-automatic operating-mode selector switch.

Three operating mode indicator lights: manual (red, flashing), maintenance (yellow, flashing), automatic (green) with legend plates.

Key operated test switch to simulate loss of voltage on either source and to permit testing of the complete automatic throw-over control system.

Two source available indicator lights (green) with legend plates.

Two control power transfer position indicator lights (amber) with legend plates.

Indicator lights shall be push-to-test LED pilot lights.

Use solid-state, draw-out case mounted protective relays that conform to the requirements of ANSI/<<IEEE C37.90>> as follows:

Two 3-phase ANSI device type 47 voltage phase sequence relays that respond to phase failure, phase unbalance and reversed phase sequence.

One single-phase ANSI device type 25 synchronism-check relay to determine that proper phase angle and voltage exist.

In the automatic mode the control system shall have the following sequence of operation:

Normal configuration: both main circuit breakers closed and the tie circuit breaker open.

Upon phase reversal or loss of voltage of either source to 70% of nominal, and after a time delay of 1 second (adjustable from 0.1 to 10 seconds), open the main circuit breaker corresponding to the failed source then immediately close the tie circuit breaker if voltage is available at the other main circuit breaker.

After the above operation, and when the failed source has been restored to normal, and synchronism check is maintained for 5 minutes (adjustable from 1 to 10 minutes, << automatically; or  permit manual controls to>> make a closed transition re-transfer: close the main circuit breaker corresponding to the restored source then immediately open the tie circuit breaker.

Include provisions to prevent automatic throw-over under the following conditions:

Simultaneous failure of both sources.

If a main or tie circuit breaker has tripped due to overcurrent or ground fault.

If either main or the tie circuit breaker is in the test or disconnected position.

If mode selector switch is in the manual or maintenance position.

If the two sources are out of synchronization.

In the maintenance mode the control system shall have the following sequence of operation:

Normal configuration: both main circuit breakers closed and the tie circuit breaker open.

Operating the control switch for either main circuit breaker shall, after synchronization check, close the tie circuit breaker then immediately open the main circuit breaker corresponding to the control switch.

After the above operation, operating the control switch for the tie circuit breaker shall, after synchronization check, close the open main circuit breaker then immediately open the tie circuit breaker.

Include provisions to prevent the above maintenance mode operations under the following conditions:

If main or tie circuit breaker has tripped due to overcurrent or ground fault.

Phase reversal or loss of phase-to-phase voltage of either source.

If main or either tie circuit breaker is in the test or disconnected position.

If the two sources are out of synchronization.

In the manual mode the control system shall have the following sequence of operation:

Normal configuration: both main circuit breakers closed and the tie circuit breaker open.

Operating the control switch for either main circuit breaker shall open or close the main circuit breaker corresponding to the control switch.

Operating the control switch for the tie circuit breaker shall close or open the tie circuit breaker.

In the manual mode, electrically interlock the main and tie circuit breakers to prevent paralleling of sources.

Use an industrial-grade PLC to control the automatic throw-over system.

PLC shall retain programming and data through power interruptions of four months duration.

PLC shall have dual power supplies connected to the two UPSs described below. Power supplies shall meet <<IEEE C62.41>>, Category B requirements for surge voltage protection.

PLC shall include digital input modules with not less than 2500 VRMS isolation between input terminals and logic. Each input channel shall have two LED indicators: an input LED that illuminates when the input receives an ON signal; a logic LED that illuminates when the input is correctly converted to a processor level logic signal. Input channels shall include but not be limited to:

Two voltage phase-sequence relays.

Synchronism-check relay.

Mode selector switch.

Two test switches.

Three circuit breaker manual close/trip control switches.

Three overcurrent trip switches.

Three sets of truck operated breaker cell connected/disconnected switches.

Two sets of four UPS status relays (AC input present, low battery, inverter operating, bypass active).

Not less than 20 percent spare input channels.

PLC shall include digital output modules with not less than 2500 VRMS isolation between input terminals and logic. Each output channel shall have three LED indicators: a logic LED that illuminates when module receives an ON signal from the processor; a load LED that illuminates when the output voltage is provided at the output terminals; a blown fuse LED that illuminates when a blown fuse is detected. Digital output modules shall contain an electronic or a field replaceable fuse for each channel. Output channels shall include but not be limited to:

Three circuit breaker close circuits.

Three circuit breaker trip circuits.

Automatic mode indicator light circuit.

Automatic mode failure indicator light circuit.

Maintenance mode indicator light circuit.

Manual mode indicator light circuit.

Source A indicator light circuit.

Source B indicator light circuit.

Not less than 20 percent spare output channels.

PLC shall include RS 485 port to interface with the communications network in the switchgear.

PLC shall include both RS-232C and Ethernet ports for communication of the following switchgear status and metering information to remote PCs or the building automation system:

Automatic throw-over system status (mode selector switch position, position of each main and tie circuit breaker, source A present, source B present).

All metering and circuit breaker status information on the switchgear communications network.

PLC status (run, error, halt, battery low).

Status of each UPS (AC input present, low battery, inverter operating, bypass active).

Fully document the automatic throw-over control system programming in the O&M manual. Supply backup copies of programming plus software, interface hardware, and passwords required to modify programming or re-load programming as O&M material. Provide detailed procedures for functional testing of the automatic throw-over system.

Use two on-line, industrial-type UPSs to power the automatic throw-over system and the associated PLC. Each UPS shall have the following features:

NRTL-listed and complying with <<NEMA PE 1>>.

Sufficient battery capacity after 2 years of operation to support the PLC through a 10 minute power interruption, then power two automatic throw-over operations at the end of the 10 minute period.

Sealed lead-acid batteries that are hot-swappable and user replaceable.

Automatic static bypass switch.

Operation panel indicating status, output load, battery voltage, and system faults.

Electrical contacts to indicate:

AC input present

Low battery

Inverter operating

Bypass active.

Automatic control power transfer relays shall transfer control power bus from one control power source to the second when the first is de-energized.

      - ***************************************************************************************

      - Edit the following article to match project requirements; coordinate with Drawings; retain the entire article if needed.

      - This article describes a two-source, three breaker, open-transition re-transfer system used in a double-ended switchgear.

      - More critical facilities (e.g. large computing facilities) may require the closed transition operating sequence described in the previous article

      - Other switchgear configurations, such as those with secondary tie circuits to separate switchgear, will require different automatic throw-over system specifications.

      - ***************************************************************************************

AUTOMATIC THROW-OVER SYSTEM  (Open-Transition)

The double-ended low-voltage switchgear shall include a two-source, three-breaker automatic throw-over control system for the automatic operation of main and tie circuit breakers.

The control system shall be complete with programmable logic controller (PLC), two uninterruptible power supplies (UPSs), control power transfer relays, control switches and indicator lights, and other components as required to accomplish the specified functions.

Install a control panel on a cell door located away from the main or tie circuit breakers, with the following features:

A control switch for each main and tie circuit breaker for manual tripping and closing.

Three indicator lights with legend plates above each circuit breaker control switch to indicate open (green), closed (red), and tripped on overcurrent (yellow).

Key-operated manual- automatic operating mode selector switch.

Two operating mode indicator lights: manual (red, flashing), automatic (green) with legend plates.

Key-operated test switch to simulate loss of voltage on either source and to permit testing of the complete automatic throw-over control system.

Two source available indicator lights (green) with legend plates.

Two control power transfer position indicator lights (amber) with legend plates.

Indicator lights shall be push-to-test LED pilot lights.

Use solid-state, draw-out case mounted protective relays that conform to the requirements of ANSI/<<IEEE C37.90>> as follows:

Two 3-phase ANSI device type 47 voltage phase sequence relays that respond to phase failure, phase unbalance and reversed phase sequence.

In the automatic mode the control system shall have the following sequence of operation:

Normal configuration: both main circuit breakers closed and the tie circuit breaker open.

Upon phase reversal or loss of voltage of either source to 70% of nominal, and after a time delay of 1 second (adjustable from 0.1 to 10 seconds), open the main circuit breaker corresponding to the failed source then immediately close the tie circuit breaker if voltage is available at the other main circuit breaker.

After the above operation and when the failed source has been restored to normal, << automatically; or  permit manual controls to>> make an open transition re-transfer: open the tie circuit breaker, then after a 5 second time delay (adjustable form 1 to 10 seconds), close the main circuit breaker corresponding to the restored source.

Include provisions to prevent automatic throw-over under the following conditions:

Simultaneous failure of both sources.

If a main or tie circuit breaker has tripped due to overcurrent or ground fault.

If tie circuit breaker is in the test or disconnected position.

If mode selector switch is in the manual position.

When in the automatic mode, disable the breaker control switches.

In the manual mode the control system shall have the following sequence of operation:

Normal configuration: both main circuit breakers closed and the tie circuit breaker open.

Operating the control switch for either main circuit breaker shall open or close the main circuit breaker corresponding to the control switch.

Operating the control switch for the tie circuit breaker shall close or open the tie circuit breaker.

In the manual mode, electrically interlock the main and tie circuit breakers to prevent paralleling of sources.

Use an industrial-grade PLC to control the automatic throw-over system.

PLC shall retain programming and data through power interruptions of four months duration.

PLC shall have dual power supplies connected to the two UPSs described below. Power supplies shall meet <<IEEE C62.41>>, Category B requirements for surge voltage protection.

PLC shall include digital input modules with not less than 2500 VRMS isolation between input terminals and logic. Each input channel shall have two LED indicators: an input LED that illuminates when the input receives an ON signal; a logic LED that illuminates when the input is correctly converted to a processor level logic signal. Input channels shall include but not be limited to:

Two voltage phase-sequence relays.

Mode selector switch.

Two test switches.

Three circuit breaker manual close/trip control switches.

Three overcurrent trip switches.

Three sets of truck operated breaker cell connected/disconnected switches.

Two sets of four UPS status relays (AC input present, low battery, inverter operating, bypass active).

Not less than 20 percent spare input channels.

PLC shall include digital output modules with not less than 2500 VRMS isolation between input terminals and logic. Each output channel shall have three LED indicators: a logic LED that illuminates when module receives an ON signal from the processor; a load LED that illuminates when the output voltage is provided at the output terminals; a blown fuse LED that illuminates when a blown fuse is detected. Digital output modules shall contain an electronic or a field replaceable fuse for each channel. Output channels shall include but not be limited to:

Three circuit breaker close circuits.

Three circuit breaker trip circuits.

Automatic mode indicator light circuit.

Automatic mode failure indicator light circuit.

Manual mode indicator light circuit.

Source A indicator light circuit.

Source B indicator light circuit.

Not less than 20 percent spare output channels.

PLC shall include RS 485 port to interface with the communications network in the switchgear.

PLC shall include both RS-232C and Ethernet ports for communication of the following switchgear status and metering information to remote PCs or the building automation system:

Automatic throw-over system status (mode selector switch position, position of each main and tie circuit breaker, source A present, source B present).

All metering and circuit breaker status information on the switchgear communications network.

PLC status (run, error, halt, battery low).

Status of each UPS (AC input present, low battery, inverter operating, bypass active).

Fully document the automatic throw-over control system programming in the O&M manual. Supply backup copies of programming plus software, interface hardware, and passwords required to modify programming or re-load programming as O&M material. Provide detailed procedures for functional testing of the automatic throw-over system.

Use two on-line industrial type UPSs to power the automatic throw-over system and the associated PLC. Each UPS shall have the following features:

NRTL-listed and complying with <<NEMA PE 1>> .

Sufficient battery capacity after 2 years of operation to support the PLC through a 10 minute power interruption then power two automatic throw-over operations at the end of the 10 minute period.

Sealed lead-acid batteries that are hot-swappable and user replaceable.

Automatic static bypass switch.

Operation panel indicating status, output load, battery voltage, and system faults.

Electrical contacts to indicate:

AC input present.

Low battery.

Inverter operating.

Bypass active.

Automatic control power transfer relays shall transfer control power bus from one control power source to the second when the first is de-energized.

      - ***************************************************************************************

      - Edit the following article to match project requirements; coordinate with Drawings; retain if needed.

      - ***************************************************************************************

Surge Protection

Each low-voltage switchgear that is being used as the Service Equipment for a structure, or as the Main for a structure fed by a feeder, shall include a Type 2 Surge Protective Device connected to the main bus on the load side of the Service, or Main, Breaker. Refer to Section << 26 4300 - Surge Protective Devices>>.

      - ***************************************************************************************

      - Edit the following article to match project requirements; retain if an outdoor enclosure is needed.

      - ***************************************************************************************

OUTDOOR ENCLOSURE

Outdoor low-voltage switchgear shall have a walk-in weatherproof enclosure with the following features:

Full length, minimum 4’-6” wide, interior aisle.

Access/exit doors with panic hardware at each end of aisle.

Hinged access doors with tamper-resistant hardware and pad-lockable handles at the rear of each switchgear section.

LED lighting providing 30 vertical foot candles on face of switchgear 3 ft above floor.

Refer to Section << 26 5100 - Interior Lighting>> for material and installation requirements.

One GFCI duplex convenience receptacle per 10 feet of length.

Thermostatically-controlled exhaust fan(s). Powered outlet dampers interlocked with powered inlet dampers. Use 30% efficiency filters on air inlets. Provide exterior rain-proof louvers on air inlets and exhaust fan outlets.

Thermostat controlled breaker cell strip heaters.

Step-down transformer and panelboard to serve the enclosure loads plus 25% spare capacity.

Removable steel cover plates over bottom conduit entrance areas.

White or light gray interior paint finish.

ANSI #61 exterior epoxy paint finish

      - ***************************************************************************************

      - Retain the following article if factory testing is required for this project.

      - ***************************************************************************************

FACTORY TESTS

Perform factory production tests that conform to <<IEEE C37.20.2>>, <<ANSI C37.50>>. Provide certification of design tests and other tests conforming to ANSI/<<IEEE C37.20.2>>, <<ANSI C37.50>> and <<ANSI C37.51>>​.

Set the circuit breaker trip units and current sensor taps to values scheduled on the Drawings or indicated in the coordination study. Test calibration of trip units and associated current sensors by primary current injection into each breaker pole, one pole at a time.

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements; include the words “modified differential” for double ended switchgear and switchgear with multiple sources. Retain the throw-over test for double-ended switchgear with throw-over capability.

      - ***************************************************************************************

Make performance tests of the low-voltage switchgear << modified differential; or  None - N/A>> ground fault protection systems by primary current injection into each breaker pole, one pole at a time. Include neutral sensor in test circuit.

Make performance tests of the automatic throw-over system.

Make performance tests of the switchgear communications network.

Make performance tests of the switchgear metering.

PART 3 - EXECUTION

    - ****************************************************************************************

      - Retain the following article when existing construction is affected.

    - ****************************************************************************************

EXISTING WORK

Maintain access to existing low-voltage switchgear that is to remain active.

EXAMINATION

Examine surfaces to receive low-voltage switchgear for compliance with installation tolerances and other conditions affecting performance of the product. Do not proceed with installation until unsatisfactory conditions have been corrected.

INSTALLATION

Install switchgear where indicated on the Drawings and according to manufacturer's instructions, ANSI/<<IEEE C37.20.1>>, and <<NFPA 70>>. Have the manufacturer’s installation instructions available at the construction site.

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements; coordinate with Drawings; omit seismic subparagraph if switchgear is exempt from seismic design.

      - ***************************************************************************************

Install switchgear on a reinforced concrete housekeeping pad as shown on the Drawings.

Refer to Section << 26 0548.16 - Seismic Controls for Electrical Systems>>.

The pad must be level to within 1/8 inch per 3-foot distance in every direction.

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements; coordinate with Drawings; retain if needed.

      - ***************************************************************************************

Install busway connections as required in Section << 26 2500 - Enclosed Bus Assemblies>> and by the switchgear manufacturer’s installation instructions.

Terminate each busway in the switchgear section containing the corresponding device.

Provide for seismic motion at the top of the switchgear as recommended by the busway or switchgear manufacturer.

Install conduits as required in Section << 26 0533 - Raceways and Boxes for Electrical Systems>> and Section << 26 0548.16 - Seismic Controls for Electrical Systems>>.

Terminate conduits in the switchgear section containing the corresponding device.

Provide for seismic motion at the top of top of the switchgear as recommended by the switchgear manufacturer.

Install plugged couplings set flush with the top of the concrete pad.  After switchgear is set in place, extend conduits to 1-1/4 inch above the pad and terminate with insulated grounding bushings.

Ground and bond the low-voltage switchgear as required in Section << 26 0526 - Grounding and Bonding for Electrical Systems>>.

Install conductors as required in Section << 26 0519 - Low Voltage Electrical Power Conductors and Cables>>.

Train conductors neatly in groups; bundle and secure if recommended by manufacturer, to withstand fault current.

Tighten electrical connectors and terminals, including bus bar and grounding connections, according to the manufacturer’s published torque-tightening values. Where manufacturer's torque values are not indicated, use those specified in <<UL 486A-486B>>​.

        - ******************************************************************************

        - Edit the following subparagraph to match project requirements; coordinate with Drawings; retain if needed.

        - ******************************************************************************

Where the calculated short circuit current exceeds 65,000 amperes, securely lace and support line and load cables in accordance with the switchgear manufacturer’s installation instructions.

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements; coordinate with Drawings; retain if needed.

      - ***************************************************************************************

Install zone selective interlock wiring to circuit breakers in other electrical equipment as indicated on the Drawings. Follow switchgear manufacturer’s instructions.

      - ***************************************************************************************

      - Omit the following paragraph if the switchgear is exempt from seismic design. Coordinate with structural to determine this.

      - ***************************************************************************************

Comply with requirements for seismic control devices and mounting and anchoring requirements specified in Section << 26 0548.16 - Seismic Controls for Electrical Systems>>.

IDENTIFICATION

Install electrical identification on low-voltage switchgear and conductors according to Section << 26 0553 - Identification for Electrical Systems>>.

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements; coordinate with Drawings; retain if needed.

      - ***************************************************************************************

Mark floor in front and rear of switchgear to <<NFPA 70>> required working clearances according to Section ​<< 26 0553 - Identification for Electrical Systems>>​.

Install engraved laminated Category I nameplate for each device. Refer to Section << 26 0553 - Identification for Electrical Systems>>.

Post one-line diagrams data and operating instructions in accordance with Section << 26 0553 - Identification for Electrical Systems>>.

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements; coordinate with Drawings; retain if needed.

      - ***************************************************************************************

Install an engraved nameplate Category 2 nameplate, red background with white lettering, with operating procedures for the automatic throw-over control system. Refer to Section << 26 0553 - Identification for Electrical Systems>>.

FIELD QUALITY CONTROL

Upon completion of installation, inspect interior and exterior of switchgear.  Remove paint splatters and other spots, dirt, and debris.

Adjust all access doors and operating handles for free mechanical and electrical operation as described in the manufacturer's instructions.

Verify that circuit breakers are in the proper cells and that setting of solid state trip devices and current sensor taps match values scheduled on the Drawings.

Witness proper torque of accessible bus connections and mechanical fasteners while unit is being installed.

      - ***************************************************************************************

      - Edit the following paragraphs to match project requirements; coordinate with Drawings; retain if needed.  Testing of the M-T-M is automatically selected when M-T-M is activated in Part 1, under 'Action Submittals."

      - Testing of key interlocks is automatically activated when Key Interlocks is activated in Part 1, under "Action Submittals."

      - ***************************************************************************************

Test the main-tie-main automatic breaker transfer system for proper functioning and accurate sequence of operation if such a system is provided.

Test each key interlock system for proper functioning if keyed interlocks are provided.

After completing installation, cleaning, and testing, touch up scratches and mars on finish to match original finish.

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements; coordinate with Drawings; retain if needed.  Testing required by Section << 26 0813 - Electrical Acceptance Testing>> is typically only for ML-1, ML-2, and systems over 800 amps.

      - ***************************************************************************************

Coordinate inspections and tests with those required by Section ​<< 26 0813 - Electrical Acceptance Testing>>​.

      - ***************************************************************************************

      - Edit the following article to match project requirements.  Retain if manufacturer's field service is required for this project.

      - ***************************************************************************************

MANUFACTURER'S FIELD SERVICE

Provide the services of a factory trained service engineer from the manufacturer to inspect and certify the installation and to oversee energizing and testing.

Manufacturer’s service engineer shall set all adjustable protective devices to the values recommend in the final coordination study.

Manufacturer’s service engineer shall certify that the equipment has been installed, adjusted, and tested in accordance with the manufacturer’s recommendations.

Provide one full workday of training for up to three owner’s representatives at the project site. A manufacturer’s qualified representative shall conduct training. The training program shall consist of instruction on the operation and maintenance of the assembly, circuit breakers, and major components within the assembly.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 26 2300, REV. 4, DATED APRIL 15, 2026.