Section 26 2413 
Switchboards

  - ************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 6 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Electrical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality Sections.

      - ==========================================================

      - Seismic Design:  This template cannot be properly edited for job-specific seismic requirements without the following three (3) decisions having been made first:

      - Whether the switchboard is not subject to seismic design or is exempt from ASCE 7 Ch. 13.

      - How to comply with ASCE 7 paragraph 13.2.1.

      - Whether the switchboard must operate after a seismic event and is, therefore, a Designated Seismic System (DSS).  The only way a switchboard can be a DSS is if it is fed from a seismically credited generator or UPS.

      - I) If the switchboard is not subject to seismic design, or is exempt per ASCE 7 paragraph 13.1.4,  the seismic-related requirements herein are not applicable, and the same goes for the remaining two decisions (i.e., II and III).

      - II) There are two (2) options for complying with ASCE 7 paragraph 13.2.1:

        - A. Project-specific design and documentation, prepared by the Engineer of Record (EOR) or the construction subcontractor (i.e., Delegated Design); or

        - B. Manufacturer certification

      - If the latter option applies then this Section (26 2413) shall reference Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>, and a project-specific version of Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>> shall be created and included in the Project Spec.

      - III) DSS: If a switchboard must function after the design-basis earthquake, it is assigned an Importance Factor (Ip) of 1.5 and, as a result of this, and the fact that switchboards are “active,” it is a DSS that requires Special Certification.  If this applies then, regardless of the previous decision (i.e., II), this section shall reference Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>, and a project-specific version of Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>> shall be created and included in the Project Spec.

      - If II.A applies, and will be accomplished via Delegated Design, then this Section shall reference Section << 26 0548.16 - Seismic Controls for Electrical Systems>>, and a project-specific version of Section << 26 0548.16 - Seismic Controls for Electrical Systems>> shall be created and included in the Project Spec.  The seismic design criteria will be included therein.

      - Finally, another reason to include Section << 26 0548.16 - Seismic Controls for Electrical Systems>> in a Project Specification is to specify seismic control/ restraint.  Section << 26 0548.16 - Seismic Controls for Electrical Systems>>is not applicable for the following projects:

      - - Where the switchboards are not subject to seismic design, or are exempt

      - - Where the switchboards are certified by the manufacturer as being seismically qualified

      - Refer to LANL ESM Chapter 7 - Electrical, Section D5010 paragraph 2.6 for requirements applicable to using a “switchboard” as opposed to using a “power panelboard” or a “low-voltage power circuit breaker switchgear assembly”. Refer to LANL Master Specifications Section << 26 2416 - Panelboards>> and Section << 26 2300 - Low-Voltage Switchgear>>.

    - **********************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

Section covers floor-mounted deadfront low-voltage switchboards which consist of an enclosure, circuit breakers, instruments and metering equipment, monitoring equipment or control equipment, with associated interconnections and supporting structures.

RELATED requirements

Section << 01 2500 - Substitution Procedures>>

Section << 01 3300 - Submittal Procedures>>

Section ​<< 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>​​​​​​​​

Section << 26 0519 - Low Voltage Electrical Power Conductors and Cables>>

Section << 26 0526 - Grounding and Bonding for Electrical Systems>>

Section << 26 0533 - Raceways and Boxes for Electrical Systems>>

Section << 26 0548.16 - Seismic Controls for Electrical Systems>>

Section << 26 0553 - Identification for Electrical Systems>>

Section << 26 0813 - Electrical Acceptance Testing>>

Section << 26 2713 - Electricity Metering>>

Section << 26 4300 - Surge Protective Devices>>

reference standards

ANSI 61 - Drinking Water System Components – Health Effects.

IEEE 837 - Qualifying Permanent Connections Used in Substation Grounding.

IEEE C37.13 - IEEE Standard for Low-Voltage AC (1058 V and Below) Power Circuit Breakers Used in Enclosures.

IEEE C37.17 - IEEE Standard for Trip Systems for Low-Voltage (1000 V and below) AC and General Purpose (1500 V and below) DC Power Circuit Breakers.

NECA 1 - Standard for Good Workmanship in Electrical Construction.

NECA 400 - Standard for Installing and Maintaining Switchboards.

NECA 407 - Standard for Installing and Maintaining Panelboards.

NEMA AB 3 - Molded Case Circuit Breakers and their Application.

NEMA PB 2 - Deadfront Distribution Switchboards.

NEMA PB 2.1 - General Instructions for Proper Handling, Installation, Operation, and Maintenance of Deadfront Distribution Switchboards Rated 1000 Volts or Less.

NETA ATS - Standard for Acceptance Testing Specifications for Electrical Power Equipment And Systems.

NETA MTS - Standard for Maintenance testing specifications.

NFPA 70 - National Electrical Code.

UL 486A-486B - Wire Connectors.

UL 489 - Molded-Case Circuit Breakers, Molded-Case Switches and Circuit Breaker Enclosures.

UL 891 - Switchboards.

UL 1066 - Low-Voltage AC and DC Power Circuit Breakers Used in Enclosures.

UL 1581 - Reference Standard for Electrical Wires, Cables, and Flexible Cords.

ACTION SUBMITTALS

Submit the following in accordance with Section << 01 3300 - Submittal Procedures>>:

Catalog Data: Submit catalog data describing each type switchboard, circuit breaker, metering, accessory item, and component specified. Include data substantiating that materials comply with specified requirements.

Installation Instructions: Indicate application conditions and limitations of use stipulated by Product testing agency specified under Quality Assurance. Include instructions for storage, handling, protection, examination, installation, and starting of Product.

Operation and Maintenance Instructions: Submit operation and maintenance instructions including step-by-step inspection and maintenance test procedures and a listing of recommended spare parts. Include instructions for testing circuit breakers.

Performance Data/Curves: Submit time current characteristic (TCC) curves for each circuit breaker.

Shop Drawings: Submit shop drawings for each switchboard including dimensioned plans and elevations and component lists. Include front and side views of enclosure showing overall dimensions, enclosure type, enclosure finish, unit locations, and conduit entrances. Include the following:

Front, side, and plan view of the switchboards.

Single line or three line diagrams.

Nameplate schedule.

Component lists.

Conduit entry locations.

Busway entry locations and details.

Switchboard ratings including short circuit current rating (SCCR), voltage, and current.

Major component ratings including voltage, current, and interrupting (AIC).

Conductor terminal sizes and types.

Shipping splits.

Enclosure type with details for types other than NEMA Type 1.

Bus configuration and current ratings.

Features, characteristics, ratings, and factory settings of individual protective devices and auxiliary components.

          - **********************************************************************

          - The following subparagraph is a designer-choice and applies only if Kirk-Key interlocks will be specified for the switchboard.  This is not common.

          - **********************************************************************

Key interlock scheme drawing and sequence of operations.

          - **********************************************************************

          - Omit the following subparagraph if not required. Coordinate with Structural to make the choice below.

          - **********************************************************************

Additional information for seismic:

Include dimensioned plans and elevations that identify the weight, and the locations of the horizontal and vertical centers or gravity.

Indicate field anchorage or mounting provisions to hold the equipment in place and resist forces derived from the criteria specified in Section ​​<< 01 8734 - Seismic Qualification of Nonstructural Components (IBC); or  26 0548.16 - Seismic Controls for Electrical Systems>>​​.

Identify anchors and other mounting devices.

Include information on the size, type, and spacing of factory-installed mounting brackets, holes, and other mounting provisions

Test Reports: Submit results of field inspections and tests required by this Section.

EXTRA MATERIALS

Provide one spray can of touch-up paint that matches switchboard finish.

O&M:  Furnish any special tools that are required to operate and maintain the equipment.

Setup: Furnish any special tools and/or equipment that are required to set up the equipment.

Furnish a total of three (3) of each size and type power and control fuse installed in the switchboard.

QUALITY ASSURANCE

Provide products that are listed and labeled by a Nationally Recognized Testing Laboratory (NRTL), where such products are required by <<NFPA 70>>​ to be listed, or such products contain an electrical hazard as follows:

For AC circuits – Greater than 50 volts.

For DC circuits – Greater than 100 volts.

Comply with <<IEEE C37.13>>  and <<IEEE C37.17>>​

Comply with <<NEMA PB 2>>  and <<NEMA AB 3>>

Comply with <<UL 891>>, <<UL 489>>, <<UL 1066>>,  <<UL 486A-486B>>, and <<UL 1581>>.

​delivery, storage, and handling

Receive, inspect, handle, and store switchboard(s) according to the following:

Manufacturer's written instructions.

<<NECA 1>> and <<NECA 400>>

<<NEMA PB 2.1>>

FIELD MEASUREMENTS

Verify field measurements against manufacturer’s shop drawings, as applicable, prior to assembly.

PART 2 - PRODUCTS

MANUFACTURERS

Eaton: “Pow-R-Line"

Siemens: “Sentron”

Square D: “QED-2”

      - ***************************************************************************************

      - The following Article is a designer-choice and applies only if substitutions are allowed on the project.

      - ***************************************************************************************

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section << 01 2500 - Substitution Procedures>>.

PERFORMANCE REQUIREMENTS

Provide switchboards and accessories that will perform satisfactorily in the following service conditions without mechanical or electrical damage or degradation of operating characteristics:

Elevation of 7,500 feet above sea level.

Maximum ambient temperature of extremes of 32 to 104 degrees F.

Operating relative humidity: 0 to 80 percent, without condensation.

        - ******************************************************************************

        - The following subparagraph is a designer-choice and applies to outdoor equipment.

        - ******************************************************************************

Maximum solar heat gain: 110 W/sq ft.

Conform to <<NEMA PB 2>> service conditions during and after installation of switchboards.

      - ***************************************************************************************

      - Retain the paragraphs in the following article when the switchboard is subject to seismic design. Coordinate with Structural to make the choices. Designated Seismic Systems must be fed from a seismically credited generator or UPS. This is very rare.

      - Edit the article in accordance with project requirements. The first paragraph under 'seismic performance requirements' is for switchboard that must remain in place during and after a seismic event, but is not required to operate. The second paragraph is for equipment that must stay in place And operate. This makes it a designated seismic system, or DSS.

      - If DSS applies, this shall (also) be indicated on the drawings (i.e., as a minimum, on the sheet where the component is first shown/ indicated.).

      - ***************************************************************************************

SEISMIC PERFORMANCE REQUIREMENTS

The switchboard shall remain in place without separation of any parts when subjected to the design basis earthquake

Per Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>

        - *** OR ***

As represented by the seismic forces derived from the criteria indicated << on the drawings; or  in Section 26 0548.16 - Seismic Controls for Electrical Systems>>

The switchboard is a Designated Seismic System and, as such, it shall remain in place and be fully operational following the design basis earthquake

Per Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>

        - *** OR ***

As represented by the seismic forces derived from the criteria indicated << on the drawings; or  in Section 26 0548.16 - Seismic Controls for Electrical Systems>>

      - ***************************************************************************************

      - This long authors note is for the Design Agency.

      - 1.  Switchboard information required on the Drawings includes the following (from NEMA PB 2):

      - a.     Rating of supply

        - 1.  Voltage

        - 2.  Number of phases

        - 3.  Bus rating in amperes

        - 4.  Available short circuit-current at the line terminals of the switchboard

        - 5.  Frequency (if other than 60 Hz.)

      - b.   Cables/Conductors

        - 1.  Size

        - 2.  Type

        - 3.  Number

        - 4.  Entry location (top or bottom)

      - c.  Busway

        - 1.  Entry location(s) and phase orientation

        - 2.  Description

        - 3.  Grounding method

      - d. Ground-fault protection for main and feeder circuit breakers (Refer to LANL ESM Chapter 7 - Electrical, Section D5010 paragraph 2.6.3-E.)

      - e.  Enclosure type (NEMA 1, NEMA 3R walk-in)

      - f. Main disconnect device (Refer to LANL ESM Chapter 7 - Electrical, Section D5010 [paragraph 2.6.1-for requirement to have a single main disconnect.)

        - 1.  Type (e.g. fixed molded-case circuit breaker, draw-out power circuit breaker,)

        - 2.  Ampere rating

        - 3.  Standard or 100% continuous current rated

        - 4.  Poles

        - 5. Trip unit settings (Refer to LANL ESM Chapter 7 - Electrical, Section D5000 paragraph 4.2-D.4)

      - g.  Locations where the incident energy is greater than 40 cal/cm2

        - 1.  These locations will have to be compartmentalized

      - h  Feeder and branch circuit devices

        - 1.  Type (e.g. panel-mounted circuit breaker, rear connected circuit breaker,)

        - 2.  Ampere ratings

        - 3.  Poles

        - 4.  Quantity

        - 5. Trip unit settings (Refer to LANL ESM Chapter 7 - Electrical, Section D5000 [paragraph4.2-D.4.])

      - i.  Zone-selective interlocking: within switchboard, between switchboard and upstream or downstream switchboards or switchgear.

      - j.  Intended application: service equipment, non-service equipment, separately derived system.

      - k.  Construction features

        - 1.  Front accessible, rear accessible, front and side accessible, rear and side accessible, etc.

        - 2.  Individually mounted circuit breakers

        - 3.  Panel (Group) mounted circuit breakers

      - l.  Unusual service conditions beyond those described under PERFORMANCE REQUIREMENTS.

      - m.  Where working access will be available (front, rear, side).

      - ***************************************************************************************

SWITCHBOARD GENERAL REQUIREMENTS

Provide enclosed switchboard that is designed and fabricated in accordance with <<NEMA PB 2>>, and has electrical ratings and configurations as indicated on Drawings or specified in this Section.

Where shown on the drawings as the Service Equipment, switchboards shall be identified as being suitable for use as Service Equipment.

​Switchboards shall include a grounding bar or bus.

All locations in the switchboard that have an incident energy of 40 cal/sq. cm. or higher must be in a barriered compartment.

SWITCHBOARD ENCLOSURE

Provide switchboard with NEMA Type 1 general purpose or NEMA Type 3R weather-resistant walk-in enclosure as indicated on the Drawings or as required by the installation location.

Section alignment:

Switchboards with front accessible load connections shall have sections rear aligned.

Switchboards with rear accessible load connections shall have sections front and rear aligned.

Provide removable steel base channels (1.5 inch floor sills) bolted to the frame to rigidly support the entire shipping section for moving on rollers and floor mounting.

Enclosure shall be painted on all surfaces with manufacturer’s standard medium gray, applied by electro-deposition over an iron phosphate pre-treatment.

Front covers shall be screw removable with a single tool and doors shall be hinged with removable hinge pins.

      - ***************************************************************************************

      - Switchboards with rear-connected circuit breakers and compartmented/barriered construction are considered to be more reliable and safer to maintain than those with front connections. However, rear connected switchboards are significantly more expensive and larger than switchboards with front accessible connections, and, of course, require rear access. Carefully consider costs versus benefits before specifying a rear-connected switchboard. The following requirements do not apply to sections with panel-mounted circuit breakers.

      - ***************************************************************************************

Provide compartments and barriers in switchboard sections containing rear-connected circuit breakers.

Provide separate compartments for circuit breakers, distribution bus, and cable connections.

All incoming or outgoing busways or conduits and power conductors shall be routed through and terminated in the cable compartments. Provide adequate space for the busways or conduits that will terminate in each section.

Provide insulating barriers between the circuit breaker compartment and the distribution bus compartment.

Provide insulating barriers between the circuit breaker compartment and the adjacent sections.

Individually mount each circuit breaker in a compartment with full steel barriers at the top, bottom, and sides.

        - ******************************************************************************

        - The following subparagraph is a designer-choice and applies If the main breaker has an incident energy greater than 40 cal, on the line side.

        - ******************************************************************************

Main circuit breaker shall be in a separate compartment.

SWITCHBOARD BUSSING

Provide switchboard with copper phase ​​<< and neutral; or  None - N/A>>​​ bus.

Provide full-rated, non-tapered bus through switchboard.

For 4-wire systems, the neutral bus shall be of equivalent ampacity as the phase bus bar unless otherwise indicated on the Drawings.

Switchboards used on 480V and 480Y/277V systems shall have bus insulators and separations rated for minimum 600V.

Bus connection areas shall be silver-plated.

All bus joints shall consist of Grade 5 hardware and conical spring washers (Belleville).

All bolted bus connections shall be accessible for maintenance after switchboard is installed.

Make full provisions for the addition of future sections; include all necessary hardware to accommodate splicing for future additions.

Fully insulate bus bars in rear accessible compartments. Do not reduce spacing of insulated bus.

Provide copper equipment ground that extends through each switchboard section.

Size ground bar per <<UL 891>> but not smaller than required for mounting <<IEEE 837>> 2-hole compression lugs.

Provide bolt holes in NEMA 1.75-inch pattern to accept 2-hole lugs.

Bond ground bus to each switchboard section.

Make full provisions for the addition of future switchboard sections; include all necessary hardware to accommodate splicing for future additions.

      - ***************************************************************************************

      - The following Article is a designer-choice and applies if metering is part of the switchboard.

      - ***************************************************************************************

SWITCHBOARD METERING

Provide electronic meter, instrument transformers, test switches and plugs, and fuses specified in Section << 26 2713 - Electricity Metering>>​, in a dedicated, barriered instrument compartment.

Mount top of meter readout approximately 60 inches above the bottom of the switchboard.

Furnish <<NEMA PB 2>> transformer compartment for current transformers specified in Section << 26 2713 - Electricity Metering>>.

Provide current transformers appropriately sized for use on the main.

Provide potential transformers if required by the meter.

SWITCHBOARD CIRCUIT BREAKERS

Provide circuit breakers as indicated on the Drawings and specified in this Section.

Provide circuit breakers of the type, rating, and features as indicated on the Drawings.

Provide 600 V rated circuit breakers on 480 V or 480Y/277 V systems.

Provide permanently-installed handle lock-off device that will accept a padlock for each circuit breaker.

      - ***************************************************************************************

      - Select draw-out mounted main circuit breaker where circuit breaker weight will be equal to or greater than 42 lb. Some 1200 ampere circuit breakers weigh less than the calculated 42 lb NIOSH lifting limit and may be fixed mounted. NFPA 70 requires than a main circuit breaker 1000 amperes and greater on a 470Y/277 V system have ground-fault protection, necessitating an electronic trip unit. Zone-selective interlocking might be required within switchboards with electronic trip circuit breakers. Zone-selective interlocking might also be required between switchboards with electronic trip circuit breakers and upstream low-voltage power circuit breaker switchgear. Refer to LANL ESM Chapter 7 - Electrical, Section D5010 (paragraph 2.6.3).

      - ***************************************************************************************

Main Circuit Breaker

Provide fixed-mounted molded-case main circuit breaker if circuit breaker weight is less than 42 lb.

If ground-fault protection or zone-selective interlocking is required, provide electronic trip unit as described below.

If ground-fault protection or zone-selective interlocking is not required, provide circuit breaker with thermal-magnetic trip unit having an adjustable instantaneous trip.

Provide draw-out mounted main circuit breaker if circuit breaker weight is equal to or greater than 42 lb.

Provide molded-case or insulated case circuit breaker that complies with <<UL 489>>​, or power circuit breaker that complies with <<IEEE C37.13>>.

Provide electronic trip unit as described in paragraph Electronic Trip Units, in this article.

Provide separate compartment for main circuit breaker, such that the line side incident energy will not be available while working in the rest of the switchboard.

Feeder and branch circuit breakers:

Provide fixed-mounted molded-case feeder and branch circuit breakers.

Circuit breakers shall comply with <<UL 489>>.

If ground-fault protection or zone-selective interlocking is not required, provide circuit breakers with thermal-magnetic trip unit having an adjustable instantaneous trip.

If ground-fault protection or zone-selective interlocking is required, provide circuit breakers with electronic trip unit as described in paragraph Electronic Trip Units, in this article.

          - **********************************************************************

          - Switchboards with compartmented/ barriered construction and rear-accessible load connections are considered to be more reliable and safer to maintain than those with front connections. However, rear connected switchboards are significantly more expensive and larger than switchboards with front accessible connections, and, of course, require rear access. Carefully consider costs versus benefits before specifying a rear-connected switchboard.

          - **********************************************************************

Load connections shall be ​​​<< front-accessible; and  rear accessible>>​​​.

      - ***************************************************************************************

      - Not all trip units require ground-fault pickup and delay.

      - ***************************************************************************************

Electronic Trip Units:

Provide NRTL-listed circuit breaker electronic trip units conforming to <<IEEE C37.17>> Tri.

Provide field interchangeable rating plug.

Trip unit shall have adjustable functions as follows:

Long-time pickup and delay.

Short-time pickup and delay.

Instantaneous pickup with OFF position.

Ground fault pickup and delay, where shown on drawings.

        - ******************************************************************************

        - The following subparagraph is a designer-choice and is only required when systems must be selectively coordinated.  This is typically only required for Emergency systems and is very rare.

        - ******************************************************************************

Provide zone selective interlocking for each electronic trip unit. Implement zone selective interlocking between main and feeder circuit breakers within the switchboard with electronic trip units. Interlock both short-time and ground-fault time delays with upstream and downstream trip units so the circuit breaker closest to a fault will trip with no delay.

Trip unit shall use true RMS current sensing.

The following trip indications shall be visible on the front of the trip unit:

Long-time.

Short-time or instantaneous.

Ground fault.

Provide a removable and sealable transparent cover for trip unit adjustments and rating plug to comply with <<NFPA 70>>  requirement 240.6(C).

Provide neutral conductor current transformers if required for ground-fault protection.

SURGE PROTECTION

Provide Surge Protective Devices per Section << 26 4300 - Surge Protective Devices>>.

IDENTIFICATION

Provide engraved laminated Category I nameplate for each device.  Refer to Section << 26 0553 - Identification for Electrical Systems>>.

Show the entire single line switchboard bus work, as depicted on the factory record drawing, on an engraved nameplate. The nameplate plate shall be located at eye level on the front cover of the switchboard incoming service section.

CONTROL WIRING

Use Type SIS flexible stranded 90 degree C wire that is VW-1 flame test rated per <<UL 1581>> for control and communications wiring.

Secure wires in bundles using nylon ties; anchor bundles to the switchgear assembly using pre-punched wire lances.

Connect current transformer secondary leads to accessible short-circuiting terminal blocks before connecting to any other device.

Terminate control and communications conductors on terminal blocks with suitable numbering strips; use crimp-on solderless lugs.

Provide wire markers at each end of all control and communications wiring.

      - ***************************************************************************************

      - The following Article and paragraphs are designer-choices and apply  if Switchboard Accessories are required for the project.

      - ***************************************************************************************

SWITCHBOARD ACCESSORIES

Provide the following accessories, modifications, or special features for switchboards as indicated on the Drawings, or as required.

Provide portable, floor supported, elevating carriage with roller base, for movement of circuit breakers in and out of switchboard structure. Provide appropriate lifter bars and attachments for lifting circuit breakers.

Provide shunt-trip for circuit breaker(s) indicated on the Drawings.

Provide transformer(s) with 220 degrees F insulation and primary plus secondary fuses to provide 120 volt control power as required by: metering and monitoring system; ​​<< outdoor enclosure lights, receptacles;  electric heaters; and  adequate power for transformer cooling fans>>​​. Provide transformers rated for not less than 125 percent of the connected equipment load. Provide fuses with blown-fuse indicators while fuse is installed in the fuse mounting.

      - ***************************************************************************************

      - The following paragraphs and subparagraphs are designer-choices, as required for the project.

      - ***************************************************************************************

For switchboards installed outdoors or in damp indoor locations, provide thermostatically-controlled electric heaters in each section.

Provide 240V heaters, 250 watts minimum, with sufficient capacity to control moisture condensation in each section.

Provide industrial-type thermostat for each section to maintain 60 to 90 degrees F.

Provide truck operated cell switch to indicate racking position of the main circuit breaker.

Provide a bus transition section to interface with the existing ​​<< _______>>​​ /​​<< _______>>​​  kVA (AA/FA) ​​<< liquid filled; or  dry-type>>​​ transformer. Transformer was manufactured by ​​<< _______>>​​ and is shown on manufacturer's shop drawing number ​​<< _______>>​​, dated ​​<< _______>>​​.

      - ***************************************************************************************

      - The following Article is a designer-choice and applies if there are outdoor switchboards on the project.

      - ***************************************************************************************

OUTDOOR ENCLOSURE

Provide walk-in outdoor enclosure with the following features:

Full length interior aisle not less than 3 ft.-6 inches wide.

Access/exit doors with panic hardware at each end of aisle.

Hinged access doors with tamper-resistant hardware and pad-lockable handles at the rear of each switchgear section.

LED lighting that provides not less than 30 vertical foot candles on face of switchgear 3 ft above floor.

One GFCI convenience duplex receptacle per 10 feet of enclosure length.

Thermostatically-controlled exhaust fan(s). Powered outlet dampers interlocked with powered inlet dampers. Provide 30 percent efficiency filters on air inlets. Provide exterior rain-proof louvers on air inlets and exhaust fan outlets.

Removable steel cover plates over bottom conduit entrance areas.

White or light gray interior paint finish.

<<ANSI 61>>​ exterior epoxy paint finish to match LANL standard utility color, Fawn #3604.

PART 3 - EXECUTION

    - **********************************************************************************************

      - For switchboards that are subject to seismic design, if Project Spec includes Section << 26 0548.16 - Seismic Controls for Electrical Systems>>, and if requirements associated with installation, testing, and inspection of mounting and/or anchorage devices differ from those requirements in Section << 26 0548.16 - Seismic Controls for Electrical Systems>>, they must be described herein (in PART 3). Also, if this is applicable, identify special types of seismic-control devices required for each application using the same terminology used for those devices in PART 2.

      - The following article is a designer-choice and applies if "Existing Work" on the project will be affected.

    - **********************************************************************************************

EXISTING WORK

Maintain access to each existing switchboard that is to remain active.

Clean and repair each existing switchboard that is to remain or be reinstalled.

EXAMINATION

Examine surfaces to receive switchboard(s) for compliance with installation tolerances and other conditions affecting performance of the product. Do not proceed with installation until unsatisfactory conditions have been corrected.

INSTALLATION

Install switchboard(s) where indicated on the Drawings and according to manufacturer's instructions, <<NECA 407>>​​​, and <<NFPA 70>>. Have the manufacturer’s installation instructions available at the construction site.

Provide a minimum of 1/2 inch space between the back of switchboard and a wall; provide a minimum of 6 inch space for damp locations.

Remove temporary lifting eyes, channels, brackets, and temporary blocking of moving parts from switchboard enclosure and components.

Ground and bond switchboards as required in Section << 26 0526 - Grounding and Bonding for Electrical Systems>>​.

Install raceways as required in Section << 26 0533 - Raceways and Boxes for Electrical Systems>>.

Terminate raceways in the switchboard section containing the corresponding device.

​Risers entering the switchboard from below grade should be RTRC (fiberglass).  This negates the need for grounding bushings.

Install conductors as required in Section << 26 0519 - Low Voltage Electrical Power Conductors and Cables>>.

Bundle and secure conductors, if recommended by manufacturer, to withstand fault current.

Tighten electrical connectors and terminals, including bus bar and grounding connections, according to the manufacturer’s published torque-tightening values.  Where manufacturer's torque values are not indicated, use those specified in <<NETA ATS>>, or <<NETA MTS>> Tables 100.12.1, 100.12.2, 100.12.3, or 100.12.4, or <<NFPA 70>> Annex I as appropriate

      - ***************************************************************************************

      - Omit the following paragraph if the switchboard is exempt from seismic design.

      - ***************************************************************************************

Comply with requirements for seismic control devices and mounting and anchoring requirements specified in Section ​<< 26 0548.16 - Seismic Controls for Electrical Systems>>​.

IDENTIFICATION

Identify switchboard and install warning signs and arc-flash warning labels as required in Section << 26 0553 - Identification for Electrical Systems>>​.

Provide Category I nameplates for overcurrent protective devices. Refer to Section << 26 0553 - Identification for Electrical Systems>>.

FIELD QUALITY CONTROL

Clean, inspect, test, and energize switchboards in accordance with <<NECA 407>>.

Verify that circuit breakers are in the proper locations and that settings of  trip units and current sensor taps match values scheduled on the Drawings.

Exercise each circuit breaker three times to verify smooth mechanical operation.

Witness proper torque of accessible bus connections and mechanical fasteners while switchboard is being installed.

      - ***************************************************************************************

      - Retain the following paragraph if formal acceptance testing is required by Section << 26 0813 - Electrical Acceptance Testing>>. This is typically only for ML-1, ML-2, and systems over 800 Amps.

      - ***************************************************************************************

Coordinate inspections and tests with those required by Section << 26 0813 - Electrical Acceptance Testing>>.

After completing installation, cleaning, and testing, touch up scratches and mars on finish to match original finish.

      - ***************************************************************************************

      - Retain the following article if Manufacturer's Field Service is required. This is rare.

      - ***************************************************************************************

MANUFACTURER'S FIELD SERVICE

Provide the services of a factory trained representative from the manufacturer to inspect and certify the installation and to oversee energizing and testing.

Manufacturer’s representative shall certify in writing that the equipment has been installed, adjusted, and tested in accordance with the manufacturer’s recommendations.

Provide one full work day of training for up to three owner’s representatives at the Project site.  A manufacturer’s qualified representative shall conduct training session.  The training program shall consist of instruction on the operation and maintenance of the switchboard, circuit breakers, and major components.

END OF SECTION

    - *********************************************************************************************

      - Do not omit the following reference information:

    - *********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 26 2413, REV. 6, DATED APRIL 15, 2026.