Section 26 2416 
Panelboards

  - ************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTIOn

Rev. 5 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Electrical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality Sections.

      - ==========================================================

      - Seismic Design: This template can only be properly edited for job-specific seismic requirements once the following three (3) decisions have been made:

      - I.     Whether the panelboard is exempt from ASCE 7 Ch. 13.

      - II.     How ASCE 7 paragraph 13.2.1 is going to be complied with.

      - III.     Whether the panelboard must operate after a seismic event. (i.e., it is a Designated Seismic System (DSS))

      - Note: In some cases, equipment is not in the scope of ASCE 7, particularly if it is outside a building, not in a path of egress, and does not have to remain in place or function after a seismic event. This will have to be determined by the responsible structural engineer.

      - I) If the panelboard is not in the scope of ASCE 7, or if it is exempt from ASCE 7 per paragraph 13.1.4, then the seismic-related requirements herein are not applicable, and the same goes for the remaining two decisions (i.e., II and III).

      - II) There are two (2) options for complying w/ ASCE 7 paragraph 13.2.1:

      - A.  Project-specific design and documentation, prepared by:

      - a. the Engineer of Record (EOR)

      - b. the construction subcontractor (i.e., Delegated Design)

      - B.  Manufacturer certification.

      - If the latter option applies then this Section (26 2416) shall reference Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>, and a project-specific version of Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>> shall be created and included in the Project Spec.

      - III) DSS: If a panelboard must function after the design-basis earthquake, it is assigned an Importance Factor (Ip) of 1.5 and, as a result of this, and the fact that panelboards are “active,” it is a DSS that requires Special Certification. If a panelboard must function after a seismic event, it must be supplied by a seismically credited generator or UPS.  If this applies then, regardless of the previous decision (i.e., II), this Section (26 2416) shall reference Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>, and a project-specific version of Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>​ shall be created and included in the Project Spec.

      - If II.A applies, and will be accomplished via Delegated Design, then this Section (26 2416) shall reference Section << 26 0548.16 - Seismic Controls for Electrical Systems>>, and a project-specific version of Section << 26 0548.16 - Seismic Controls for Electrical Systems>> shall be created and included in the Project Spec. The seismic design criteria will be included therein.

      - Finally, another reason to include Section << 26 0548.16 - Seismic Controls for Electrical Systems>> in a Project Spec is to specify seismic control/ restraint. Such use of Section << 26 0548.16 - Seismic Controls for Electrical Systems>>is not applicable, only for projects in which panelboards are exempt and those in which compliance w/ ASCE 7 paragraph 13.2.1 is achieved via II.B. Seismic control/ restraint is achieved by devices (e.g., supports and attachments) that provide restraint against excessive movement during an earthquake without compromising the effectiveness of vibration isolators. Since these devices are included in Section << 26 0548.16 - Seismic Controls for Electrical Systems>>, if a Project Spec includes it then only devices that differ from those therein (that are required for use) need be included herein.

  - ************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

      - ***************************************************************************************

      - The following two paragraphs are designer-choice, based on if panelboards, load centers, or both, are part of the project.

      - ***************************************************************************************

Panelboards for feeder and branch circuit loads.

      - ***************************************************************************************

      - The use of load center panelboards is limited to ML-4 panelboards with a maximum mains rating of 225 amperes, a maximum of 42 single-pole spaces, and an available short-circuit current not exceeding 10,000 amperes RMS symmetrical.  Load center type panelboards should only be used for light duty non-critical applications.

      - Note:  “Load center panelboards” are tested under the same UL standard as panelboards.  “Load center” is a term that is used by manufacturers to indicate a lighter duty, commodity panel, but it has no actual definition in the electrical industry.

      - ***************************************************************************************

Load center type panelboards for 120/240 V single-phase, or 208/120 V three phase, loads.

RELATED Requirements

Section << 01 2500 - Substitution Procedures>>​

Section << 01 3300 - Submittal Procedures>>​

Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>​

Section << 26 0548.16 - Seismic Controls for Electrical Systems>>

Section << 26 4300 - Surge Protective Devices>>​

reference STANDARDS

NECA 1 - Standard for Good Workmanship in Electrical Construction.

NECA 407 - Standard for Installing and Maintaining Panelboards.

NEMA PB 1 - Panelboards.

NEMA PB 1.1 - General Instructions for Proper Installation, Operation and Maintenance of Panelboards Rated 1000V or Less.

NFPA 70 - National Electrical Code.

UL 50 - Enclosures for Electrical Equipment, Non-Environmental Considerations.

UL 67 - Panelboards.

UL 489 - Molded-Case Circuit Breakers, Molded-Case Switches and Circuit Breaker Enclosures.

UL 870 - Wireways, Auxiliary Gutters, and Associated Fittings.

ACTION SUBMITTALS

Submit the following in accordance with Section << 01 3300 - Submittal Procedures>>​:

Catalog Data: Submit catalog data describing each type panelboard, accessory item, and component specified. Include data substantiating that materials comply with specified requirements.

Installation Instructions: Manufacturer’s instructions concerning installation.

Operation and Maintenance Instructions: Submit operation and maintenance instructions.

EXTRA MATERIALS

Furnish six spare keys of each type for panelboard cabinet locks.

Furnish one spray can of touch-up paint that matches panelboard finish.

QUALITY ASSURANCE

Comply with <<NFPA 70>>​ for installation considerations such as bending space for conductors.

Furnish products that are listed and labeled by a Nationally Recognized Testing Laboratory (NRTL), where such products are required by<<NFPA 70>> to be listed, or such products contain an electrical hazard as follows:

For AC circuits – Greater than 50 volts

For DC circuits and batteries – Greater than 100 volts.

Comply with <<NEMA PB 1>>, and  <<NEMA PB 1.1>>​.

Furnish products suitable for operation at 7,500 ft. altitude.

​Delivery, storage, and handling

Receive, inspect, handle, and store panelboards according to <<NECA 1>>, and <<NECA 407>>.

PART 2 - PRODUCTS

    - **********************************************************************************************

      - The following Article is a designer-choice and applies only if substitutions are allowed on the project.

    - **********************************************************************************************

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section << 01 2500 - Substitution Procedures>>.

PERFORMANCE REQUIREMENTS

Provide panelboards and accessories that will perform satisfactorily in the following service conditions:

Elevation of 7500 feet above sea level.

Maximum ambient temperature of 104 degrees F.

        - ******************************************************************************

        - The following is a designer-choice and applies to outdoor equipment.

        - ******************************************************************************

Maximum solar heat gain: 110 W/sq ft.

Conform to <<NEMA PB 1>> service conditions during and after installation of panelboards.

      - ***************************************************************************************

      - Seismic: For panelboards that are subject to seismic design, if Project Spec includes Section << 26 0548.16 - Seismic Controls for Electrical Systems>>, and if mounting and/or anchorage devices are to be used that differ from those specified in Section << 26 0548.16 - Seismic Controls for Electrical Systems>>, they must be described herein (in PART 2).

      - Retain the paragraphs in the following Article when the panelboard is subject to seismic design. Omit the article when the panel board is exempt from seismic design.

      - Include the first paragraph if the panelboard is required to remain in place after an event, but is not required to function. (positional retention)

      - Include the second paragraph if the panelboard is required to function after an event. (Designated Seismic System)

      - If the panelboard is a Designated Seismic System, this shall (also) be indicated on the drawings (i.e., as a minimum, on the sheet where the component is first shown/indicated.).

      - ***************************************************************************************

SEISMIC PERFORMANCE REQUIREMENTS

The panelboard shall remain in place without separation of any parts when subjected to the design basis earthquake

Per Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>.

        - *** OR ***

As represented by the seismic forces derived from the criteria indicated << on the drawings; or  in Section 26 0548.16 - Seismic Controls for Electrical Systems>>.

The panelboard is a Designated Seismic System and, as such, it shall remain in place and be fully operational following the design basis earthquake

Per Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>.

        - *** OR ***

As represented by the seismic forces derived from the criteria indicated << on the drawings; or  in Section 26 0548.16 - Seismic Controls for Electrical Systems>>.

PANELBOARDS

Furnish panelboards as indicated on the Drawings and specified in this Section.

Panelboards shall be <<UL 67>> listed and shall conform to <<NEMA PB 1>>.

Main bus rating for the panelboards described in this Section shall not exceed 800 amperes and main circuit breaker frame size shall not exceed 800 amperes.

Furnish panelboard cabinets for flush or surface mounted as indicated on the Drawings.

Furnish NEMA Type 1 enclosures, except where the Drawings or conditions of installation indicate the following enclosure requirements:

NEMA 3R: Raintight

NEMA 3S: Raintight and dust tight

NEMA 4X: Corrosion-resistant fiberglass enclosure, watertight, dust tight, and resistant to oil and coolant seepage

NEMA 12: Dust tight, dripproof, and resistant to oil and coolant seepage.

Furnish galvanized steel cabinets constructed according to <<UL 50>> requirements.

Furnish trim fronts that meet the strength and rigidity requirements of <<UL 50>>.

Each panelboard trim front shall include a door.

Fronts for surface-mounted panels shall be same dimensions as box.

Fronts for flush panels shall overlap boxes at least 1 inch.

Fronts shall have gray enamel electro-deposited over cleaned, phosphatized steel.

For NEMA 1 panelboards, furnish fronts with hinged door-in-door trim construction.  The front shall contain a smaller lockable door, which when open, shall provide access to all device handles and rating labels.  The hinged front, when open, shall provide access to all conductors and wiring terminals.  The panelboard door shall open by a single lockable latch; the entire hinged front trim shall open by removing screws.

Furnish a panelboard circuit directory card in a metal frame mounted inside the panelboard door. The directory card shall include spaces for circuit numbers and sufficient spaces to allow each circuit to be described in sufficient detail to be distinguished from all others.

Furnish cylindrical tumbler type locks for doors. Furnish sliding vault locks with 3-point latching for enclosures more than 48 inches high. Key all lock assemblies alike.

Panelboard phase and neutral bus shall be copper.  Panelboards used on 480V and 480Y/277V systems shall have bus insulators and separations rated for minimum 600V.

Furnish equipment ground bus that is adequate for feeder and branch circuit equipment grounding conductors.

Furnish panelboards having short circuit current ratings not less than the available fault current indicated on the Drawings.  With the exception of panelboard with a current-limiting main circuit breaker, do not use “series ratings” for circuit breaker interrupting capacities.  The short circuit rating for a panelboard without a current-limiting main circuit breaker shall not exceed the lowest interrupting capacity rating of any circuit breaker installed in the panelboard.

Circuit Breakers for Square-D iLine panels shall not be numbered.  They shall be identified by a letter.  These panels are not positionally dependent and if numbers are used, they can be confused with the phases that would normally be associated with those numbers.  A single letter can either be a single-pole circuit, a double-pole circuit, or a three-pole circuit.

Furnish thermal-magnetic circuit breakers that meet the requirements of <<UL 489>>.

Furnish circuit breakers of the type, rating, and features as indicated on the Drawings.

Furnish 600V-rated circuit breakers for 480V or 480Y/277V systems.

Furnish circuit breakers with the following minimum  interrupting capacities:

208Y/120V and 120/240V applications: 10,000 amperes, RMS symmetrical

480V and 480Y/277V applications: 14,000 amperes, RMS symmetrical.

Furnish field adjustable instantaneous trip setting for circuit breakers with frame size greater than 225 amperes.

Furnish bolt-on type circuit breakers, or circuit breakers that connect to the panel bus through positive gripping connector jaws and are secured by an independent mechanical locking device.

Single-pole, 15 and 20 ampere circuit breakers intended to switch fluorescent lighting loads on a regular basis shall have the SWD marking.

Circuit breakers intended to switch high intensity discharge lighting loads on a regular basis shall have the HID marking.

Furnish UL Class A ground fault interrupter circuit breakers where shown on Drawings.

Furnish circuit breakers with provisions for connecting the size and number of conductors indicated on the Drawings.

Furnish a permanently-installed handle lock-off device for each circuit breaker.

Furnish handle lock-off device that will accept a 1/4-inch padlock shackle.

Securely attach the device to the circuit breaker case; the attachment shall not depend on a friction fit or the presence of the panelboard front for the handle lock-off device to remain in place and be functional.

      - ***************************************************************************************

      - The following paragraph, and subparagraphs, are designer-choices.  Include accessories that are required.

      - ***************************************************************************************

Furnish the following accessories, modifications, or special features for panelboards as indicated on the Drawings.

Conduit Covers for Surface Mounted Panels: Same gage and finish as panel front with flanges for attachment to panel, wall, and the floor.

Shunt trip: Shunt-trip main circuit breaker or shunt-trip branch circuit breakers.

Control Power Source: Control power transformer of capacity indicated, for contactor shunt trip or other devices.  Mount in cabinet of panel indicated.  Protect primary with current-limiting fuses.  Furnish fused protection of control circuits.

Auxiliary Wireway Space: Dimensions and arrangement as indicated on the Drawings.

Auxiliary Wireway Barrier: Arranged to isolate section of wireway as indicated.

Auxiliary Wireway: Conform to <<UL 870>>.

Column Type Panelboard Configuration: Narrow cabinet extended as wireway to overhead junction box equipped with ground and neutral terminal buses.

Feed-Through Lugs: Sized to accommodate feeders indicated.

Surge Protective Devices: Refer to Section << 26 4300 - Surge Protective Devices>>.

Manufacturers:

Eaton:

480 V and 480Y/277 V: “PRL3a” and “PRL4”

208Y/120 V and 120/240 V: “PRL1a” and “PRL2a”

Siemens:

480 V and 480Y/277 V: “P2”, “P3”, and “P4”

208Y/120 V and 120/240 V: “P1”

Square D:

480 V and 480Y/277 V: “NF” and “I-LINE”

208Y/120 V and 120/240 V: “NQ” and “I-Line”

LOAD CENTER PANELBOARDS

Furnish <<UL 67>> listed and labelled load center type panelboards as indicated on the Drawings and specified in this Section.

Main bus rating for the load center type panelboards described in this Article shall not exceed 225 amperes.

Furnish steel load center cabinets for flush or surface mounted as indicted on the Drawings.

Furnish NEMA Type 1 enclosures for indoor applications.

Furnish NEMA Type 3R enclosures for outdoor applications.

Furnish steel trim fronts that meet the strength and rigidity requirements of <<UL 50>>.

Fronts for surface-mounted panels shall be same dimensions as box

Fronts for flush panels shall overlap boxes at least 1 inch

Fronts shall have gray enamel finish.

Furnish equipment ground bus that is adequate for feeder and branch circuit equipment grounding conductors, as well as other required bonding jumpers.

Load centers identified for use as service equipment shall be NRTL-labeled for this application.

Furnish thermal-magnetic circuit breakers that meet the requirements of <<UL 489>>.

Furnish circuit breakers of the type, rating, and features as indicated on the Drawings.

Furnish circuit breakers with an interrupting capacity of 10,000 amperes, RMS symmetrical.

Stab-in type circuit breakers are acceptable.

Furnish circuit breakers that are not less than 3/4 inches wide.

Furnish a permanently-installed handle lock-off device for each load center circuit breaker.

Furnish handle lock-off device that will accept a 1/4-inch padlock shackle.

Firmly attach the device to the circuit breaker case; the attachment shall not depending on a friction fit or the presence of the load center front for the handle lock-off device to remain in place and be functional.

Manufacturers:

Eaton: “BR” and “CH”

Siemens: “EQ" and “Ultimate”

Square D: “QO”

PART 3 - EXECUTION

    - **********************************************************************************************

      - For panelboards subject to seismic design, if Project Spec includes Section << 26 0548.16 - Seismic Controls for Electrical Systems>>, and if requirements associated with installation, testing, and inspection of mounting and/or anchorage devices differ from those requirements in Section << 26 0548.16 - Seismic Controls for Electrical Systems>>, they must be described herein (in PART 3). Also, if this is applicable, identify special types of seismic-control devices required for each application using the same terminology used for those devices in PART 2.

      - The following Article, Existing Work, is a designer-choice and applies if work will take place in an existing facility.

    - **********************************************************************************************

EXISTING WORK

Maintain access to existing panelboards and other installations that are to remain active and that require access. Modify installation or furnish access panel.

Clean and repair existing panelboards, if necessary, to accomplish the scope of the project.

INSTALLATION

Install panelboards where indicated on the Drawings and according to manufacturer's instructions, <<NEMA PB 1.1>>, <<NECA 407>>, and <<NFPA 70>>.  Have the manufacturer’s installation instructions available at the construction site.

Position panelboards so the top circuit breaker handle is not more than 6 ft.-7 inches above the standing surface of the working space in front of the panelboard.

      - ***************************************************************************************

      - Omit the following paragraph if the panelboard is exempt from seismic design.

      - ***************************************************************************************

Comply with requirements for mounting, anchoring, and seismic control devices specified in Section << 26 0548.16 - Seismic Controls for Electrical Systems>>​.

IDENTIFICATION

New installations: Furnish printed circuit directories for each branch circuit panelboard.

Furnish one hard copy and an electronic copy of the panelboard schedule to the Facility Manager at project closeout.

Install a plastic-laminated copy of the circuit directory on the inner side of the panelboard door.

      - ***************************************************************************************

      - The following paragraph is a designer choice and applies to existing installations.

      - ***************************************************************************************

Existing installations: Where circuits have been added to an existing panelboard, modify the panel directory to reflect the new circuits.

FIELD QUALITY CONTROL

Clean, inspect, and energize panelboards. Operate each circuit breaker on and off three times to verify smooth mechanical operation.

After completing installation, cleaning, and testing, touch-up scratches and mars on finish to match original finish.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING REFERENCE IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 26 2416, REV. 5, DATED APRIL 15, 2026.