Section 26 2713 
Electricity Metering

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION section

Rev. 6 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Electrical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality Requirements.

      - ==========================================================

      - NOTE:  Metering is required when (1) buildings are 5000 square feet or more or (2) the Main or Service is 400 Amps or greater.

      - Electrical systems connected to the LANL distribution system but billed for electrical services by LA County are not covered by this Section.

  - ************************************************************************************************************

PART 1 - GENERAL

Section Includes

Multi-function, digital electrical meter

Test switches

Instrument transformers

      - ***************************************************************************************

      - Retain Meter Cabinets if needed on the project.  Sometimes, all the metering equipment is in the main gear and a metering cabinet is not necessary.

      - ***************************************************************************************

Meter current transformer cabinet

Related Requirements

Section << 01 2500 - Substitution Procedures>>

Section << 01 3300 - Submittal Procedures>>

Section << 26 0553 - Identification for Electrical Systems>>

Section << 26 2300 - Low-Voltage Switchgear>>​

Section << 26 2413 - Switchboards>>​

Reference standards

ANSI C12.1 - Electric Meters - Code for Electricity Metering.

ANSI C12.9 - Test Switches and Plugs for Transformer-Rated Meters.

ANSI C12.20 - American National Standard for Electricity Meters - 0.1, 0.2, and 0.5 Accuracy Classes.

IEEE C57.13 - IEEE Standard Requirements for Instrument Transformers.

NECA 1 - Standard for Good Workmanship in Electrical Construction.

NFPA 70 - National Electrical Code.

UL 486A-486B - Wire Connectors.

COORDINATION

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements. Retain the following paragraph if metering will be installed in the main panel, instead of using a metering cabinet.

      - ***************************************************************************************

Coordinate installation of metering components in the service, or main, ​​<< switchboard; or  switchgear assembly>>​​.

Coordinate the features of the meter and associated instrument transformers with the ratings and characteristics of the circuit to be metered.

Provide not less than 14 working days’ notice to LANL STR to arrange for LANL Utilities to inspect, program, and test the meter prior to Project final inspection.

LANL-PERFORMED WORK

LANL Utilities will inspect, test, program, and adjust the meter, meter wiring, Ethernet communication wiring, and Ethernet communications interface.

SUBMITTALS

Submit the following per Section << 01 3300 - Submittal Procedures>>:

Catalog data and manufacturer's technical data.  Provide catalog sheets showing ratings, dimensions, and enclosure details.

Installation instructions indicating application conditions and limitations of use stipulated by Product testing agency specified under Article Quality Assurance.  Include instructions for storage, handling, protection, examination, preparation, installation, and starting of Product.

Operation and maintenance instructions.

EXTRA MATERIALS

Furnish spare fuses—not less than one set of three of each size and type.

QUALITY ASSURANCE

Conform to the installation requirements of <<NFPA 70>>​.

Conform to requirements of <<ANSI C12.1>>​

Furnish products listed and labeled by a Nationally Recognized Testing Laboratory (NRTL) where <<NFPA 70>> requires them to be listed, or they contain voltages of over 50 volts AC or 100 volts DC.

DELIVERY, STORAGE, AND HANDLING

Receive, store, and protect, and handle products according to <<NECA 1>>

PART 2 - PRODUCTS

PRODUCT OPTIONS AND SUBSTITUTIONS

Substitutions are not allowed on the meter itself.  For other products, see Section << 01 2500 - Substitution Procedures>>.

MULTI-FUNCTION DIGITAL ELECTRICAL METER

Provide addressable multi-function, microprocessor-based, digital electrical meter(s) as indicated on the Drawings.  Meter shall meet the following standards:

Meet <<ANSI C12.20>>, Electricity Meters 0.2 accuracy class.

Setup parameters required for the meter shall be stored in non-volatile memory and retained in the event of a control power interruption.  Any battery used to provide non-volatile memory must be serviceable from the front of the meter.

Manufacturer: Square D. Contact LANL UI Metering at umetering@lanl.gov for current meter selection/standard. No substitution.

      - ***************************************************************************************

      - Adequate instrument transformers may exist in retrofit applications.  The standard meter used by LANL-UI does not require Potential Transformers for 480/277 volt systems.

      - ***************************************************************************************

INSTRUMENT TRANSFORMERS

Provide ​<< Current; and  Potential>>​​​​​​​​​​​​​​​​​​ transformers, conforming to <<IEEE C57.13>> metering accuracy class 0.3, of suitable ratio and burden for specified metering.

Provide current transformers (CT) having 5 Amp secondary and a continuous current rating factor of not less than 1.33.

Current transformers for low voltage circuits (600 V and less) shall have 10 kV BIL.  Current transformers for 15 kV class circuits shall have 110 kV BIL.

Provide with window opening adequate for the conductors or bus bars.

Manufacturer: ABB

          - **********************************************************************

          - Edit the following subparagraphs to match Project requirements.  Select CT to match system voltage, current, and usage.

          - **********************************************************************

Type CMS, through 200:5 at 600 V or less.

Type CMF, through 1200:5 at 600 V or less.

Type CMV, through 3000:5 at 600 V or less.

Type CLC, through 4000:5 at 600 V or less.

Type CLE, through 5000:5 at 600 V or less.

Type KIR-11, indoors at 15 kV.

Type KOR-11, outdoors at 15 kV.

Type KON-11, outdoors at 15 kV.

      - ***************************************************************************************

      - The specified multi-function digital meter does not require potential transformers when connected to a 480Y/277 V system.

      - The following paragraph is a designer-choice, depending on if Potential Transformers are needed.

      - ***************************************************************************************

Provide potential transformers (PT) having 120 VAC secondary.

Potential transformers for low voltage circuits (600 V and less) shall have 10 kV BIL.  Potential transformers for 15 kV class circuits shall have 110 kV BIL.

Manufacturer: ABB

          - **********************************************************************

          - Edit the following subparagraph to match Project requirements. Select PT to match system voltage.

          - **********************************************************************

Type VIZ-11 with 2 primary fuses for 15 kV system indoors.

Type VOY-11 for 15 kV system outdoors.

Type PPW for 480 V system.

      - ***************************************************************************************

      - Edit the following article to match Project requirements.  Adequate test switches and plugs may exist in retrofit applications.

      - **************************************************************************************

TEST SWITCHES AND PLUGS

Provide semi-flush mounted test switches in meter potential and current circuits to facilitate testing of the meter installation and also external connection of additional portable metering equipment.

Provide test switches that comply with <<ANSI C12.9>>  and automatically short circuit current transformer circuits when the switches are opened prior to inserting the test plug.

Test switch shall have enough potential and shorting type current poles as are needed by the number of potential transformers and current transformers being used.

Provide plastic cover for each test switch.

Provide matching test plugs designed for in-service testing.

Manufacturers: States “Type FMS”.

      - ***************************************************************************************

      - Edit the following article to match Project requirements.

      - ***************************************************************************************

POTENTIAL CIRCUIT FUSES

Provide UL Class CC, time-delay, 600 V, 3-ampere fuses to protect each potential lead to the meter.

Provide each fuse with a cover having a blown-fuse indicator.

Manufacturer: Bussman “Type FNQ-R fuses, BC Series fuse blocks, and SAMI-7I fuse covers.”

      - ***************************************************************************************

      - The following paragraph is a designer-choice, for indoor medium-voltage installations.

      - ***************************************************************************************

For indoor medium-voltage metering installations, protect the primary of each potential transformer with indoor, current-limiting, 1/2 Amp, 14,400 V fuses having blown fuse indication.  Manufacturer: S&C “Fusistor.”

      - ***************************************************************************************

      - The following paragraph is a designer-choice, for outdoor medium-voltage installations.

      - ***************************************************************************************

For outdoor medium-voltage metering installations, protect the primary of each potential transformer with outdoor, 1 Amp, 14,400 V power fuses.  Manufacturer: S&C “SMD-20 with SMU-20 fuse unit”.

CURRENT TRANSFORMER SHORTING BLOCK

Provide 600v, 30A, 6-terminal CT shorting block to isolate all CT circuits to meter.

WIRING AND TERMINATIONS

Current transformer secondary circuits: TYPE SIS SWITCHBOARD WIRE stranded copper.  Use 12 AWG for circuits less than 50 ft.; when 50 ft or more, use 10 AWG.

Potential transformer secondary circuits:  use 12 AWG, Type, TYPE SIS SWITCHBOARD WIRE stranded copper,

Use crimp-on, nylon-insulated, insulation-grip, brazed-seam terminals for instrument wiring as follows:

On Nutted studs:  Use ring tongue terminals.  Manufacturer: Burndy “Type TN” for all current circuits.

On Barrier terminal strips: Use flanged fork terminals.  Manufacturer: Burndy “YAE-Z” for potential circuits.

On DIN-type terminal blocks: Use pin terminals.  Manufacturer: 3M “MNG-P”.

Use 18 AWG shielded, twisted pair, Belden 8723 cable for RS-485 connections per meter manufacturer recommendations.

      - ***************************************************************************************

      - Edit the following article to match Project requirements.  Use meter cabinets for retrofit applications or where there is insufficient space to mount the meter and test switches in the main panelboard or switchgear.

      - ***************************************************************************************

METER CABINETS

Provide a metal current transformer (CT) cabinet with hinged door to house the meter test switches, fuse blocks, << potential transformers,; or  None - N/A>> current transformers, and CT shorting block.

Minimum cabinet size: 36” high, 30” wide, 11” deep.

Manufacturer: Hoffman A-363011HCT.

Provide a meter cabinet with hinged door to house the meter module, display module, communications interfaces, and accessories.

Minimum cabinet size: 12” high, 12” wide, 6” deep.

Manufacturer: Hoffman A-12R126HCLO.

Outdoor installations shall be rated NEMA 3R minimum with a door-in-door enclosure (for meter display protection).

PART 3 - EXECUTION

    - **********************************************************************************************

      - Retain the following article when existing construction is involved.

    - ***************************************************************************************

EXISTING WORK

Maintain access to existing meters and other installations remaining active and requiring access. Modify installation or provide access panel.

Clean and repair existing, LANL-acceptable meters and associated cabinets, instrument transformers and test blocks to remain or to be reinstalled.

EXAMINATION

Examine surfaces to receive meters and associated cabinets, instrument transformers and test blocks for compliance with installation tolerances and other conditions affecting performance of the raceway system.  Do not proceed with installation until unsatisfactory conditions have been corrected.

INSTALLATION

Install metering equipment according to manufacturer's instructions.  Have the manufacturer’s installation instructions available at the construction site.

Tighten electrical connectors and terminals according to manufacturers published torque-tightening values.  Where manufacturer's torque values are not furnished, use those specified in <<UL 486A-486B>>​.

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements.

      - ***************************************************************************************

Identify meter, << test switches; and  instrument transformers>> and meter wiring  according to Section << 26 0553 - Identification for Electrical Systems>>, Identification for Electrical Systems. <<  Install voltage and arc-flash warning labels on cover of instrument transformer cabinet.; or  None - N/A>>

Install CT cabinet and meter cabinet adjacent to service, or main, equipment.

Install 3/4 inch plywood backboard painted with two coats of fire-retardant paint in the CT cabinet.

Mount current transformers on plywood backboard in the CT cabinet; position transformers to minimize stress from power conductors.

Mount potential circuit fuse block and CT shorting block on plywood backboard in the CT cabinet.

Recess mount meter test switches in current transformer CT cabinet door.

Locate meter cabinet so display is approximately 60 inches above the floor.

Interconnect metering components as indicated on the Drawings.

      - ***************************************************************************************

      - The following paragraph is a designer-choice, when instrument transformers will be installed within a service, or main, switchboard or switchgear assembly, instead of in a separate cabinet. Coordinate this paragraph with Section << 26 2300 - Low-Voltage Switchgear>> or Section << 26 2413 - Switchboards>> as applicable.

      - Coordinate with LANL ISD-TS, if necessary, if a network connection is needed.

      - ***************************************************************************************

Install metering components within the electrical service, or main, switchgear. Refer to Section ​​<< 26 2300 - Low-Voltage Switchgear; or  26 2413 - Switchboards>>​​.

Install potential transformers and associated potential fuses in dedicated potential transformer compartment.

Install current transformers on main bus in accordance with switchgear manufacturer’s standard details.

Install meter in a dedicated metering compartment.

Recess mount meter test switches in switchgear metering compartment door.

Locate meter display on switchgear metering compartment door approximately 60 inches above the floor.

Interconnect metering components as indicated on the Drawings.

Provide control power to meter in accordance with the manufacturer’s instructions.

Use a dedicated, fuse-protected, 120 V circuit or a dedicated, fuse-protected, control power transformer if potential transformers are required for the metering voltage inputs.

Control power may be derived from the fuse-protected metering voltage inputs when potential transformers are not required.

Wire current and potential leads through test switch.

Install fuse protection in the potential leads on the line side of the test switch.

Use shorting-type switches for the current transformer leads.

Provide communications connection between the building telecommunications system and the Ethernet port associated with the meter.

Install conduit pathway for communications cables from the << meter cabinet; or  switchboard or switchgear metering cubicle>> to within 1 ft. of the telecommunications outlet.

Install suitable communications cables and terminations.

Connect meter to telecommunications outlet using a CAT-6 cord.

FIELD QUALITY CONTROL

Inspect accessible components for cleanliness, mechanical, and electrical integrity, and for presence of damage or deterioration before energizing.

LANL STR, Construction Supervisor, or Job Superintendent will contact the Utilities and Infrastructure group at least 7 days before the completion of the project so that UI can inspect, test, program and adjust the meter, meter wiring, and communications interface.

Correct deficiencies in material, wiring, or installation that may be discovered.

After completing installation, cleaning, and testing, touch-up scratches and mars on finish to match original finish.

END OF SECTION

    - ***************************************************************************************

      - Do not omit the following reference information:

    - ***************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 26 2713, REV. 6, DATED APRIL 15, 2026.