Section 26 2726 
Wiring Devices

  - ************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 7 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Electrical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality Sections.

  - ************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

      - ***************************************************************************************

      - The following paragraphs are designer-choices based on project-specific requirements.

      - ***************************************************************************************

Receptacles - ​​​​<< Click to select options from the drop down menu;  General Use;  Industrial Heavy Duty;  Hazardous Locations; and  Automatic Receptable Control - New Construction only>>​​​​

General Use Snap switches - ​<< Click to select options from the drop down menu;  General Use; and  Hazardous Locations>>​

Pendant/Cord Connector Devices

Wallbox dimming controls

Wall plates

Multioutlet (receptacle) assemblies

Occupancy sensing lighting controls

Occupancy sensing lighting/receptacle control system

Dual-Level Lighting Control

Stairwell Lighting Control

related requirements

Section << 01 2500 - Substitution Procedures>>​

Section << 01 3300 - Submittal Procedures>>.

Section ​<< 26 0553 - Identification for Electrical Systems>>​​

Section << 26 5100 - Interior Lighting>>

reference standards

ASHRAE 90.1 - Energy Standards for Buildings Except Low-Rise Residential Buildings.

NECA 1 - Standard for Good Workmanship in Electrical Construction.

NEMA WD 6 - Wiring Devices - Dimensional Specifications.

NFPA 70 - National Electrical Code.

UL 5 - Surface Metal Raceways and Fittings.

UL 20 - General-Use Snap Switches.

UL 498 - Attachment Plugs and Receptacles.

UL 894 - Switches for Use in Hazardous (Classified) Locations.

UL 1449 - Standard for Surge Protective Devices.

UL 1472 - Solid-State Dimming Controls.

UL 1682 - Plugs, Receptacles, and Cable Connectors of the Pin and Sleeve Type.

UL 2043 - Fire Test for Heat and Visible Smoke Release for Discrete Products and Their Accessories Installed in Air-Handling Spaces.

UL 2682 - Switch-Rated Plugs and Receptacles.

COORDINATION

Coordinate with other work, including painting, electrical boxes and wiring installations, to interface installation of wiring devices with other work.

Field locations of walls, partitions, doors, windows and equipment may vary from locations shown on the Drawings. Prior to locating sleeves, boxes and chases for roughing-in of conduit and equipment, coordinate with other trades to determine exact field location of the above items. Verify direction of door swings so that local switches are properly located on the strike side of the doorway.

Coordinate wiring device colors with ​​​<< Architect;  Interior Designer;  Facility Manager; and  _______>>​​​.

Coordinate receptacle requirements for items of equipment provided to the Project under other sections in the specification package, or by LANL.

      - ***************************************************************************************

      - The following Article is a designer-choice, based on project-specific requirements.  Submittals are only required for occupancy sensors or similar complicated wiring devices.

      - ***************************************************************************************

ACTION SUBMITTALS

Submit the following per Section << 01 3300 - Submittal Procedures>>:

Catalog Data:  Only required for occupancy sensors or similar complicated wiring devices.

QUALITY ASSURANCE

Comply with <<NFPA 70>> (NEC) for installation requirements.

Furnish products listed and labeled by a nationally recognized testing laboratory (NRTL).

​Delivery, Storage, and handling

Receive, store, and protect, and handle products according to <<NECA 1>>.

COORDINATION

Coordinate with other work, including painting, electrical boxes and wiring installations, to interface installation of wiring devices with other work.

Field locations of walls, partitions, doors, windows and equipment may vary from locations shown on the Drawings. Prior to locating sleeves, boxes and chases for roughing-in of conduit and equipment, coordinate with other trades to determine exact field location of the above items. Verify direction of door swings so that local switches are properly located on the strike side of the doorway.

Coordinate wiring device colors with ​​<< Architect;  Interior Designer;  Facility Manager; and  _______>>​​.

Coordinate receptacle requirements for items of equipment provided to the Project under other sections in the specification package, or by LANL.

PART 2 - PRODUCTS

    - **********************************************************************************************

      - The following Article is a designer-choice, based on if substitutions are allowed on the project.

    - **********************************************************************************************

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section << 01 2500 - Substitution Procedures>>.

RECEPTACLES

Provide back- and side-wired, screw terminal, straight-blade and locking-type receptacles as indicated on the drawings. Back-stab connections are not acceptable.

Receptacles shall meet the performance and design requirements of  <<UL 498>>.

Hubbel EdgeConnect receptacles may be the most appropriate for locations where torquing of screws is not possible, such as in gloveboxes.

Receptacle configurations shall be in accordance with <<NEMA WD 6>>.

Catalog numbers in this section do not indicate receptacle color; see Article << 2.14; or  _______>>Finishes below.

For 125 volt convenience receptacles connected to general purpose 20 ampere branch circuits, provide straight-blade NEMA 5-15R, 15 amperes, 125 volts, grounding duplex receptacles. Receptacle mounting strap, ground terminal, and ground contacts shall be formed from one piece of brass alloy.

Manufacturer: Hubbell “HBL5262.”

Where indicated on the Drawings for special-purpose 125 volt duplex receptacles connected to 20 ampere branch circuits, provide straight-blade NEMA 5-20R, 20 amperes, 125 volts grounding duplex receptacles. Receptacle mounting strap, ground terminal, and ground contacts shall be formed from one piece of brass alloy.

Manufacturer: Hubbell “HBL5362.”

For 125 volt receptacles connected to 20 ampere individual branch circuits provide straight-blade NEMA 5-20R, 20 amperes, 125 volts, grounding single receptacles. Receptacle mounting strap, ground terminal, and ground contact shall be formed from one piece of brass alloy.

Manufacturer: Hubbell “HBL5361.”

For 125 volt receptacles connected to individual 15 ampere branch circuits provide straight-blade NEMA 5-15R, 15 amperes, 125 volts, grounding single receptacles. Receptacle mounting strap, ground terminal, and ground contact shall be formed from one piece of brass alloy.

Manufacturer: Hubbell “HBL5261.”

      - ***************************************************************************************

      - The following two paragraphs are designer-choice.  Isolated ground systems may only be installed with the permission of the LANL ESM Electrical Point of Contact.  The first paragraph is for general purpose circuits.  The second paragraph is for Individual Branch Circuits.

      - ***************************************************************************************

For isolated ground 125 volt circuit receptacles connected to isolated ground 20 ampere branch circuits provide straight-blade NEMA 5-20R, 20 amperes, 125 volts, isolated grounding duplex receptacles with orange triangle on face.

Manufacturer: Hubbell “IG5362”

For isolated ground 125 volt circuit receptacles connected to individual isolated ground branch circuits provide straight-blade NEMA 5-20R, 20 ampere, 125 volts, isolated grounding single receptacles with orange triangle on face.

Manufacturer: Hubbell “IG5361”

For ground fault circuit interrupter (GFCI) receptacles provide straight-blade NEMA 5-15R, 15 ampere, 125 volts, grounding, “feed through” type, GFCI, duplex receptacle that meet the requirements of UL Standard 943, Ground Fault Circuit Interrupters. Provide units that can be installed in a 2-3/4-inch deep outlet box without an adapter.

Manufacturer: Hubbell “GF15”

For integral surge-protected 125 volt convenience receptacles connected to general purpose branch circuits provide straight-blade NEMA 5-15R, 15 amperes, 125 volts, grounding duplex receptacles that meet the requirements of <<UL 1449>>. Receptacle mounting strap, ground terminal, and ground contacts shall be formed from one piece of brass alloy. Receptacle shall include an LED to indicate power and surge protection status and an audible alarm with silencer to indicate loss of surge protection.

Manufacturer: Hubbell “HBL5262SA”

Provide straight-blade and twist lock receptacles for special applications as indicated on the Drawings.

Where items of equipment are provided to the Project under other sections of this specification or by LANL, provide a compatible receptacle for the cap or plug and cord of the equipment.

      - ***************************************************************************************

      - Match devices to plug connectors for LANL-furnished equipment.  Although both UL 1682 and UL 2682 are acceptable, UL 2682 is preferred.  UL 1682 is for Pin and Sleeve connectors.  UL 2682 is for Butt Contacts.  In the long run, Butt Contacts are more durable and reliable, as sleeves are prone to loosen up and result in high resistance connections.

      - ***************************************************************************************

RECEPTACLES, INDUSTRIAL HEAVY DUTY

For equipment furnished with cords and attachment plugs configured to the current edition of <<NEMA WD 6>>, provide the corresponding receptacles. Provide receptacles that meet the performance and design requirements of <<UL 498>>. For equipment not furnished with cords and attachment plugs conforming to <<NEMA WD 6>>, provide receptacles and matching plugs as specified below.

For 20, 30, 60, and 100 ampere heavy duty receptacles located in dry, damp, or wet locations provide butt-contact or pin-and-sleeve type receptacles that are color coded and uniquely configured to the particular circuit voltage and current rating.

Butt-contact or Pin and sleeve receptacles shall be NRTL listed to << UL 2682; or  UL 1682>>

      - ***************************************************************************************

      - The following paragraph is a designer choice.  Select if back boxes are required.

      - ***************************************************************************************

Provide a back box suitable for each particular receptacle device and installation location.

Where indicated on the Drawings provide 20, 30, 60, and 100 ampere butt-contact or pin and sleeve receptacles with safety interlocks that will prevent making or breaking the receptacle connection under load.

      - ***************************************************************************************

      - The following paragraph is a designer choice.  Select if matching plugs are required.

      - ***************************************************************************************

For each receptacle provide a matching plug.

Manufacturer:

Pass & Seymour “IEC 309 Industrial Products”

Meltric “switch-rated” plugs and receptacles

RECEPTACLES IN HAZARDOUS (CLASSIFIED) LOCATIONS

Provide receptacles for hazardous locations, as indicated on the drawings.

PENDANT/CORD CONNECTOR DEVICES

Provide matching, locking type, plug receptacle body connector, NEMA L5-20P and L5-20R, heavy-duty grade for pendant cords as indicated on the Drawings.

Provide connector bodies fabricated from nylon or polycarbonate with screw-open cable-gripping jaws and provision for attaching an external cable grip.

Provide external cable grips of the woven wire mesh type made of high-strength galvanized-steel wire strands, matched to cable diameter and with attachment provision designed for the corresponding connector.

      - ***************************************************************************************

      - Select type below to match Project requirements. Refer to LANL ESM Chapter 7 - Electrical, Section D5020 for guidance.  SOOW is the most common, as it can be used outdoors.  SO can only be used indoors, as it does not have a W in the type designation.  Refer to NFPA 70 Table 400.4 for a description of all the flexible cable types.

      - SO** is 600 volt rated

      - SJ** is 300 volt rated

      - ***************************************************************************************

Cord shall be << 600; or  300>> volt insulated, stranded copper conductors, type << SOOW;  SO;  SOO;  SEO;  STO;  SJO;  SJOO;  SJEO;  SJTO;  G; or  W>>.  Equipment Grounding Conductor, not smaller than that required by <<NFPA 70>>, shall have green—or green with yellow stripes—insulation.

CORDS FOR EQUIPMENT CONNECTION

Provide flexible cords and attachment plugs, or manufactured cordsets (with molded plugs), that match voltage and current ratings and number of conductors to requirements of the equipment being connected.

        - ******************************************************************************

        - Select type below to match project requirements. Refer to LANL ESM Chapter 7 - Electrical, Section D5020 for guidance.

        - ******************************************************************************

Cord shall be << 600; or  300>> volt insulated, stranded copper conductors,  type << SOOW;  SO;  SOO;  SEO;  STO;  SJO;  SJOO;  SJEO;  SJTO;  G; or  W>>​.  Equipment Grounding Conductor, not smaller than that required by <<NFPA 70>>,  shall have green—or green with yellow stripes—insulation.

Attachment Plug shall be male configuration with nylon or polycarbonate body and integral cable-clamping jaws. Match to cord and to receptacle type intended for connection.

GENERAL USE SNAP SWITCHES

Provide single pole, double pole, three-way, four-way, and illuminated handle snap switches as indicated on the Drawings.

Switches shall be rated 20 amperes, 120-277 volts AC, back and side wired, screw pressure terminal, quiet type AC switch with yoke grounding screw.  Back-stab terminations are not acceptable.  Switches shall meet the performance and design requirements of <<UL 20>>​.

Catalog numbers in this section do not indicate device color; see Article << 2.14; or  _______>> Finishes below.

Manufacturer: Hubbell “HBL1220” series.

GENERAL USE SNAP SWITCHES IN HAZARDOUS (CLASSIFIED) LOCATIONS

Provide snap switches for hazardous locations that comply with <<UL 894>>

Switch shall be rated 20 ampere, 120-277 volt AC, and shall meet the performance and design requirements of  <<UL 20>>.

Manufacturer: Appleton “EDS”.

WALLBOX DIMMING CONTROLS

Provide wallbox-mounted dimming control units that meet the requirements of <<UL 1472>>. NRTL listing shall be specific to the type of load to be controlled—e.g., fluorescent, LED, HID, incandescent.

Each dimming control shall include a solid-state dimmer, on-off switch, audible noise filter, and electromagnetic noise filter.

Dimmer wattage rating shall exceed connected load by 30 percent minimum, unless otherwise indicated on the Drawings.

Dimmer control shall provide full-range, continuously adjustable light output. Dimmer control may be by vertical slider, toggle, or rotary knob.

Dimmer control shall include voltage compensation to stabilize light output with varying AC line voltage.

Dimmer switch shall be a mechanical air-gap switch or relay that opens at the dimmer minimum setting, with single-pole or 3-way operation as required to control the lighting in each space.  Dimmer controls used in three-way applications shall provide for the full range of control at each location, regardless of the setting of the other dimmer switch.

Energized parts shall be behind a screw-secured cover. Removal of a snap-on cover shall not expose any energized parts to finger contact.

Provide wall box dimmers as indicated on the Drawings. Equip dimmers with electromagnetic filter to eliminate noise, RF and TV interference.

Manufacturer: Lutron “Nova”

      - ***************************************************************************************

      - The following paragraph is a designer-choice, based on if fluorescent lamp dimmers are part of the project.

      - ***************************************************************************************

Provide fluorescent lamp dimmers for use with electronic ballasts specified in Section ​<< 26 5100 - Interior Lighting>>​.

Manufacturer: Lutron “Nova”.

Provide LED rated  dimmers for << direct control; or  0–10 VDC control>> of LED luminaires.

WALL PLATES

For flush mounted interior receptacles and wall switches, provide 0.032 inch thick (minimum) brushed 302/304 alloy stainless steel smooth wall plates that meet the requirements of Federal Specification WP-455A.

Manufacturer: Hubbell “S” series.

For surface mounted interior receptacles and switches, furnish galvanized steel 4 inch square raised surface covers. Receptacles installed in raised covers shall be secured by more than one screw.

Manufacturer: RACO “800” series.

For GFCI receptacles in damp locations provide weatherproof, cast aluminum, hinged, self-closing device covers.

Manufacturer: Hubbell “WP26” or “WPFS26”.

For GFCI receptacles in wet locations provide cast aluminum, hinged, “extra duty” self-closing device covers that are weatherproof whether or not the attachment plug cap is inserted.

Manufacturer: Hubbell “WP826” or “WP826H”.

Provide single, multi-gang, and combination type wall plates that mate and match with corresponding wiring devices.

Use metal plate-securing screws to match plate finish.

      - ***************************************************************************************

      - Use Section << 26 0533 - Raceways and Boxes for Electrical Systems>>, where other than simple multi-outlet assemblies are required.

      - ***************************************************************************************

MULTIOUTLET  (RECEPTACLE) ASSEMBLY

Furnish multioutlet assembly that meets the requirements of <<UL 5>>.

Components of assemblies shall be designed to be used together to provide a complete matching assembly of raceways and receptacles.

      - ***************************************************************************************

      - Select from the following three paragraphs to match Project requirements.  Standard stocked finish should be used in utilitarian spaces or where the raceway will be field painted.  Grey should be used where it will match or accent architectural finishes.  Stainless steel should be used only in laboratory spaces where there is the possibility of corrosion.

      - ***************************************************************************************

Furnish multioutlet assembly surface metal raceway fabricated from cold rolled galvanized steel and coated with standard stocked baked enamel finish.

      - *** OR ***

Furnish multioutlet assembly surface metal raceway fabricated from cold rolled galvanized steel and coated with a gray baked enamel finish.

      - *** OR ***

Furnish multioutlet assembly surface metal raceway fabricated from Type 304 stainless steel.

Raceway shall be of a two piece design with a metal base and a snap on metal cover.

Nominal dimensions of the assembled raceway shall be 1-1/4 inches wide by 3/4 inch high.

Furnish fittings required for a complete installation.

      - ***************************************************************************************

      - In the following paragraph, select how far apart the receptacles are in the multioutlet assembly.

      - ***************************************************************************************

Provide multioutlet assembly with pre-wired single NEMA 5-15R receptacles spaced << 6;  9;  12; or  18>> inches on center and wired alternately to 2 circuits with three 12 AWG THHN insulated conductors and a green—or green with yellow stripes—THHN-insulated, 12 AWG equipment grounding conductor.

      - ***************************************************************************************

      - Use the following paragraphs to match Project requirements for isolated ground power systems.  Isolated ground systems may only be used with the permission of the LANL ESM Electrical POC.

      - ***************************************************************************************

Provide isolated ground multioutlet assembly with pre-wired single NEMA 5-15R isolated ground receptacles spaced << 9;  12; or  18>> inches on center and connected to 1 circuit with two 12 AWG THHN insulated conductors and a green, or green with yellow stripes, THHN insulated 12 AWG equipment grounding conductor.

Manufacturer: Wiremold “Plugmold 2000”. Wiremold “Plugmold 6000” when the Wiremold also contains data circuits.

      - ***************************************************************************************

      - In many cases the lighting control system described in the Article Occupancy-Sensing Lighting/Receptable Control System will be necessary due to the complex control system required by ANSI/ASHRAE/IES Standard 90.1. This Article is automatically activated when the associated paragraph is activated in Section Includes.

      - ***************************************************************************************

OCCUPANCY-SENSING LIGHT controls

For each private office with less than 400 square feet area, provide a << 120 volt; or  277 volt>>, passive infrared automatic occupancy-sensing wall switch with 180 degree coverage, built-in light level sensor, adjustable time delay, adjustable sensitivity, and a switching technology that is suitable for electronic ballast inrush currents. Device shall have dual manual buttons and dual relays for user-controlled dual-level lighting switching. Light level sensor shall hold off the second relay when adequate daylighting is present in the office. Relay contacts shall be rated for at least 1200 watts ballast load at << 120; or  277>> volts.

Manufacturer: WattStopper “PW-200-U.”

For each private office with greater than 400 square feet area, provide a ceiling-mount combination passive-infrared/ultrasonic automatic sensor with built-in light level sensor, adjustable time delay, and adjustable sensitivity. Provide universal voltage power pack to derive operating voltage for sensor and to switch 20 amperes of ballast-type lighting load.<<  Power pack shall be suitable for use in environmental air spaces.; or  None - N/A>> Where indicated on the Drawings provide auxiliary relay pack for daylighting control.

Manufacturer: WattStopper “DT-300-U” with “BZ-U” series power pack.

For open office and laboratory areas provide one ceiling mount ultrasonic sensor per 900 square feet, or fraction thereof. Provide universal voltage power pack to derive operating voltage for sensor and to switch 20 amperes of ballast-type lighting load.<<  Power pack shall be suitable for use in environmental air spaces.; or  None - N/A>>

Manufacturer: WattStopper “WT-2205” with “BZ-U” series power pack.

For each conference room with less than 400 square feet area, provide a << 120 ; or  277 >>volt, passive infrared occupancy-sensing wall switch with 180 degree coverage, built-in light level sensor, adjustable time delay, adjustable sensitivity, and a switching technology that is suitable for electronic ballast inrush currents. Device shall have dual manual buttons and dual relays for user-controlled dual-level lighting switching. Relay contacts shall be rated for at least 1200 watts ballast load at << 120; or  277>> volts.

Manufacturer: WattStopper “PW-200-U.”

For each conference room with greater than 400 square feet area provide one ceiling-mount combination passive-infrared/ultrasonic automatic sensor per 900 square feet or fraction thereof to control the general lighting. Provide sensor having adjustable time delay and adjustable sensitivity. Provide universal voltage power pack to derive operating voltage for sensor and to switch 20 amperes of ballast-type lighting load.<<  Power pack shall be suitable for use in environmental air spaces.; or  None - N/A>>

Manufacturer: WattStopper “DT-305-U” with “BZ-U” series power pack.

For each computer room provide one ceiling-mount combination passive-infrared/ultrasonic automatic sensor per 1000 square feet or fraction thereof. Provide with adjustable time delay and adjustable sensitivity. Provide universal voltage power pack to derive operating voltage for sensor and to switch 20 amperes of ballast-type lighting load.<<  Power pack shall be suitable for use in environmental air spaces.; or  None - N/A>>

Manufacturer: WattStopper “DT-305-U” with “BZ-U” series power pack.

For each break room, file room, copy machine room, or utility room provide a ceiling-mount combination passive-infrared/ultrasonic automatic sensor with adjustable time delay and adjustable sensitivity. Provide universal voltage power pack to derive operating voltage for sensor and to switch 20 amperes of ballast-type lighting load. << Power pack shall be suitable for use in environmental air spaces.; or  None - N/A>>

Manufacturer: WattStopper “DT-305-U” with “BZ-U” series power pack.

For each restroom provide a ceiling mount ultrasonic sensor. Sensor shall have isolated relay contacts for interlocking with HVAC system controls. Provide universal voltage power pack to derive operating voltage for sensor and to switch 20 amperes of ballast-type lighting load.<<  Power pack shall be suitable for use in environmental air spaces.; or  None - N/A>>

Manufacturer: WattStopper “WT-1100” with “BZ-U” series power pack.

For each corridor provide one ceiling mount ultrasonic sensor for each 90 ft or fraction thereof. Provide universal voltage power pack to derive operating voltage for sensor and to switch 20 amperes of ballast-type lighting load. <<  Power pack shall be suitable for use in environmental air spaces.; or  None - N/A>>

Manufacturer: WattStopper “WT-2255” with “BZ-U” series power pack.

For each stairwell by each door provide one ceiling mount ultrasonic sensor. Provide universal voltage power pack to derive operating voltage for up to 3 sensors and with Form C normally open and normally closed contacts configured to switch 3 amperes of ballast-type lighting load in a fail-on configuration.

Manufacturer: WattStopper “WT-600” with “A277C-P” 277 V or “A120C-P” 120 V series power pack.

Catalog numbers in this section do not indicate device color; see Article << 2.14; or  _______>>​ Finishes below.

      - ***************************************************************************************

      - In many cases the lighting control system described in this article will be necessary due to the complex control system required by ASHRAE 90.1.

      - ***************************************************************************************

OCCUPANCY-SENSING LIGHTING/RECEPTACLE CONTROL SYSTEMS

For each room, except mechanical or electrical rooms, provide an integrated digital occupancy-sensing lighting/receptacle control system as described below and as indicated on the Drawings.

The occupancy-sensing lighting/receptacle control systems shall provide the lighting and receptacle control functions required by <<ASHRAE 90.1>>.

Each system shall consist of components arranged in a free topology local network and interconnected with low-voltage digital communications cables. System components shall include but not be limited to the following, as required to provide the required control functions:

Occupancy sensor(s),

Daylighting sensor(s) for spaces with windows or skylights,

Wall-mounted manual control(s),

Lighting circuit controller(s),

Receptacle circuit controller(s) for private offices, open offices, and computer classrooms,

Interconnecting cables,

Configuration and management tools.

Occupancy sensor(s) shall be suitable for the characteristics of the particular space. Set points for sensitivity, time-out, and other parameters shall be adjustable from the floor using the configuration and management tool described below. The following are minimum requirements for sensor technology and density:

For each private office or conference room with less than 400 square feet area, provide a corner or ceiling mounted passive infrared occupancy sensor.

For each private office with greater than 400 but less than 1000 square feet area, provide a corner or ceiling mounted combination passive-infrared/ultrasonic occupancy sensor.

For open office and laboratory areas, provide one ceiling mount ultrasonic occupancy sensor for each 900 square feet or fraction thereof.

For each conference room greater than 400 square feet, provide one ceiling mounted combination passive-infrared/ultrasonic occupancy sensor for each 900 square feet or fraction thereof.

For each computer room, provide one ceiling mounted combination passive-infrared/ultrasonic occupancy sensor for 1000 square feet or fraction thereof.

For each break room, file room, or copy machine room, provide a ceiling mounted combination passive-infrared/ultrasonic occupancy sensor.

For each restroom, provide a ceiling-mounted ultrasonic occupancy sensor.

For each corridor, provide one ceiling mount ultrasonic sensor for each 90 ft or fraction thereof.

Provide ceiling-mounted daylighting sensor(s) for each space with skylights or with side-lighting having an effective aperture of 10 percent or more.  Provide:

Closed-loop photosensors that measure the ambient light level in order to automatically switch or dim one zone of lighting to maintain desired illuminance in the zone.

Set points and other parameters adjustable remotely using the configuration and management tool described below.

Provide wall-mounted manual controls as required to accomplish the following:

Multi-level lighting control as described in this Section.

Dimming as indicated on the Drawings.

Multi-scene control as indicated on the Drawings.

Provide lighting circuit controllers with characteristics listed below to interface the digital occupancy-sensing lighting control system with the line-voltage room lighting circuits:

Input/output voltage: << 120; or  277>> V, 60Hz

20 A combined load per controller.

One, two, or three output relays as required for room lighting control configuration.

Where dimming is indicated on the Drawings, 0–10 Vdc dimmer control signal.

Class 2 power supply for local network.

Zero-crossing circuitry for each relay for reliability and increased product life.

        - ******************************************************************************

        - The following subparagraph is a designer-choice and applies if the components are in an environmental air space.

        - ******************************************************************************

Listed according to <<UL 2043>>.

For private offices, open offices, and computer classrooms:  Provide receptacle circuit controllers with characteristics listed below to interface the digital occupancy-sensing lighting control system with the 120 V general power and computer power receptacle circuits as required by <<ASHRAE 90.1>>, as follows:

Input/output voltage: 120 VAC, 60Hz.

20 A load.

Class 2 power supply for local network.

Zero-crossing circuitry for relay, for reliability and increased product life.

        - ******************************************************************************

        - The following subparagraph is a designer-choice and applies if the components are in an environmental air space.

        - ******************************************************************************

Listed according to <<UL 2043>>.

Provide a network bridge for each local network (room or corridor segment) to enable all of the local networks to be aggregated into a larger system, which, in turn, can be remotely managed from the building automation system (BAS) using the BACnet communications protocol. The network bridge may be integral to the lighting circuit controller described above.

Provide cables to interconnect components of the digital occupancy-sensing lighting control system. Requirements:

Cat << 6;  6a;  7;  8; or  _______>>​​ cables with 8P8C connectors.

Plenum-rated.

Couplers and splitters as necessary to complete interconnections.

Provide a configuration and management tool for each installation to:

Read, store, and modify configuration of occupancy and daylighting sensors.

Copy sensor settings from one room or installation to another.

Use setup and calibration data to prepare LEED documentation.

Monitor communications within a local network for troubleshooting purposes.

Manufacturer: Watt Stopper “DLM”

FINISHES

Wiring device catalog numbers do not designate device color. Provide devices with colors as follows:

Wiring devices connected to normal power system: Ivory or other device color as selected by Architect or Interior Designer, unless otherwise indicated or required by <<NFPA 70>>​ (NEC).

Wiring devices connected to isolated ground power system: Orange triangle on ivory or other device color as selected by Architect or Interior Designer.

Wiring devices connected to emergency or standby power system: Red.

SPD devices: Surge symbol on ivory or other device color as selected by Architect or Interior Designer.

For renovation or expansion of existing facilities, provide devices and plates to match existing, remaining devices and plates.

PART 3 - EXECUTION

PREPARATION

Verify outlet boxes are installed at proper locations and heights, as shown on drawings.

Verify that outlet boxes in walls or ceilings are positioned in accordance with  <<NFPA 70>>, Section 314.20.

Verify that outlet boxes for GFCI receptacles are in locations that will be readily accessible after equipment is in place.

Verify wall openings are neatly cut, and will be completely covered by wall plates.

Verify branch circuit wiring installation is completed, tested, and ready for connection to wiring devices.

Clean debris from outlet/device boxes before installing devices.

INSTALLATION

Install products following manufacturer's instructions. Have the manufacturer’s installation instructions available at the construction site.

Install devices plumb, level, and secure.

Except as otherwise indicated on the Drawings, mount devices flush, with long dimension vertical, and grounding point of receptacles on top. Group adjacent switches and receptacles under single, multi-gang wall plates.

When drawings call for horizontally mounted receptacles, mount with neutral on top.

Cover devices and assemblies during painting.

Install wall plates on switch, receptacle, and blank outlets after painting is complete.

Install galvanized steel plates on outlet boxes and junction boxes in unfinished areas, above accessible ceilings, and on surface-mounted outlets.

Install Class 2 wiring for occupancy sensing lighting/receptacle control system in accordance with <<NFPA 70>>,  Article 725.

Install a grounded conductor (neutral) to each switch/controller wall box.

Connect the designated neutral terminal/wire on an electronic lighting control device to the grounded (neutral) conductor for the controlled circuit. Do not use the equipment grounding conductor in place of the grounded conductor.

      - ***************************************************************************************

      - The following articles: Dual-Level Lighting Control, Stairwell Lighting Control, and Automatic Receptacle Control, are designer-choice based on project-specific requirements.

      - ***************************************************************************************

DUAL-LEVEL LIGHTING CONTROL

Provide dual-level lighting control or dimming control in spaces 100 square feet and larger, except the following where only full ON-OFF control is required:

Public corridors

Primary building entrances and lobbies

Restrooms

Mechanical, electrical, and telecommunications equipment rooms

Storage rooms

Spaces with only one luminaire with rated input power less than 100 W.

Spaces with an <<ASHRAE 90.1>> lighting power allowance of less than 0.6 W/sq. ft

Spaces indicated on the Drawings as requiring 24-hour operation

Coordinate manual controls with automatic controls so the manual control can reduce the lighting load by at least 50 percent in a reasonably uniform lighting pattern.

Coordinate multi-level lighting controls with daylighting apertures, such as windows.

Coordinate multi-level-lighting controls with luminaire ballasts specified in Section << 26 5100 - Interior Lighting>>.

STAIRWELL LIGHTING CONTROL

Install ultrasonic occupancy sensors and control relays and circuit luminaires to reduce stairwell lighting power by 50 percent within 30 minutes of all occupants leaving the controlled zone as required by <<ASHRAE 90.1>>.

Mount an occupancy sensor near each stair door. Locate sensors on the side wall of the stairwell above door height to detect opening the stairwell doors.

Connect occupancy sensor auxiliary contacts and control relay contacts in a “fail on” configuration.

AUTOMATIC RECEPTACLE CONTROL – For new construction only

In private offices, open offices, and computer classrooms connect 125 V receptacles to receptacle circuit controllers so not less than 50 percent of the receptacles will be switched off by occupancy sensing controls within 30 minutes of all occupants leaving the space, as required by <<ASHRAE 90.1>>.  Controlled receptacles must be marked per <<NFPA 70>>, 406.3(F).

Receptacle control is not required for equipment indicated on the Drawings as requiring 24 hour operation.

Receptacle control is not required in spaces indicated on the Drawings where an automatic shutoff would endanger the safety of the room or building occupants.

Connect general-purpose receptacles to provide a uniform distribution of controlled receptacles.

Split-wire vertically mounted duplex receptacles so the top receptacle will be controlled and the bottom receptacle will be always on.

Split-wire horizontally mounted duplex receptacles so the left receptacle will be controlled and the right receptacle will be always on.

CONNECTION TO EFFECTIVE GROUND-FAULT CURRENT PATH

Connect wiring device grounding terminal to branch circuit equipment grounding conductor.

IDENTIFICATION

Identify wiring devices with circuit number as required in Section << 26 0553 - Identification for Electrical Systems>>.

FIELD QUALITY CONTROL

Inspect each wiring device for defects before installing.

Operate each operable device at least six times with circuit energized; verify proper operation.

Verify 15 and 20 ampere receptacles for proper polarity and ground continuity using latest device that impresses a momentary current of at least 10 amperes on the branch circuit conductors and equipment grounding conductor path.

Test ground-fault circuit interrupter operation by using the integral test and reset functions.  Do not use an external tester for this purpose.

Replace damaged or defective wiring devices.

CLEANING AND ADJUSTING

Clean devices and wall plates. Replace stained or improperly painted wall plates or devices.

Adjust devices and wall plates to be flush and level.

      - ***************************************************************************************

      - The following paragraph is a designer-choice and applies to occupancy sensing lighting control devices.

      - ***************************************************************************************

Adjust time-out controls for each occupancy sensing light switches to the following settings:

Any controller that controls fluorescent luminaires: not less than 30 minutes.

Classrooms, private offices, open offices, laboratories, and restrooms: longest time out setting, but not more than 30 minutes.

Break rooms, storage rooms, and copy machine rooms: 5-minute time-out setting.

Conference rooms: 10-minute time-out setting.

Corridors and lobbies: 15-minute time-out setting.

      - ***************************************************************************************

      - The following paragraph is a designer-choice and applies to occupancy sensing lighting control devices.

      - ***************************************************************************************

Adjust ambient light sensor in occupancy sensors to hold off or reduce the electric lighting when daylighting exceeds 80 percent of the design illuminance at the work area. For example, in an office with a design illuminance of 50 footcandles, the ambient light sensor should keep the lights off as long as the daylighting exceeds 40 footcandles.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 26 2726, REV. 7, DATED APRIL 15, 2026.