Section 26 5600 
Exterior Lighting

  - ************************************************************************************************************

    - LANL MASTER SPECIFICATION Section

Rev. 7 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Electrical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality Sections.

      - ==========================================================

      - Seismic: In order to edit this section for job-specific seismic requirements, refer to author notes that say/begin with “Seismic,” and the Seismic Specification Guide for Nonstructural Components: Electrical Components (posted on LANL specs webpage) for guidance on properly editing this Section.

  - ************************************************************************************************************

PART 1 - General

SECTION INCLUDES

Exterior luminaires - general.

      - ***************************************************************************************

      - Retain the following paragraphs that apply to the project.  "Fuses and fuse holders" are only used for pole mounted luminaires.  Check with manufacturer to see if they are required.

      - ***************************************************************************************

LED luminaires.

High pressure sodium lamps.

​High pressure sodium lamp ballasts.

Poles and accessories.

Drill-in lighting pole foundations.

Lighting control equipment.

Fuses and fuse holders.

Related requirements

Section << 01 2500 - Substitution Procedures>>

Section << 01 3300 - Submittal Procedures>>

Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>​

Section << 03 3001 - Reinforced Concrete>>​

Section ​​<< 26 0519 - Low Voltage Electrical Power Conductors and Cables>>​​​

Section ​<< 26 0526 - Grounding and Bonding for Electrical Systems>>​

Section ​<< 26 0533 - Raceways and Boxes for Electrical Systems>>​​

Section << 26 0548.16 - Seismic Controls for Electrical Systems>>​

reference standards

47 CFR 15 - Radio Frequency Devices.

AAMA 611 - Specification for Anodized Architectural Aluminum.

AAMA 2605 - Voluntary Specification, Performance Requirements and Test Procedures for Superior Performing Organic Coatings on Aluminum Extrusions and Panels (with Coil Coating Appendix).

AASHTO LTS - Standard Specifications for Structural Supports for Highway Signs, Luminaires, and Traffic Signals.

ANSI C136.10 - American National Standard for Roadway and Area Lighting Equipment - Locking-Type Photocontrol Devices and Mating Receptacles - Physical and Electrical Interchangeability and Testing.

ANSI C136.13 - American National Standard for Roadway and Area Lighting Equipment—Metal Brackets for Wood Poles.

ANSI O5.1 - Wood Poles: Specifications and Dimensions.

ASCE 7 - Minimum Design Loads and Associated Criteria for Buildings and Other Structures.

ASTM A29/A29M - Standard Specification for General Requirements for Steel Bars, Carbon and Alloy, Hot-Wrought.

ASTM A36/A36M - Standard Specification for Carbon Structural Steel.

ASTM A53/A53M - Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless.

ASTM A123/A123M - Standard Specification for Zinc (Hot-Dip Galvanized) Coatings on Iron and Steel Products.

ASTM A153/A153M - Standard Specification for Zinc Coating (Hot-Dip) on Iron and Steel Hardware.

ASTM A194/A194M - Standard Specification for Carbon Steel, Alloy Steel, and Stainless Steel Nuts for Bolts for High Pressure or High Temperature Service, or Both.

ASTM A252/A252M - Standard Specification for Welded and Seamless Steel Pipe Piles.

ASTM A575 - Standard Specification for Steel Bars, Carbon, Merchant Quality, M-Grades.

ASTM B108/B108M - Standard Specification for Aluminum-Alloy Permanent Mold Castings.

AWPA U1 - Use Category System:  User Specification for Treated Wood.

ICC (IBC) - International Building Code.

IEC 60529 - Degrees of Protection Provided by Enclosures (IP Code).

IEEE C62.41.2 - IEEE Recommended Practice on Characterization of Surges in Low-Voltage (1000 V and less) AC Power Circuits.

IES LM-79 - Approved Method:  Optical and Electrical Measurements of Solid-State Lighting Products.

IES LM-80 - Approved Method: Measuring Maintenance of Light Output Characteristics of Solid-State Light Sources.

IESNA (LH) - Lighting Handbook..

National Energy Policy Act - National Energy Policy Act.

NECA/IESNA 501 - Standard for Installing Exterior Lighting Systems.

NEMA 1 - NEMA Ratings for Enclosures.

NEMA C78.42 - American National Standard for Electric Lamps—High-Pressure Sodium (HPS) Lamps.

NEMA C82.4 - Lamp Ballasts—Ballasts for High-Intensity-Discharge and Low-Pressure Sodium Lamps.

NEMA C136.21 - American National Standard for Roadway and Area Lighting Equipment—Vertical Tenons Used with Post Top–Mounted Luminaires.

NEMA ICS 2 - Industrial Control and Systems Controllers, Contactors and Overload Relays Rated 600 Volts.

New Mexico Night Sky Protection Act - New Mexico Night Sky Protection Act.

NFPA 70 - National Electrical Code.

SAE J429 - Mechanical and Material Requirements for Externally Threaded Fasteners.

UL 508A - Industrial Control Panels.

UL 773 - Plug-in, Locking Type Photocontrols for Use with Area Lighting.

UL 773A - Nonindustrial Photoelectric Switches for Lighting Control.

UL 1029 - High-Intensity-Discharge Lamp Ballasts.

UL 1449 - Standard for Surge Protective Devices.

UL 1598 - Luminaires.

dEFINITIONS

For definitions and acronyms, refer to COE Glossary of Terms.

Unless otherwise specified or indicated, terms used in this Section are as defined in <<NFPA 70>> (NEC) or <<IESNA (LH)>>.

      - ***************************************************************************************

      - Retain the following article if submittals are required.  Retain the appropriate subparagraphs.  If specific model numbers are specified, and all the salient information is known, submittals are unnecessary.

      - ***************************************************************************************

ACTION Submittals

Submit the following in accordance with Section << 01 3300 - Submittal Procedures>>:

Catalog Data: Submit catalog data describing poles, luminaires, efficacy, lamps, ballasts, and pole and luminaire finishes. Include data substantiating that materials comply with specified requirements. Arrange data for luminaires in the order of luminaire designation.

Performance Curves/Data: Submit certified photometric data for each type of luminaire.

      - ***************************************************************************************

      - Retain the following article when spare/extra materials are required for project. Check with customer to see if there is a place to store these spare/extra materials. If not, the customer may not want the spare/extra materials and this article can be omitted.

      - ***************************************************************************************

EXTRA MATERIALS

Furnish the following extra materials matching products installed. Package with protective covering for storage and identify with labels describing contents.

LED Luminaires: 5 percent of quantity of LED luminaires of each type, but no fewer than two of each type.

HID Lamps: 5 percent of quantity of high intensity discharge (HID) lamps of each type, but no fewer than two lamps of each type.

Ballasts: 1 percent of quantity of ballasts of each type, but not less than one of each type.

Lenses, Diffusers, Covers, Globes, and Guards: 1 percent of quantity of each type, but not less than one of each type.

Photoelectric Relays: 5 percent of quantity of photoelectric relays of each type, but not less than two of each type.

Fuses: 5 percent of quantity of fuse of each type, but not less than two of each type.

QUALITY ASSURANCE

Comply with the following codes and standards, as appropriate for the type of luminaire:

<<NFPA 70>>, for installation requirements

<<AASHTO LTS>>-5.

<<ICC (IBC)>>.

<<ASCE 7>>.

<<New Mexico Night Sky Protection Act>>.

<<National Energy Policy Act>> requirements for lighting products.

Provide luminaires listed and labeled by a nationally recognized testing laboratory (NRTL).

Use manufacturers that are experienced in manufacturing poles, luminaires, lamps and ballasts similar to those indicated for this Project and have a record of successful in-service performance.

DELIVERY, STORAGE, AND HANDLING

Receive, inspect, handle, and store products according to the manufacturer’s written instructions and <<NECA/IESNA 501>>.

PART 2 - PRODUCTS

    - **********************************************************************************************

      - Seismic: If Project Spec includes Section ​<< 26 0548.16 - Seismic Controls for Electrical Systems>>​, and if mounting and/or anchorage devices are to be used that differ from those specified in Section ​<< 26 0548.16 - Seismic Controls for Electrical Systems>>​ , they must be described herein (in PART 2). If this applies, use the same terminology for these devices in PART 3 in order to identify the type of devices required for each application.

      - Retain the following article if substitutions are allowed.

    - **********************************************************************************************

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section << 01 2500 - Substitution Procedures>>.

​PERFORMANCE REQUIREMENTS

Elevation: 7500 feet above sea level.

<<ICC (IBC)>> and <<ASCE 7>> design wind conditions:

Exposure Category: C.

Basic Wind Speed: << _______>> mph.

Importance Factor: 1.00.

Ambient temperatures, degrees C (degrees F):

Annual averages: 2.1 (35.8) minimum, 15.6 (60.0) maximum, 8.8 (47.9) average.

Annual nighttime average: 5.4 (41.7).

Annual extremes: -15.0 (5.0) minimum, 31.7 (89.0) maximum.

Annual warmest day 24-hour average: 20.7 (69.3).

Annual warmest day nighttime average: 16.4 (61.6).

Maximum solar heat gain: 110 W/sq. ft.

Lightning flash density: three flashes to ground per square km per year.

      - ***************************************************************************************

      - Seismic: Retain the paragraphs in the following article based on project requirements when luminaires are subject to seismic design. For luminaires that are either subject to positional retention only, or for those that are DSS, if there are too many systems/components to list here, then list them in an appendix to this section, and then merely refer to that appendix in the paragraph. Omit this article when luminaires are exempt from seismic design.

      - ***************************************************************************************

SEismic Performance requirements

The luminaires shall remain in place without separation of any parts when subjected to the design basis earthquake

Per Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>.

        - *** OR ***

As represented by the seismic forces derived from the criteria indicated ​<< on the Drawings; or  in Section 26 0548.16 - Seismic Controls for Electrical Systems>>​.

The luminaires are a Designated Seismic Systems and, as such, it shall remain in place and be fully operational following the design basis earthquake

Per Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>.

        - *** OR ***

As represented by the seismic forces derived from the criteria indicated << on the Drawings; or  in Section 26 0548.16 - Seismic Controls for Electrical Systems>>.

EXTERIOR Luminaires - General

Furnish exterior luminaires that comply with requirements specified in this Section and in the luminaire schedule on the Drawings.

Luminaires shall be NRTL-listed as conforming to <<UL 1598>>​.

Photometric characteristics shall be based on IESNA approved methods for photometric measurements performed by a recognized photometric laboratory.

Each exterior luminaire with light source exceeding 6400 lumens shall comply with the <<New Mexico Night Sky Protection Act>>. There shall be no light emitted above a horizontal plane through the lowest light-emitting part of the luminaire.

Luminaire housing shall be primarily metal.

Metal parts shall be free from burrs and sharp corners and edges.

Sheet metal components shall be fabricated from corrosion-resistant aluminum, formed and supported to prevent sagging and warping.

Exposed fasteners: Stainless steel.

      - ***************************************************************************************

      - The following paragraphs are designer choices.

      - ***************************************************************************************

Doors and frames shall be smooth operating and free from light leakage under operating conditions.

Relamping shall be possible without the use of special tools.

Doors, frames, lenses and diffusers shall be designed to prevent accidental falling during relamping and when secured in the operating position.

Door: Removable for cleaning or replacing lens.

Luminaire minimum reflecting surface reflectance: As follows unless scheduled otherwise:

White surfaces: 85 percent.

Specular surfaces: 83 percent.

Diffusing specular surfaces: 75 percent.

Provide lenses, diffusers, covers and globes as scheduled on the Drawings fabricated from materials that are UV stabilized to be resistant to yellowing and other changes due to aging or exposure to heat and ultraviolet radiation.

Doors shall have resilient gaskets that are heat-resistant and aging-resistant to seal and cushion lens and refractor.

      - ***************************************************************************************

      - The following article is a designer-choice,  if LED luminaires are used.  This should always be the case.

      - ***************************************************************************************

LED Luminaires

Conform to <<UL 1598>> and to <<UL 8750>>.

Lead and mercury free.

Photometric characteristics: Established using <<IES LM-79>>​.

Ingress protection for optical assembly: IP65 or better in accordance with <<IEC 60529>>​.

Color characteristics as follows in accordance with the New Mexico Night Sky Act:

Color temperature: 2200 to 2700 K.

LED and driver cooling system: Passive and shall resist the buildup of debris.

LED luminaire output after 50,000 hours of operation: Not less than 70 percent of the initial lumen output when determined in accordance with <<IES LM-80>>​.

LED luminaire electrical characteristics:

Supply voltage: 120 V, 208 V, 240 V, 277 V, or 480 V, as indicated on the Drawings.

Total harmonic distortion (current): Not more than 20 percent

Power factor: Not less than 90 percent

RF interference: Meet FCC, <<47 CFR 15>>​​.

Driver input surge protection device: <<UL 1449>> recognized component meeting <<IEEE C62.41.2>>, Category C, High Exposure.

      - ***************************************************************************************

      - Omit the following paragraph if luminaire-mounted photocontrols are not required. Luminaire-mounted photocontrols are typically used for roadway lighting, but not for security, parking, or storage area lighting.

      - ***************************************************************************************

For each luminaire provide a luminaire-mounted locking-type photocontrol receptacle conforming to <<ANSI C136.10>>.

Manufacturers:

BetaLED “BLD”.

Leotek “SLN”.

Kim “Warp 9”.

      - ***************************************************************************************

      - Retain the following article if HPS lamps are used

      - ***************************************************************************************

High Pressure Sodium LAMPS

Comply with <<NEMA C78.42>> and the luminaire schedule on the Drawings.

Manufacturers: General Electric, North American Phillips, Sylvania.

      - ***************************************************************************************

      - Retain the following article if HPS lamp ballasts are used

      - ***************************************************************************************

HIGH Pressure Sodium LAMP BALLASTS

Ballasts with associated capacitors and igniters shall comply with <<UL 1029>> and <<NEMA C82.4>> for lamps specified in this Section and in the luminaire schedule on the Drawings.

Ballasts shall be of the following circuit types:

Lamp rated 150 watts or less: lag type – high reactance autotransformer – high power factor (HX-HPF).

Lamp rated 250 watts or greater: constant wattage autotransformer (CWA).

Core and coil ballasts: Constructed with class H or higher insulation system vacuum-impregnated with a 100-percent-solids-based resin.

Ballast and igniter/starter combination shall reliably start HPS lamp down to -40 C.

Solid-state igniter/starter or accessory shall automatically deactivate if a lamp arc cannot be initiated after 10 to 12 minutes.

Where scheduled on the Drawings, provide HPS ballasts for 150 watt and smaller lamps with an instant re-strike starter that will generate a multiple pulse to re-strike lamp arc after a momentary power interruption.

Solid-state igniter/starter shall have an average life in the pulsing mode of 10,000 hours at the intended ambient temperature. Igniter case temperature not to exceed 90 degrees C.

Manufacturer: To match fixture manufacturer or equivalent.

      - ***************************************************************************************

      - Retain the following article if poles are used.  This is automatically activated when the associated paragraph is activated in Section Includes.

      - ***************************************************************************************

POLES AND ACCESSORIES

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements. This Section contemplates poles 30 ft and taller used for roadway and parking lot lighting; less rigorous requirements would apply to pedestrian-scale poles.

      - ***************************************************************************************

Furnish poles and accessories that comply with requirements specified in this Section and the luminaire schedule on the Drawings.

Pole, base, and anchorage shall carry the luminaires, supports, and appurtenances at the indicated height above grade without deflection or whipping.

Mountings, fastenings and other appurtenances shall be fabricated from corrosion-resistant materials that are compatible with poles and luminaires and will not cause galvanic action at contact points. Mountings shall correctly position luminaires to provide scheduled light distribution.

A reinforced access handhole, minimum 2.5 x 5 inches, shall be located in the wall of each metal pole.

A welded grounding lug, with 1/2 inch hole, shall be accessible through the handhole of each metal pole. Grounding connection shall be designed to prevent electrolysis when used with copper ground wire.

Metal poles shall have anchor type bases and galvanized steel anchor bolts, leveling nuts and bolt covers.

Where poles are indicated as “breakaway” type on the Drawings, each pole shall have a frangible aluminum transformer base that meets the requirements of <<AASHTO LTS>>-5.

Each non-breakaway metal pole shall have a metal base cover that covers the entire base plate and anchorage.

Protect painted, anodized, or brushed pole finishes during shipment and installation. Minimum protection shall consist of spirally wrapping each pole shaft with protective paper secured with tape, and shipping small parts in boxes.

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements; omit if steel poles are not used. Consult structural engineer for appropriate metal gauge; 7-gauge or even 3-gauge poles may be needed for tall poles or special applications.

      - ***************************************************************************************

Steel poles shall be fabricated from tubing having minimum ​​<< 11-gauge;  7-gauge; or  3-gauge>>​​ steel with minimum yield/strength of 48,000 psi.

Poles shall be anchor bolt mounted type.

Poles shall be one-piece construction up to 40 feet in length. Poles over 40 feet in length may be in two or more sections with overlapping joints.

Poles shall be tapered, either round in cross section or polygonal.

Poles shall be welded construction with no bolts, rivets, or other means of fastening except as specifically approved.

Tops of shafts shall be fitted with a round or tapered cover.

Pole markings shall be approximately 3 to 4 feet above grade and shall include manufacturer, year of manufacture, and length.

Provide poles with finish color indicated on the Drawings and conforming to Article FINISHES of this Section. If pole is not galvanized, coat inside of pole with suitable rust-inhibiting finish.

Base covers for steel poles shall be structural-quality, hot-rolled carbon-steel plate having a minimum yield of 36,000 psi. Finish shall be the same as the corresponding poles.

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements; omit the following if aluminum poles are not used. Consult structural engineer for appropriate metal thickness; 0.188-inch or even 0.220-inch wall-thickness poles may be needed for tall poles or special applications.

      - ***************************************************************************************

Aluminum poles shall be fabricated from corrosion resistant aluminum Alloy 6063-T6 or Alloy 6005-T5 for wrought alloys or Alloy 356-T4 for cast alloys.

Poles shall be square or round, tapered or straight as indicated on the Drawings.

Aluminum poles over 30 feet tall shall include factory-installed vibration dampers.

Poles shall be seamless extruded or spun seamless type with minimum ​​<< 0.125 inch;  0.188 inch;  0.220 inch; or  _______>>​​ wall thickness.

Tops of shafts shall be fitted with a round or tapered cover.

Base shall be anchor bolt mounted, made of cast 356-T6 aluminum alloy in accordance with <<ASTM B108/B108M>> and shall be machined to receive the lower end of shaft. Joint between shaft and base shall be welded.

Base cover shall be cast 356-T6 aluminum alloy in accordance with <<ASTM B108/B108M>>.

Hardware, except anchor bolts, shall be either 2024-T4 anodized aluminum alloy or stainless steel.

      - ***************************************************************************************

      - Omit  the following paragraph if wood poles are not used.

      - ***************************************************************************************

Pressure-treated wood poles shall conform to <<ANSI O5.1>>.

Treatment shall conform to <<AWPA U1>> for the wood species used.

Bore, roof and gain poles before treatment.

      - ***************************************************************************************

      - Omit  the following paragraph if steel mast arms are not used.

      - ***************************************************************************************

Steel mast arms shall be fabricated from 2-inch pipe, continuously welded to pole attachment plate and have span and rise as indicated on the Drawings. Provide with same finish as pole.

      - ***************************************************************************************

      - Omit  the paragraph following if aluminum mast arms are not used.

      - ***************************************************************************************

Aluminum mast arms shall be tapered oval tubing, continuously welded to pole attachment plate and have span and rise as indicated on the Drawings. Provide with same finish as pole.

      - ***************************************************************************************

      - Omit  the following paragraph if metal pole brackets are not used.

      - ***************************************************************************************

Metal pole brackets shall be designed to match pole metal and finish. Provide cantilever brackets without underbrace, in the sizes and styles indicated on the Drawings, with straight tubular end section to accommodate the luminaire.

      - ***************************************************************************************

      - Omit  the following paragraph if wood pole brackets are not used.

      - ***************************************************************************************

Wood pole brackets shall conform to <<ANSI C136.13>>.

      - ***************************************************************************************

      - Omit the following paragraph if pole-top tenons are not used.

      - ***************************************************************************************

Pole-top tenons: Conform to <<NEMA C136.21>>, fabricated to support the luminaire indicated, and securely fastened to the pole top.

      - ***************************************************************************************

      - Omit  the following paragraph if drill-in light pole foundations will be used.

      - ***************************************************************************************

Anchor bolts: Steel rod having minimum yield strength of 50,000 psi, with the top 12 inches galvanized per <<ASTM A153/A153M>>.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Holophane Corporation.

Hubbell Lighting, Inc.

Lithonia Lighting.

Millerbernd Manufacturing Company.

Union Metal Corp.

Valmont Industries, Inc.

      - ***************************************************************************************

      - Retain the following article if drill-in lighting pole foundations are used.  This is automatically activated when the associated paragraph is activated in Section Includes.

      - Drill-in lighting pole foundations may be a cost-effective alternative to cast-in-place lighting pole foundations. This Specification contemplates foundations for 30 ft. to 50 ft. poles used for roadway and parking lot lighting; less rigorous requirements would apply to pedestrian scale poles.

      - ***************************************************************************************

Drill-in Lighting Pole foundations

Furnish drill-in lighting pole foundations as indicated on the Drawings.

Drill-in lighting pole foundations for 30 ft., 35 ft., and 40 ft. poles with one or two luminaires shall have the following minimum dimensions:

Base Plate: 15.75 inches square, 1 inch thick, 11 to 17 inch diameter bolt circle, slots for four 1” x 4” carriage bolts.

Shaft: 8 inch diameter, 7 ft. long, 0.25 inch wall thickness, with two 2.5 x 12 inch cable slots with top 12 inches below the base plate.

Helix: 14 inch diameter, 0.38 inch thick, with 3-inch pitch formed by metal die.

Drill-in lighting pole foundations for 45 ft., and 50 ft. poles with one or two luminaires shall have the following minimum dimensions:

Base Plate: 15.75 inches square, 1 inch thick, 13.5 to 17 inch diameter bolt circle, slots for four 1” x 4” carriage bolts.

Shaft: 10 inch diameter, 10 ft. long, with two 2.5 x 12 inch cable slots with top 12 inches below the base plate.

Helix: 16 inch diameter, 0.38 inch thick, with 3-inch pitch formed by metal die.

All material shall comply with the following specifications:

Base Plate: <<ASTM A36/A36M>> structural steel.

Shaft: Steel pipe piles, seamless or straight welded, Grade -2 per <<ASTM A252/A252M>> or steel pipe Type E or S Grade-B per <<ASTM A53/A53M>>.

Helix: <<ASTM A29/A29M>>​ Grade M1010 hot-rolled steel plate or coil.

Pilot point: <<ASTM A575>>​ hot rolled steel bar, 1.25 inch diameter.

Bolts: Carriage bolts, <<SAE J429>> Grade 5, 1-8UNC-2A x 4” long, hot-dip galvanized per <<ASTM A153/A153M>>.

Nuts: Heavy hex per <<ASTM A194/A194M>> Grade 2H or <<ASTM A53/A53M>> Grade DH, meeting the supplementary requirements of <<ASTM A252/A252M>>.

Base plate shall be perpendicular to the shaft axis within 1 degree and the hole centerline shall be concentric to the shaft axis within 0.2 inches.

Pilot point and shaft axes shall be concentric within 0.125 inches and in-line within 2 degrees.

Clean all welds on base plate, helix, and pilot point by hand-grinding and sand-blasting. Hot-dip galvanize foundations per <<ASTM A153/A153M>> after fabrication, welding, and cleaning to a minimum 3-mil coat thickness.

Manufacturer’s identification and date code shall be permanently stamped on the base plate.

Manufacturer: Hubbell Power Systems.

      - ***************************************************************************************

      - Retain the following article if Lighting Control Equipment is a part of the project.  It is automatically activated when the associated paragraph in "Section Includes" is activated.

      - Comply with exterior lighting system control requirements in LANL ESM Chapter 7 - Electrical, Section G4020. The building automation system may be used to good advantage instead of time switches and photocontrols for control of exterior lighting so long as LANL ESM functional requirements are met.

      - ***************************************************************************************

Lighting Control Equipment

Furnish photoelectric relays to control exterior lighting as indicated on the Drawings.

For photoelectric relays mounted on luminaires use products that conform to <<UL 773>>​​, with contacts arranged to fail in the “ON” position. For each luminaire provide a luminaire-mounted locking-type receptacle conforming to <<ANSI C136.10>>.

For photoelectric relays not mounted on luminaires use products conforming to either <<UL 773>> or <<UL 773A>>​​. Provide the photoelectric relays with contacts to switch mechanically-held contactors.

Photoelectric relay contacts shall be factory set to turn exterior lighting “ON” at or below 3 foot-candles and “OFF” at 4 to 10 foot-candles. A time delay shall prevent switching from transient light sources.

Furnish one or more time switches to control exterior lighting as indicated on the Drawings.

Use a mechanical astronomic dial type or an electronic type time switch, arranged to turn “ON” at sunset and turn “OFF” at predetermined time as described in PART 3.

Time switch shall have either an automatically wound spring mechanism or an energy-storage capacitor to maintain accurate time for a minimum of 7 hours following power failure.

Time switch shall have Form C contacts to switch mechanically-held contactors and a manual on-off bypass switch.

Provide time switch with <<UL 508A>>, NEMA 3R housing if installed outdoors or <<NEMA 1>> housing if installed indoors.

Furnish a “hand-off-auto” control switch and enclosure to facilitate testing of the lighting system.

Furnish one or more multi-pole lighting contactors to control exterior lighting as indicated on the Drawings.

Mechanically-held contactors shall conform to <<NEMA ICS 2>>.

Contactors shall have the number of contacts as indicated on the Drawings or as required by the number of circuits to be controlled. Contacts shall have a minimum rating of 30 amperes at 277 volts AC per pole for ballast loads. Contacts shall be field-convertible from normally-open to normally-closed, or shall be Form C.

Use 120 volts AC operating coils, or as shown on drawings.

Provide contactor with <<UL 508A>>, NEMA 3R housing if installed outdoors or <<NEMA 1>> housing if installed indoors.

      - ***************************************************************************************

      - Retain the following article if Fuses and Fuse-Holders are a part of the project.  It is automatically activated when the associated paragraph in "Section Includes" is activated.

      - ***************************************************************************************

Fuses and Fuse holders

Furnish fuse overcurrent protection for each pole-mounted luminaire to isolate faulted ballasts or drivers from the lighting circuit.

Use 600 volt, Class CC, time-delay, current-limiting fuses.

Select fuses rated between 200 percent and 300 percent of the luminaire ballast or driver maximum current.

Manufacturer: Bussman “LP-CC”.

Furnish in-line fuse holders for installation in pole hand hole or transformer base.

Use non-breakaway type fuse holders unless breakaway poles are indicated on the Drawings.

Use breakaway type fuse holders where breakaway poles are indicated on the Drawings.

Load and line terminal sizes and types shall correspond to line and load conductor sizes and quantities.

Both breakaway and non-breakaway fuse holders shall have insulating boots.

Manufacturers: Ferraz Shawmut “FEC” for phase conductor(s), “FEBN” for neutral conductor.

Finishes

Furnish luminaires, poles, and accessories with finishes as scheduled that are resistant to fading, chalking, and other changes due to aging and exposure to heat and ultraviolet light. Acceptable finishes for metals are:

Hot-dipped galvanized steel: <<ASTM A123/A123M>>.

Brushed aluminum.

Anodized aluminum: <<AAMA 611>> Class I.

Powder coated aluminum: Fluorocarbon polymer powder coating per <<AAMA 2605>> over chrome phosphate conversion coated aluminum.

Powder coated steel: Fluorocarbon polymer powder coating per <<AAMA 2605>> over zinc phosphate conversion coated shot-blasted steel.

Reject luminaires, poles, and accessories with finish having runs, streaks, stains, holidays and defects.

Replace luminaires, poles, and accessories showing evidence of yellowing, fading, chalking, and other changes indicating failure during warranty period.

Use stainless steel for exposed hardware.

PART 3 - EXECUTION

    - **********************************************************************************************

      - Seismic: For luminaires that are subject to seismic design, if Project Spec includes Section ​<< 26 0548.16 - Seismic Controls for Electrical Systems>>​, and if requirements associated with installation, testing, and inspection of mounting and/or anchorage devices differ from those requirements in Section ​<< 26 0548.16 - Seismic Controls for Electrical Systems>>​, they must be described herein (in PART 3). Also, if this is applicable, identify special types of seismic-control devices required for each application using the same terminology used for those devices in PART 2.

      - Retain the following is existing work is part of the project.

    - **********************************************************************************************

EXISTING WORK

Disconnect and remove abandoned exterior luminaires as indicated on the Drawings.

Disconnect and remove abandoned luminaire poles and associated foundations as indicated on the Drawings.

Maintain electrical circuit to existing exterior luminaires that are to remain active.

Clean and repair existing exterior luminaires that are to remain or be reinstalled, as a part of the scope of this project.

EXAMINATION

Examine areas, spaces, and surfaces to receive exterior luminaire (s) or poles for compliance with installation tolerances and other conditions affecting performance of the product. Do not proceed with installation until unsatisfactory conditions have been corrected.

INSTALLATION

Install products in accordance with manufacturer's instructions, <<NECA/IESNA 501>>, and approved shop drawings.

Locations of luminaires and poles shown on the Drawings are diagrammatic. Coordinate luminaire locations with building finishes, building structure, paving and striping, utility piping, security fences, and existing trees. Obtain approval for location changes through LANL Subcontract Technical Representative (STR).

Set poles and luminaires plumb, square, level and secure.

Install surface mounted luminaires directly to an outlet box which is supported from structure, or as shown on drawings.

      - ***************************************************************************************

      - The following paragraph is a designer choice that does not apply to LED luminaires.

      - ***************************************************************************************

Install lamps in luminaires in accordance with manufacturer's instructions..

      - ***************************************************************************************

      - Retain the following article if concrete light pole foundations will be used.

      - ***************************************************************************************

CONCRETE FOUNDATIONS

Construct concrete foundations with exterior 4,500 psi concrete and reinforcing conforming to Section << 03 3001 - Reinforced Concrete>>.

Comply with details on the Drawings and manufacturer's recommendations for foundation dimensions, reinforcing, anchor bolts, nuts and washers.

Position power conduits << and ground rod; or  None - N/A>> to terminate within the pole shaft area and a minimum of one inch above the top of the foundation; refer to Section << 26 0533 - Raceways and Boxes for Electrical Systems>>.

Cure concrete foundations for 7 full curing days before erecting poles.

      - ***************************************************************************************

      - "Drill-in lighting pole foundations" are automatically activated when they are activated in Part 1.

      - ***************************************************************************************

Drill-in Lighting Pole foundations

Install drill-in light pole foundations in accordance with the manufacturer’s instructions.

Set foundation plumb with base plate a minimum of 2 inches above finished grade.

Align cable slots with conduit trench.

Position power conduits to terminate within the pole shaft area and a minimum of 1 inch above the top of the foundation; refer to Section << 26 0533 - Raceways and Boxes for Electrical Systems>>​.

POLE ERECTION

Do not erect poles without luminaires, unless luminaire may be damaged during erection.

Use fabric web slings to raise and set poles.

Use leveling nuts or shims to make poles plumb. When leveling nuts are used, set the lower nuts not more than 1 inch from the concrete foundation.

Tighten anchor bolt nuts and other pole hardware to torque recommended by manufacturer.

After pole is leveled, pack non-shrink grout between anchor base and concrete foundation to provide a full bearing surface. Use a short piece of 1/2-inch diameter pipe to make a drain hole through grout; arrange to drain condensation from interior of pole.

Set embedded poles to depth indicated on the Drawings, but not less than 1/6th of pole length below finish grade.

Auger holes large enough to permit the use of tampers throughout the full depth of the hole.

Backfill in 6-inch layers and thoroughly tamp each layer so compaction of backfill is equal to or greater than that of the undisturbed earth.

GROUNDING

Install grounding for exterior lighting in accordance with Section << 26 0526 - Grounding and Bonding for Electrical Systems>>.

      - ***************************************************************************************

      - Retain the following paragraph if a grounding electrode is required.

      - ***************************************************************************************

At metal poles mounted on reinforced concrete foundations, the rebar in the concrete foundation will be the grounding electrode. Attach a 4 AWG copper conductor to the rebar with a NRTL listed connector and leave enough copper extending above the concrete to connect to the grounding lug in the pole.  If there is no concrete foundation, install a 10 foot long, minimum 5/8-inch diameter copper-clad ground rod at each pole, and connect with 6 AWG copper conductor.

      - ***************************************************************************************

      - Edit the following paragraphs to match project requirements.

      - ***************************************************************************************

Connect ground lug of metal pole to ground rod using a 6 AWG copper conductor.

Connect ground lug of metal pole to concrete encased electrode with a 4 AWG copper conductor.

Connect ground lug of metal pole to circuit equipment grounding conductor.

For non-metallic poles, ground metallic components of luminaire to grounding electrode.

      - ***************************************************************************************

      - Edit the following article to match project requirements. Security, parking area, and storage area lighting systems typically use a control system as described herein. Roadway lighting systems typically use luminaire-mounted photo controls.

      - ***************************************************************************************

LigHting Control System

Install exterior lighting control system components in accordance with the manufacturers’ instructions. Have installation instructions available at the construction site.

Install a HAND-OFF-AUTO selector switch in the control system to allow for testing of luminaires.

Provide separate control of exterior lighting system as follows:

Egress lighting to the public way: Photoelectric relays or as shown on Drawings.

Pedestrian walkway and roadway lighting: “ON” at dusk, “OFF” at dawn.

Parking facility and landscape lighting: “ON” at dusk, “OFF” at predetermined time between 8:30 p.m. and 2:30 a.m. or sunrise, automatically changing the settings each day in accordance with seasonal changes. Approximately 10 percent of parking lot lighting shall remain on until dawn for personnel security.

      - ***************************************************************************************

      - If fuses are not needed at the base of poles, omit the article below.

      - ***************************************************************************************

Fuses and Fuse holders

Install fuse(s) and fuse holders in pole hand hole or transformer base for each luminaire.

Install fuse holder and fuse in each phase conductor.

Orient breakaway fuse holders so no energized conductors will be exposed in the event of a pole knockdown.

Install insulator boots over fuse holders and tape wrap where conductor enters boot.

Raceways And Boxes

Install raceway system for exterior lighting using materials and methods specified in Section << 26 0533 - Raceways and Boxes for Electrical Systems>>.

Building Wire

Install wiring for exterior lighting using materials and methods specified in Section << 26 0519 - Low Voltage Electrical Power Conductors and Cables>>.

FIELD QUALITY CONTROL

Inspect installed lighting for damage. Replace, or repair, damaged luminaires, poles, and components.

Test installed luminaires for proper operation.

Replace or repair malfunctioning luminaires and components, then re-test.

Repeat procedure until all luminaires operate properly.

ADJUSTING AND CLEANING

Clean each luminaire, including plastics and glassware. Use methods and materials recommended by manufacturer.

Aim adjustable luminaires to provide required light intensities as indicated on the Drawings or as directed by the LANL STR.

Adjust exterior lighting controls as indicated on the Drawings or directed by the LANL STR.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 26 5600, REV. 7, DATED APRIL 15, 2026.