SECTION 26 0519

LOW VOLTAGE ELECTRICAL POWER CONDUCTORS AND CABLES

**************************************************************************************************************

LANL MASTER SPECIFICATION

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality Sections.
**************************************************************************************************************

GENERAL

SECTION INCLUDES

*************************************************************************************************************

Edit article to match Project requirements. Delete items not applicable to Project.

*************************************************************************************************************

Building wire (600 V)

Metal-clad cable (600 V)

Wire and cable connectors

Insulating tape and tubing

Wire pulling lubricant

QUALITY ASSURANCE

Comply with the National Electrical Code (NEC) installation requirements.

Provide products that are listed and labeled by a Nationally Recognized Testing Laboratory (NRTL).  If listed products are unavailable, contact LANL Electrical Safety Office via LANL Subcontract Technical Representative (STR) for instructions.

Calibrated tools and test instruments shall be maintained and calibrated per NETA ATS.

*************************************************************************************************************

Edit the following to match project conditions.

*************************************************************************************************************

ACTION SUBMITTALS

Note:  Certification of the Subcontractor’s tool and instrument calibration program is an element of the Subcontractor’s Quality Assurance Program required by Section 01 4000; submit under that Section.  If not present in Specification, submit under this Section.

*************************************************************************************************************

Edit the following to match project conditions.

*************************************************************************************************************

informational/CLOSEOUT SUBMITTALS

Submit the following

Field Test Records:

Tool and instrument calibration records.

Termination torque records.

Cable pulling records.

Field Quality Control inspection reports and tests results.

Documentation of 10% witness of torqueing per Field Quality Control article (3.9).  Note: For further information, refer to Section 01 4000.

Receiving, Storing and Protecting

Receive, store, and protect, and handle products per NECA 1, Standard Practices for Good Workmanship in Electrical Construction.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Refer to Section 01 2500, Substitution Procedures.

When manufacturers or products are listed in this section, the lists are meant to be examples of products that meet it and not meant to be all-inclusive.  Any product that meets the same salient features listed is acceptable.

  - BUILDING WIRE

Provide building wire as shown on the Drawings with the following characteristics:

Description: Single conductor 600 V insulated wire.

Conductor:

*************************************************************************************************************

Edit the following to match project conditions. *************************************************************************************************************

[Unless otherwise indicated on the Drawings:] 98% conductivity, annealed, uncoated copper, ASTM B 3 Standard Specification for Soft or Annealed Copper Wire, solid or stranded as specified in Part 3 of this Section.

Aluminum conductors may be used under the following conditions:

- Conductors are AA 8000 series aluminum alloy registered in ASTM B 800 Standard Specification for 8000 Series Aluminum Alloy Wire for Electrical Purposes—Annealed and Intermediate Tempers, compact stranded per ASTM B 801 Standard Specification for Concentric-Lay-Stranded Conductors of 8000 Series Aluminum Alloy for Subsequent Covering or Insulation.

- Conductors are 8AWG or larger

- If construction drawings show copper conductors, Subcontractor is responsible for recalculating wire sizes, voltage drop, raceway sizes, junction box sizes, and conduit body sizes.
Note: If the raceway size is 2 inches or less, it is exempt from seismic design.  If, by using aluminum conductors instead of copper, the size of the raceway exceeds 2 inches, the raceways are subject to seismic design.

Insulation: The following types, rated 600 volts:

*************************************************************************************************************

Edit the following to match project conditions. Use thermoset (XHHW-2) conductor insulation for all branch circuits and feeders for Safety Class; Safety Significant; and NEC Article 695, 700, 701, and 708 systems. Thermoset insulation may also be needed for wiring in high temperature or high radiation environments. If these systems or conditions do not exist on this Project, delete the information within brackets. *************************************************************************************************************

[Unless otherwise indicated on the Drawings:] Type THHN/THWN-2

[Where indicated on the Drawings:] Type XHHW-2

*************************************************************************************************************

Edit the following to match Project requirements. If the project is construction of a new facility the following applies.  Delete if not applicable to Project.

Note:  Color codes are really only meaningful during construction.  After construction, the only colors that matter are for the Neutral and the Grounding.  All other colors are ungrounded conductors and it is not practical to assume that a particular line or phase is a consistent color throughout the installation.

*************************************************************************************************************

Color-code conductors in new installations as follows:

Use colored insulation for color coding conductors 6 AWG and smaller, unless part of a cable assembly. Conductors that are part of a cable assembly may be marked at termination points.

Use  water and oil resistant colored plastic adhesive tape, 3/4 inch minimum width, for color coding conductor 4 AWG and larger.

Manufacturer: 3M “Scotch 35"

Use the following color codes for AC power system conductors:

| Conductor | 480Y/277V | 208Y/120V | 208Y/120V Isolated Ground* |
| --- | --- | --- | --- |
| Phase A | Brown | Black | Black |
| Phase B | Orange | Red | Red |
| Phase C | Yellow | Blue | Blue |
| Grounded (Neutral) | Gray | White | White |
| Equipment Grounding | Green | Green | Green |
| Isolated Ground | --- | --- | Green/Yellow |
| Switched | Purple or color of feeding circuit with labels: S1, S2… | Pink or color of feeding circuit with labels: S1, S2… | --- |

* 	isolated grounds may only be used with the approval of the LANL Electrical Standards Point of Contact

Note:  The phasing at the load terminals of a breaker in a Schneider Electric I-Line panel may not be ABC top to bottom; color-code the conductors by phase as noted in the table, and as marked on the terminals of the circuit breakers.

Note:  The rotation of a system might require colors to be swapped thus changing the physical location of where an expected color for a line or phase may be.  This is acceptable.

Use the following color codes for DC power system conductors:

Positive:	Red

Negative:	Black

Use the following color codes for 120/240 volt AC single-phase systems:

Line 1:   Black

Line 2:   Red

Grounded Conductor:  White

Equipment grounding conductor:  Green

Provide color code for control conductors as indicated on equipment or control system manufacturer’s drawings.

*************************************************************************************************************

If Project is an addition or modification to an existing facility, then the following applies.  Delete if not applicable.  If multiple color codes exist in a facility such that there is no predominant one, use the color codes for new installations.

If the color code for a facility is not known at the time of design, it might require an outage to ascertain the facility color code unless the responsible system engineer knows.  In the absence of being able to obtain the facility color code, assume the color code for new installations.  Brown-Orange-Yellow for 480/277 and Black-Red-Blue for 208/120.  If, upon opening the panels, the colors are the same but in a different sequence, e.g., Orange-Yellow-Brown, the existing color code for the facility should be used.

*************************************************************************************************************

Color-code conductors in existing facilities as follows:

Use colored insulation for color coding conductors 6 AWG and smaller, unless part of a listed cable assembly. Conductors that are part of a listed cable assembly may be marked at terminations.

Use  water and oil resistant colored plastic adhesive tape, 3/4 inch minimum width, for color coding conductor 4 AWG and larger.

Manufacturer: 3M, “Scotch 33+,” or “Scotch 35"

Use the following color codes for AC power system conductors:

*************************************************************************************************************

Edit the following: Design engineer shall complete the following table to identify the existing facility's color code requirements. Delete if not applicable to Project.

**************************************************************************************************************

| Conductor | 480Y/277V | 208Y/120V | 208Y/120V Isolated Ground* |
| --- | --- | --- | --- |
| Phase A |  |  |  |
| Phase B |  |  |  |
| Phase C |  |  |  |
| Grounded (Neutral) |  |  |  |
| Equipment Grounding | Green | Green | Green |
| Isolated Ground | --- | --- | Green/Yellow |
| Switched | Purple or color of feeding circuit with labels: S1, S2… | Pink or color of feeding circuit with labels: S1, S2… | --- |

* isolated grounds may only be used with the approval of the LANL Electrical Standards Point of Contact

Note:  The phasing at the load terminals of a breaker in a Schneider Electric I-Line panel may not be ABC top to bottom; color-code the conductors by phase as noted in the table, and as marked on the terminals of the circuit breakers.

Provide color code for control conductors as indicated on equipment or control system manufacturer’s drawings.

Note: In existing facilities, in order to maintain rotation, it is sometimes necessary to swap two conductors in a three-phase feeder.  In this situation, the color code sequence of the line side of the conductors will be different from the color code sequence on the load side of the conductors.

*************************************************************************************************************

Type MC cable may be used in IBC Business Group B occupancies for branch circuit wiring systems. Refer to Section D5020 in the LANL Engineering Standards for additional information. Delete when metal-clad cable is not used.

*************************************************************************************************************

  - METAL-CLAD CABLE

Provide metal-clad cable (Type MC) that complies with the NEC, and this Section.

Provide MC cables with quantities and sizes (minimum 12 AWG) of conductors as indicated on the Drawings.

Metal-clad cable shall consist of 600 V THHN insulated circuit conductors, an insulated equipment-grounding conductor, a Mylar wrapping around the conductor bundle, and a close-fitting aluminum or galvanized steel outer sheath.

Provide metal-clad cables with conductors solid or stranded as specified in Part 3 of this Section.

Metal-clad cables used to supply isolated-ground branch circuits shall have a neutral conductor, isolated ground conductor and equipment grounding conductor.  Identify each isolated ground conductor with a yellow-colored stripe on the green insulation.

Metal-clad cables used to supply multiple branch circuits shall have the appropriate phase conductors for the number of circuits, a separate neutral conductor for each circuit, and one equipment ground conductor per cable.  Uniquely identify each neutral with a colored stripe on the white insulation corresponding to the phase conductor insulation color.

Metal-clad cables used to supply multiple isolated-ground branch circuits shall have the appropriate phase conductors for the number of circuits, a separate neutral and isolated ground conductor for each circuit, and one equipment ground conductor per cable.  Uniquely identify each neutral with a colored stripe on the white insulation corresponding to the phase conductor insulation color.  Uniquely identify each isolated-ground conductor with one or more yellow-colored stripes on the green insulation.

Manufacturer: AFC Cable Systems Inc.

Provide insulated-throat or insulating-bushing connectors for Type MC cables.

  - WIRING CONNECTORS

For splices and taps on copper wire, sizes 12 to 10 AWG solid and 12 to 6 AWG stranded, use push-on, insulated, spring type connectors, or twist on connectors with helical coiled spring rated 600 V and 105 ºC that are NRTL-listed to UL 486C Splicing Wire Connectors and provide a means of visual inspection, if applicable, of the connection.  Use connectors within their identified and marked ranges and wire types.

Manufacturer:

IDEAL “In-Sure.”

IDEAL “Twister Series”

3M “Scotchlock”

Wago “773 Series”

For splices and taps on copper wire, sizes 6 AWG through 1 AWG, use the following materials:

Tin-plated copper split-bolt connectors meeting UL 486A-486B, Wire Connectors; provide with matching 600-volt snap-on insulating cover.

Multi-tap connectors meeting UL 486A-466B that have two or more range-taking mechanical lugs and matching 600-volt insulated cover.

For wire, sizes 12 AWG and larger, use UL 486A-486B listed mechanical terminals, splices, or adapters.

Provide mechanical terminals and splices made from aluminum, aluminum alloy, copper or a copper alloy, and marked “CU”, “AL-CU” or “CU-AL” Manufacturers: FCI Burndy, Ilsco, or Thomas & Betts.

*************************************************************************************************************

Edit the following to match project conditions. If aluminum conductors will not be used, delete the information within brackets. *************************************************************************************************************

For aluminum wire, use UL 486A-486B listed mechanical terminals, splices, or adapters.

Provide mechanical terminals and splices made from aluminum, aluminum alloy, and marked “AL”, “AL-CU” or “CU-AL”. Manufacturer: FCI Burndy, Ilsco, or Thomas & Betts.

For control wiring use nylon insulated crimp-on terminals with insulation grip that meeting UL 486A-486B. Manufacturer: 3M “Scotchlok MNG,” Thomas & Betts “Sta-Kon.”

Use ring tongue terminals for nutted studs.

Use flanged fork terminals for barrier terminal blocks.

Use pin terminals or ferrules for DIN type terminal blocks.

Insulation-piercing type connectors are not acceptable for power or control wiring.

  - INSULATING TAPE AND TUBING

Insulate taped splices and connections using ethylene propylene rubber (EPR) tape meeting UL 510 - Polyvinyl Chloride, Polyethylene, and Rubber Insulating Tape and is rated for 90ºC continuous operation and 130ºC short-term overload service. Manufacturer: 3M “Scotch 130C”

For the outer covering of tape-insulated splices and connections, use vinyl plastic tape meeting UL 510 - Polyvinyl Chloride, Polyethylene, and Rubber Insulating Tape and with the following characteristics:

8.5 mil minimum thickness,

ASTM D-3005, Standard Specification for Low-Temperature Resistant Vinyl Chloride Plastic Pressure-Sensitive Electrical Insulating Tape – Type 1.

Rated 600 volts and 105ºC, suitable for indoor and outdoor applications.

Retains flexibility, adhesion, and applicable at temperature ranges from 0 through 100ºF without loss of physical or electrical properties.

Resistant to abrasion, moisture, alkalis, acid, corrosion, and sunlight.

Manufacturer: 3M “Scotch Super 88.”

Provide heat shrinkable tubing meeting UL 486D – Sealed Wire Connector Systems and with the following characteristics:

Rated 600 volts

Factory applied adhesive/sealant

Split resistant

Manufacturer: 3M “ITCSN”

Use motor lead splicing kits to insulate and seal connections to leads for motors rated 480V and less. Manufacturer: 3M “5300 Series.”

WIRE PULLING LUBRICANT

Provide wire-pulling lubricant that is identified for use with the conductor insulation or jacket, has a maximum coefficient of dynamic friction of 0.25, and leaves no flammable residue. For cold weather installations, provide wire pulling lubricant suitable for conduit temperature.

EXECUTION

  - EXAMINATION

Verify that work of other trades likely to damage wire and cable is completed.

Verify raceway installation is complete and supported.

Field-verify dimensions shown on Drawings.

Wire and cable routing shown on Drawings is approximate unless dimensioned.

Route wire and cable as required to meet Project conditions.

Where cable routing is not shown, and destination only is indicated, determine exact routing and lengths required to meet Project conditions.

PREPARATION

Examine raceways and building finishes that are to receive wires and cables for compliance with installation tolerances and other conditions. Do not proceed with installation until unsatisfactory conditions have been corrected.  Ensure conduit bodies meet the Code requirements for the number of conductors.

NEC 314.16 for conductors 6 AWG and smaller

NEC 314.28 for conductors 4 AWG and larger

All ducts shall be cleaned by passing a wire brush mandrel and/or rubber duct swab (or approved alternative) of appropriate size back and forth until all foreign materials and water are removed.

Do not handle or pull cables that are colder than +14 degrees F. Store cold cables for at least 24 hours in a heated building prior to installation.

*************************************************************************************************************

Delete the following when existing construction is not affected.

*************************************************************************************************************

EXISTING WORK

Provide access to existing wiring connections remaining active and requiring access. Modify installation or install access panel.

Extend existing circuits using materials and methods as specified.

Determine and record the existing power distribution system phase rotation, ABC clockwise or ABC counterclockwise.  Maintain the existing phase rotation throughout the new installation.

Building Wire Installation

Install building wire per the NEC, the requirements in this Section, and the following NECA installation standards as applicable:

NECA 1 Standard for Good Workmanship in Electrical Construction (ANSI).

*************************************************************************************************************

Delete the following if aluminum building wire is not used.

*************************************************************************************************************

NECA/AA 104 Recommended Practice for Installing Aluminum Building Wire and Cable (ANSI).

Do not “through-pull” conductors at boxes, fittings or cabinets where a change of raceway alignment occurs.

Ensure manufacturer’s minimum cable bend radius is not violated during installation.

Do not damage conductor, insulation, or jacket by excessive installation pulling tension or sidewall bearing pressure.

Use a tension measuring device to monitor pulling force on conductors 1/0 AWG and larger where any of the following combinations of bends and raceway length is exceeded between accessible pull points:

4 equivalent 90-degree bends and 10 feet of raceway.

3 equivalent 90-degree bends and 40 feet of raceway.

2 equivalent 90-degree bends and 80 feet of raceway.

1 equivalent 90-degree bend and 150 feet of raceway.

Straight pull with more than 250 feet of raceway.

*************************************************************************************************************

Edit the following to match Project requirements. Delete if not applicable.

*************************************************************************************************************

Where a pulling winch is used, use a tension measuring device to monitor pulling force on each pull of conductors for ML-1, ML-2, fire pump, and emergency circuits. Record and submit the maximum measured pulling tension for each cable pull.

Record the maximum measured pulling tension for each monitored cable or conductor pull.

Obtain recommended maximum conductor or cable pulling tension and sidewall bearing pressure values from the manufacturer, or use the following maximum allowable values:

Maximum sidewall bearing pressure: 500 lb/ft.

Maximum tension, pulling directly on conductor: 0.008 lb/cmil

Maximum tension, pulling on basket grip over insulation jacket: 2000 lb, not to exceed 0.008 lb/cmil of conductor.

Submit the recorded cable, or conductor, pulling tension for each monitored pull and the corresponding maximum allowable pulling tension.

Notify the LANL STR of any cable where the minimum bending radius was violated during installation.

Notify the LANL STR of any conductor or cable pull where the maximum measured pulling tension exceeded 80 percent of maximum allowable pulling tension or sidewall bearing pressure. Replace the conductors where the maximum measured pulling tension exceeded 100 percent of maximum allowable pulling tension or sidewall bearing pressure.

Use solid copper conductors for power circuits 10 AWG and smaller.

Where both ends of conductor 10 AWG and smaller are terminated in pressure plate terminations or in crimped lugs, stranded conductors may be used.

Use stranded conductors for power circuits 8 AWG and larger.

Use copper conductors not smaller than 12 AWG for power and lighting branch circuits.

Install wiring at outlets with at least 6 inches of slack conductor at each outlet, a minimum of 3 inches of which extends beyond the box opening.

Splices in conductors may only be used with the permission of the Authority Having Jurisdiction (AHJ).

Use copper conductors for ML-1, ML-2, fire pump, and emergency systems.

*************************************************************************************************************

Delete the following when Type MC Cable is not used. Note that use of Type MC Cable at LANL is restricted to International Building Code “Business Group B” occupancy. Refer to Section D5020 in the LANL Engineering Standards for additional information.

*************************************************************************************************************

TYPE MC CABLE INSTALLATION

Install MC cables per NECA/NEIS 120, Standard for Installing Armored Cable (AC) and Metal-Clad Cable (MC) (ANSI), the NEC, and requirements in this Section.

Route MC cables to meet Project conditions.

[For branch circuits serving multiple outlets use conduit for the “homerun” from the branch circuit panelboard to the first outlet or junction box. Use Type MC cables for branch circuit wiring beyond the first outlet or junction box. ]

Use Type MC cables in interior, dry locations where they will be concealed above ceilings, in dry-wall partitions, in equipment enclosures, or below raised floors. Type MC cables may be installed exposed in dedicated electrical rooms and mechanical rooms if they will not be exposed to physical damage or deteriorating agents.

Install and support Type MC cables as required in Article 330 of the NEC. Use spring steel MC cable supports or UV resistant tie wraps, listed as a means of support, to support Type MC cables; do not use wire to support Type MC cables.

Connector Installation

Install conductors in terminals, splices, adapters, and connectors per the manufacturer’s instructions. Have the manufacturer’s installation instructions available at the construction site.

Do not nick conductors when removing insulation.

Do not cut conductor strands to fit into connectors, splices, adapters, or terminals.

Make connections using clean connection surfaces. Wire brush conductors immediately before installing lugs, terminals, splices, or adapters.

Terminate all power conductors using mechanical lugs.

Terminate control conductors using crimp-on terminals or ferrules. Do not place stranded conductors directly under terminal screws. Install terminals or ferrules on conductors using ratchet-type compression tools.

*************************************************************************************************************

Edit the following to match Project requirements. Delete if not applicable.

*************************************************************************************************************

In new facilities only, the power distribution system’s phase rotation shall be ABC clockwise, downstream of the utility transformer.  This phase rotation shall be maintained throughout the power distribution system.  Make or correct connections at rotating equipment input terminal to ensure proper equipment rotation.

*************************************************************************************************************

Edit the following to match Project requirements. Delete if not applicable.

*************************************************************************************************************

In existing facilities the power distribution system’s phase rotation shall match the existing phase rotation.  This phase rotation shall be maintained throughout the additions to the power distribution system.  Make or correct connections at rotating equipment’s input terminals to ensure proper equipment rotation.

Terminate wiring on devices and components as indicated on the drawings or per the manufacturer’s instructions.

The LANL STR shall be given 2 weeks written, advance-notice of the date and time when the torqueing of connectors and terminals, including screws and bolts in major electrical distribution equipment, will be performed. Major electrical distribution equipment includes: transformers, switchgear, switchboards, MCCs, panelboards, disconnect switches, motors greater than 10HP, receptacles sized greater than 50A.  The LANL STR or STR representative shall be contacted two weeks prior to torqueing such that the STR can arrange witnessing of the torqueing, or a percentage thereof.

Tighten connectors and terminals, including screws and bolts, to manufacturers published torque-tightening values using a calibrated torque wrench, torque screwdriver, or other approved method.
Note: Some equipment, or fasteners, have features or indicators that do not necessitate the use of a torque tool.  For example: heads that sheer off when the proper torque is applied, fasteners that have built in indicators of proper torque, or terminals that are manufactured for the purpose of not needing a torque tool.

Where manufacturer's torque-tightening values are not indicated, tighten connectors and terminals to torque-tightening values specified in ANSI/NETA ATS/MTS Tables 110.12.1, 110.12.2, 110.12.3, or 110.12.4, as appropriate
Note:  On older equipment that needs to be re-terminated, the metallurgy or grade isn’t always known.  Types of terminations may also be very unusual and might not fit into one of the categories in the tables.  The system engineer or other authority should be consulted as to how to proceed in cases such as this.

Provide a tabulated torqueing record.  This shall include as a minimum:

      - The torque values applied to all connectors and terminals  that are required to be torqued

      - The identification of the torque tools used

      - The torque tools next calibration due date

      - The person making each termination

      - Signing and dating by the person(s) performing the torqueing

      - The report will be signed and dated by the STR or STR representative witnessing the torqueing, if applicable

INSULATING TAPE AND TUBING Installation

Install insulating tape and tubing per the manufacturer’s instructions. Have the manufacturer’s installation instructions available at the construction site.

Insulate splices and taps of irregular shapes with manufactured insulating covers or insulating tape built up to not less than 150 percent of insulation rating of conductor.

For voltages over 600 volts: Use rubber insulating tape in half-lapped layers to develop the basic insulation over splices and taps.

For circuits less than 600 volts: Use vinyl plastic tape in half-lapped layers to provide the outer protective covering over splices and taps, or for the sole means of protection.

Insulate cylinder shaped splices and taps, connector barrels and adapter barrels using heat shrinkable insulating tubing, insulating covers manufactured for the connector, or tape insulation as described above.

Identification

Identify wire and cable under provisions of Section 26 0553, Identification for Electrical Systems.

Identify each conductor with its circuit number or other designation indicated on Drawings.

If color coding tape is used for the re-identification of conductors, the tape must be applied at each termination or splice.

FIELD QUALITY CONTROl

The LANL STR shall be given 2 weeks, written advance-notice of the date and time when inspection and testing required by this section will be conducted. At the discretion of the LANL STR, any of the following tests or inspections may be witnessed by the STR or STR representative.

Pre-installation Inspection and Tests

Inspect conductors and cables for:

Freedom from material defect or physical damage,

Correct conductor size, material, and insulation type,

For cables that contain conductors 1/0 and larger, or those supplying critical loads as determined by the responsible engineer or FOD, use a megohm meter in a 1-minute test to verify the insulation integrity of the conductors while still on the reel. Record all test results.

Use 1000-volts dc to test conductors rated 600 volts.

Conductors with insulation resistances over 50 megohms are acceptable.

Conductors with insulation resistances less than 2 megohms are defective.

If the conductor insulation resistance is between 50 megohms and 2 megohms consult the LANL STR for further direction.

Reject and replace entire reels, rolls, or boxes containing conductors or cables with material or manufacturing defects.

Observe conductors and cables during the installation process.

Reject and replace cable or conductor segments that have been kinked, dented, or otherwise damaged during handling or installation.

After installation of wires and cables, perform the following inspections and tests:

Inspect conductors and cables for:

Freedom from material defect or physical damage,

Correct conductor size, material, and insulation type, and

Correct color coding and identification.

Before energizing the circuit, perform the following and tests:

Before connecting conductors to equipment, use a megohm meter in a 1-minute test to verify the insulation integrity of each service conductor, feeder conductor, critical system branch circuit conductor, and critical system control conductor with respect to ground and other associated conductors in the same cable or raceway.

Use 1000-volts dc to test conductors rated 600 volts.

Conductors with insulation resistances over 50 megohms are acceptable.

Conductors with insulation resistances less than 2 megohms are defective.

If the conductor insulation resistance is between 50 megohms and 2 megohms consult the LANL STR for further direction.

After connecting conductors to equipment, inspect connections for correct connector size and type.

**********************************************************************************

Edit to match the project requirements

***********************************************************************************

Witness and document torqueing on not less than 10% of each type of connector and terminal.

Remove and replace defective, incorrect, or improperly installed conductors and connectors. Re-inspect and re-test replacement conductors and connectors.

Submit test and inspection records to the LANL STR.

*************************************************************************************************************

Delete the following paragraph if formal electrical acceptance testing is not required. Refer to Section D5000 in the LANL Engineering Standards for additional information.

*************************************************************************************************************

Refer to Section 26 0813, Electrical Acceptance Testing for other inspections and tests that are required before conductors may be energized.

END OF SECTION

*********************************************************

Do not delete the following reference information:

*********************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification is based on LANL Master Specification Section 26 0519 Rev. 7, dated August 24, 2020.