SECTION 26 2213

LoW VOLTAGE distribution transformers

*************************************************************************************************************

LANL MASTER SPECIFICATION

Available online at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality Sections.
*************************************************************************************************************

GENERAL

  - SECTION INCLUDES

    - General-purpose dry-type low-voltage transformers

    - Low-temperature rise dry-type low-voltage transformers

    - K-factor rated low-voltage transformers for non-linear loads

  - QUALITY ASSURANCE

    - Comply with the National Electrical Code (NEC) for components and installation.

    - Provide products that are listed and labeled by a Nationally Recognized Testing Laboratory (NRTL) for the application, installation condition, and the environment in which installed.

    - The manufacturer of the transformers shall be a certified ISO 9001 facility.

    - Provide products that comply with the following industry standards:

      - NEMA TP 1 – Guide for Determining Energy Efficiency for Distribution Transformers,

      - NEMA TP 2 – Standard Test Method for Measuring the Energy Consumption of Distribution Transformers.

      - NEMA TP 3 – Standard for the Labeling of Distribution Transformer Efficiency.

      - UL 1561 – Dry-Type General Purpose and Power Transformers

*************************************************************************************************************

Edit the following article to match project conditions.

*************************************************************************************************************

  - SUBMITTALS

    - Submit the following in accordance with Project submittal procedures.

    - Catalog Data. Include outline and support point dimensions of transformer enclosures and accessories, unit weight, voltages, kVA, impedance, NEMA TP 1 efficiency, sound level, tap configurations, insulation system type, and rated temperature rise.

*************************************************************************************************************

Edit the following articles to match project requirements; delete if no low-voltage distribution transformer on the Project is designated with an Ip greater than 1.0.

*************************************************************************************************************

      - Certification: Submit certification and backup information that transformers can perform required functions after a design earthquake as specified in "SERVICE CONDITIONS" below.

        - Transformers designated with Ip greater than 1.0 shall be certified by the manufacturer to withstand the total lateral seismic force and seismic relative displacements specified in the International Building Code (IBC) or ASCE 7 – Minimum Design Loads for Buildings and Other Structures.

        - Manufacturer’s certification shall be based on shake table testing or experience data (i.e., historical data demonstrating acceptable seismic performance), or by more rigorous analysis providing for equivalent safety.

        - Required response spectra shall exceed 1.1 times the in-structure spectra determined in accordance with IBC AC156 – Acceptance Criteria for Seismic Qualification by Shake-Table Testing of Nonstructural Components and Systems.

    - Certifications signed by manufacturers certifying that their products comply with the specified requirements.

    - Operation and maintenance instructions.

  - SERVICE CONDITIONS

    - Provide transformers and accessories that will perform satisfactorily in the following service conditions:

      - Elevation of 7500 feet above sea level.

      - Maximum ambient temperature of 104 °F.

      - 24-hour average temperature not exceeding 86 °F.

      - Load current harmonic factor not exceeding 5% THD.

      - International Building Code seismic criteria:

        - Seismic Design Category = D

        - SDS = spectral acceleration, short period = 0.75g

        - SD1 = spectral acceleration, 1-second period = 0.64g

        - ap = component amplification factor = 1.0

        - Rp = component response modification factor = 2.5

        - Ip = Component importance factor
Ip = 1.5 for life safety related components such as emergency system transformers
Ip = 1.5 for safety class or safety significant system transformers.
Ip = 1.0 for all other transformers applications

*****************************************************************************************************

Edit the following article to match project requirements; use only for outdoor equipment.

*****************************************************************************************************

      - Maximum solar heat gain: 110 W/sq ft.

  - Receiving, Storing and Protecting

    - Receive, store, and protect, and handle products according to NECA 1 – Standard Practices for Good Workmanship in Electrical Construction and NECA 409 – Recommended Practice for Installing and Maintaining Dry-Type Transformers (ANSI).

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

    - Alternate products may be accepted; follow Section 01 2500 – Substitution Procedures.

  - GENERAL

    - Transformers shall be NRTL listed to UL 1561 and shall be tested and labeled according to NEMA TP 1, NEMA TP 2, and NEMA TP 3.

    - The efficiency of each transformer shall be NEMA TP 1 Class I when tested in accordance with NEMA TP 2. Transformer efficiency shall be indicated on a label that conforms to NEMA TP 3.

    - Transformers shall be capable of continuous operation without exceeding temperature limits at an elevation of 7500 ft when de-rated as follows:

      - 97.5 percent of nameplate kVA in a 30 degrees-C average ambient with a maximum cooling air temperature of 40 degrees-C, or

      - 100 percent of nameplate kVA in a 28.5 degrees-C average ambient with a maximum cooling air temperature of 33.75 degrees-C.

    - Transformer coils may be aluminum or copper with continuous wound construction and shall be impregnated with non-hygroscopic, thermosetting varnish. Terminations shall be brazed or welded to the coil conductor.

    - Insulating materials shall be rated as a 220 degrees-C UL component recognized insulation system.

    - Furnish transformers with suitable dielectric materials and adequate air spacing between terminals for operating at an altitude of 7500 ft.

    - Transformers 15 kVA and larger shall have a minimum of two 2.5 percent full capacity above normal and four 2.5 percent full capacity below normal primary taps.

    - Transformer cores shall be constructed of a high grade, non-aging silicon steel with high magnetic permeability and low hysteresis and eddy current losses.  Magnetic flux densities shall be kept well below the saturation point. The core and coil shall be bolted to the base of the enclosure, isolated by means of rubber vibration-absorbing mounts. There shall be no metal-to-metal contact between the core and the enclosure.  Sound isolation systems requiring the complete removal of all fastening devices will not be acceptable.

    - The core of the transformer shall be visibly grounded to the enclosure by a flexible grounding conductor sized following applicable UL and NEC Standards.

    - The transformer enclosure shall be ventilated and shall be fabricated of a heavy gauge, sheet steel construction. The entire enclosure shall be finished using a process consisting of degreasing, cleaning and phosphatizing followed by electrostatic deposition of polymer polyester powder and baking cycle to provide a uniform coating of all edges and surfaces.  The coating shall be UL recognized for outdoor use. The coating color shall be light or medium grey.

*************************************************************************************************************

Edit the following article to match Project requirements; some installations may require lower sound levels. Transformers designed to have a 3 dB reduction below the sound levels specified below are available from several manufacturers as a premium special order item; proper design of transformer installations is usually a more cost-effective approach than specifying low-sound transformers.

*************************************************************************************************************

    - Maximum sound levels shall not exceed the following when tested according to IEEE Standard C57.12.91.

      - 10 – 50 kVA: 45 dB

      - 51 – 150 kVA: 50 dB

      - 151 – 300 kVA: 55 dB

      - 301 – 500 kVA: 60 dB

    - Transformers 45 KVA and less shall be suitable for wall, floor, or trapeze mounting; transformers larger than 45 KVA shall be suitable for floor or trapeze mounting.  Provide mounting accessories required for installation.

    - Provide weather shields for transformers installed outdoors.

    - Provide transformer manufacturer’s transformer lug kits with compression type equipment lugs and hardware for connecting conductors to transformer terminals.

************************************************************************************************************

Edit the following article to match project conditions. Use general purpose transformers where the average daily load will be less than 50% of the transformer nameplate rating. On the Drawings clearly indicate which transformers are “general-purpose”; this will typically be for general-purpose loads in office buildings and similar occupancies that normally operate eight to ten hours per day. Delete this article if general-purpose transformers are not required.

*************************************************************************************************************

  - General-Purpose DRY-TYPE TRANSFORMERS

    - Provide factory assembled and tested, energy-efficient, general-purpose, air cooled, two-winding, dry-type transformers with voltage and kVA ratings as indicated on the Drawings.

    - General-purpose transformers 15 kVA and larger shall be 150 degrees-C temperature rise above 40 degrees-C ambient.  The maximum temperature of the top of the enclosure shall not exceed 50 degrees-C rise above a 40 degrees-C ambient.

    - Manufacturers:

      - Square D Type “EE”,

      - Eaton/Cutler-Hammer “DS-3”and “DT-3”,

      - Sola/Hevi-Duty “ES” and “ET.”.

*************************************************************************************************************

Edit the following article to match project conditions. Use low temperature rise dry-type transformers where the average daily load will be 50% or more of the transformer nameplate rating. On the Drawings clearly indicate which transformers shall be low temperature rise; this will typically be for continuous loads (e.g. 24-hour per day loads in laboratory buildings and computer centers). Delete this article if low temperature rise transformers are not required.

*************************************************************************************************************

  - Low Temperature Rise DRY TYPE TRANSFORMERS

    - Provide factory assembled and tested energy-efficient, low temperature rise air cooled, two-winding type, dry-type transformers with voltage and kVA ratings as indicated on the Drawings.

    - Low temperature rise transformers 15 kVA and larger shall be 115 degrees-C temperature rise above 40 degrees-C ambient and shall be capable of carrying a 15 percent continuous overload without exceeding a 150 degrees-C rise in a 40 degrees-C ambient at sea level.

    - Manufacturers:

      - Square D “EE Watchdog”,

      - Eaton/Cutler-Hammer “DS-3” and “DT-3”,

      - Sola/Hevi-Duty “ES” and “ET.”.

*************************************************************************************************************Edit the following article to match project conditions. Use K-factor rated dry-type transformers for separately derived systems serving computer or other high harmonic loads. On the Drawings clearly indicate which transformers shall be K-Factor rated. Delete this article if K-factor transformers are not required.

*************************************************************************************************************

  - K-Factor Rated DRY TYPE TRANSFORMERS

    - Provide factory assembled and tested, energy-efficient, air cooled, two-winding type, dry-type transformers with voltage, kVA and K-factor ratings as indicated on the Drawings.

    - Transformers shall be 115 degrees-C temperature rise above 40 degrees-C ambient at sea level. Neither the primary nor the secondary temperature shall exceed 220 degrees-C at any point in the coils while carrying their full rating of non-sinusoidal loads. K-factors shall be defined as the sum of fundamental and harmonic I(pu)²h² per UL 1561.

    - K-Factor rated transformers shall have an impedance range of 3 percent to 5 percent, and shall have a minimum reactance of 2 percent in order to help reduce neutral current when supplying loads with large amounts of third harmonic current.

    - Size transformer neutral terminal for 200 percent of the rated secondary phase current.

    - Transformers shall be common core construction. The core laminations above 112.5 kVA shall be miter cut at the core corners to reduce hot spots, core loss, excitation current and sound level. The core laminations shall be clamped with steel angles.  Cores for transformers greater than 300 kVA shall be clamped utilizing insulated bolts through the core laminations to provide proper pressure throughout the length of the core.  The completed core and coil shall then be bolted to the base of the enclosure but isolated by means of rubber, vibration-absorbing mounts. There shall be no metal-to-metal contact between the core and coil and the enclosure. Sound isolation systems requiring the complete removal of all fastening devices will not be acceptable.

    - Transformers shall be supplied with a full width electrostatic shield resulting in a maximum effective coupling capacitance between primary and secondary of 33 picofarads.  With transformers connected under normal, loaded operating conditions, the attenuation of line noise and transients shall equal or exceed the following limits:

      - Common Mode:  0 to 1.5 Hz – 120 dB; 1.5 to 10 kHz – 90 dB;  10 to 100kHz – 65 dB;  100 kHz to 1 MHz - 40dB.

      - Traverse Mode:  1.5 to 10 kHz – 52 dB; 10 to 100 kHz – 30 dB, 100 kHz to 1 MHz – 30 dB.

    - Manufacturer:

      - Square D “EE NL and EE NLP Series”,

      - Eaton/Cutler-Hammer “KT”,

      - Sola/Hevi-Duty 3H”.

EXECUTION

  - EXISTING WORK

*************************************************************************************************************

Delete this article when existing construction is not affected.

*************************************************************************************************************

    - Disconnect and remove abandoned dry-type transformers.

    - Maintain access to existing dry-type transformers and other installations that are to remain active and to require access. Modify installation or provide access panel.

    - Clean and repair existing dry-type transformers that are to remain or be reinstalled.

  - EXAMINATION

    - Examine surfaces to receive transformers for compliance with installation tolerances and other conditions affecting performance of the control system.  Do not proceed with installation until unsatisfactory conditions have been corrected.

  - INSTALLATION

    - Install dry-type transformers where indicated on the Drawings and according to manufacturer's instructions. Manufacturer’s installation instructions shall be available at the construction site.

    - Install transformers according to NECA 409 Recommended Practice for Installing and Maintaining Dry-Type Transformers (ANSI).

*************************************************************************************************************

On the Drawings clearly indicate which transformers require vibration isolators. Delete the following article if vibration isolators are not required.

*************************************************************************************************************

    - Install transformers on vibration isolators where indicated on the Drawings. Refer to Section 26 0548, Vibration and Seismic Controls for Electrical Systems for vibration isolators.

    - Install each floor-mounted transformer on a minimum 5-inch-high reinforced concrete pad. Refer to Section 26 0548, Vibration and Seismic Controls for Electrical Systems for anchoring materials and methods.

    - Install wall-mounted transformers on wall brackets manufactured by the transformer manufacturer. Do not mount transformers larger than 15 kVA on drywall construction. Do not wall mount transformers larger than 45 kVA. Refer to Section 26 0548, Vibration and Seismic Controls for Electrical Systems for anchoring materials and methods.

*************************************************************************************************************

Space limitations sometimes necessitate wall-mounting a dry-type transformer above a floor mounted transformer. Each such proposed design must be analyzed by a mechanical engineer to determine the necessary vertical separation or other reliable means (e.g., redundant fans) to assure adequate cooling for both transformers.

*************************************************************************************************************

    - Arrange equipment to provide adequate spacing for access, replacement, and for cooling air circulation. Locate the front and rear of each ventilated transformer at least 6 inches from the wall or any obstruction to allow proper air circulation.

    - Use flexible conduits, 2 ft. minimum lengths, for connections to transformer case. Make conduit connections to transformer enclosure only at locations designated by the manufacturer’s installation instructions.

    - Connect conductors to transformer terminals using transformer manufacturer’s lug kits. Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values. Where manufacturer's torque values are not furnished, use those specified in UL 486A-486B.

    - Bond transformers and ground systems served by transformers according to Section 26 0526, Grounding and Bonding for Electrical Systems.

    - Identify transformers and install warning signs according to Section 26 0553, Identification or Electrical Systems.

  - FIELD QUALITY CONTROL

    - Clean, inspect, test, adjust, and energize transformers in accordance with NECA 409.

      - Inspect each transformer for physical damage, proper connection and grounding, and proper anchorage.

      - Keep records of inspections, tests, and adjustments; submit them to the LANL STR.

*****************************************************************************************************

Edit the following article to match project requirements. Delete if formal electrical acceptance testing is not required; refer to LANL Master Specification Section 26 0813.

*****************************************************************************************************

    - Coordinate inspections and tests with those required by Section 26 0813 – Electrical Acceptance Testing.

    - After completing installation, cleaning, and testing, touch up scratches and mars on finish to match original finish.

    - Measure primary and secondary voltages and phase rotation, and make preliminary tap adjustments. After normal operating loads have been energized adjust taps to provide the following voltage at points of use; record voltages and tap settings.

System Nominal Voltage		Minimum Load Voltage

480Y/277				460Y/265

208Y/120				200Y/115

120/240				115/230

END OF SECTION

*********************************************************

Do not delete the following reference information.

*********************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 26 2213 Rev. 2, dated September 24, 2009.