SECTION 26 2300

LOW-VOLTAGE SWITCHGEAR

*************************************************************************************************************

LANL MASTER SPECIFICATION

Available online at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  Additional tailoring requirements are contained in ESM Chapter 1 Section Z10 Att. F, Specifications.

To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality Sections.

Seismic Design:  This template cannot be properly edited for job-specific seismic requirements without the following three (3) decisions having been made first:

- Whether the switchgear is exempt from ASCE 7 Ch. 13.

- How to comply with ASCE 7 paragraph 13.2.1.

- Whether the switchgear is a Designated Seismic System (DSS).

I) If the switchgear is exempt per ASCE 7 paragraph 13.1.4 then the seismic-related requirements herein are not applicable, and the same goes for the remaining two decisions (i.e., II and III).

II) There are two (2) options for complying with ASCE 7 paragraph 13.2.1:

- Project-specific design and documentation, prepared by the Engineer of Record (EOR) or the construction subcontractor (i.e., Delegated Design); or

- Manufacturer certification

If the latter option applies then this Section (26 2413) shall reference Section 01 8734, Seismic Qualification of Nonstructural Components (IBC), and a project-specific version of 01 8734 shall be created and included in the Project Spec.

III) DSS: If switchgear must function after the design-basis earthquake, it is assigned an Importance Factor (Ip) of 1.5 and, as a result of this, and the fact that switchgear is “active,” it is a DSS that requires Special Certification.  If this applies then, regardless of the previous decision (i.e., II), this section shall reference Section 01 8734, Seismic Qualification of Nonstructural Components (IBC), and a project-specific version of 01 8734 shall be created and included in the Project Spec.

If II.A applies, and will be accomplished via Delegated Design, then this Section shall reference Section 26 0548.16, Seismic Controls for Electrical Systems, and a project-specific version of 26 0548.16 shall be created and included in the Project Spec.  The seismic design criteria will be included therein.

Finally, another reason to include Sect. 26 0548.16 in a Project Spec is to specify seismic control/ restraint.  Such use of 26 0548.16 is not applicable only for projects in which switchgear is exempt and those in which compliance with ASCE 7 paragraph 13.2.1 is achieved via II.B.   
*************************************************************************************************************

*************************************************************************************************************

Refer to LANL Engineering Standards Manual Section D5010 (paragraph 2.6) for requirements applicable to using a “low-voltage power circuit breaker switchgear assembly” as opposed to using a “power panelboard” or a “switchboard”. Refer to LANL Master Specification Sections 26 2413 – Switchboards and 26 2416 – Panelboards.

*************************************************************************************************************

GENERAL

SECTION INCLUDES

Low-voltage arc-resistant switchgear which consists of an enclosure, power circuit breakers, instruments, metering equipment, monitoring equipment or control equipment, with associated interconnections and supporting structures.

*************************************************************************************************************

Retain Article below to cross-reference requirements Subcontractor might expect to find in this Section but are specified in other Sections.  Refer to the “seismic portion” of the author note on page 1 for details.

- If the Switchgear is exempt then delete Article.

- If ASCE 7 paragraph 13.2.1 is going to be complied with via manufacturer certification, and the switchgear isn’t a DSS, then retain only the 1st subparagraph.

- If ASCE 7 paragraph 13.2.1 is going to be complied with via project-specific design and documentation, and the switchgear isn’t a DSS, then retain only the 2nd subparagraph, and edit bracketed text based on whether II.A or II.B applies:

  - If II.A applies, delete bracketed text.

- For all other circumstances, retain both subparagraphs, and edit the bracketed text in the 2nd as applicable.

*************************************************************************************************************

RELATED SECTIONS

- Section 01 8734, Seismic Qualification of Nonstructural Components (IBC), for requirements.

- Section 26 0548.16, Seismic Controls for Electrical Systems, for [seismic-design criteria,] submittal requirements, devices for seismic restraint, and installation requirements for these devices.

  - DEFINITIONS

- Arc-resistant: Designed to withstand the effects of an internal arcing fault and to direct the internally released energy away from personnel performing normal operating duties in close proximity to the equipment while the equipment is operating under normal conditions.

- Normal operating duties: Operations such as opening or closing switching devices, connecting and disconnecting withdrawable parts, reading of measuring instruments and monitoring equipment, etc. Removing or replacing active components (e.g., fuses or any other removable primary component) and activities required to carry out maintenance work are not considered to be normal operations.

- Unless otherwise specified or indicated, electrical and electronics terms used in this Section are as defined in IEEE Std 100 – The Authoritative Dictionary of IEEE Standards Terms.

  - ACTION SUBMITTALS

Provide the following submittals according to the provisions of Project submittal procedures.

Catalog Data describing each type low-voltage switchgear, circuit breaker, accessory item, and component specified. Include data substantiating that materials comply with specified requirements.

*************************************************************************************************************

Delete Section C only if switchgear is exempt from seismic.  If retained, edit paragraph in accordance with editing done in article 1.2 and the project-specific decisions referred to in the author note on pp. 1 (e.g., whether the switchgear is a DSS, whether the project spec includes Section 26 0548.16, whether the project-specific design is prepared by the engineer of record or is delegated).  *************************************************************************************************************

Installation Instructions indicating application conditions and limitations of use stipulated by Product testing agency specified under Quality Assurance. Include instructions for storage, handling, protection, examination, installation, and starting of Product, including equipment anchoring requirements to meet the seismic conditions specified in "SERVICE CONDITIONS.”

**********************************************************************************************************

Edit the following article to match project requirements; include the last sentence for “double-ended” switchgear or switchgear with multiple sources.

***********************************************************************************************************

Performance Data/Curves including time-current curves for each circuit breaker.

Shop Drawings for each low-voltage switchgear assembly including dimensioned plans and elevations and component lists. Include front and side views of enclosure showing overall dimensions, enclosure type, enclosure finish, unit locations, and conduit entrances. Include the following:

Master drawing index.

Front, side, and plan view of the switchgear.

Single line or three line diagrams.

Nameplate schedule.

Component lists.

Conduit entry locations.

Busway entry locations and details.

Assembly ratings including short circuit, voltage, and current.

Major component ratings including voltage, current, and interrupting.

Cable terminal sizes and types.

Shipping splits.

Enclosure type with details for types other than NEMA Type 1.

Bus configuration and current ratings.

Features, characteristics, ratings, and factory settings of individual protective devices and auxiliary components.

*****************************************************************************************************

Edit the following articles to match project requirements; delete if not required.

*****************************************************************************************************

Key interlock scheme drawing and sequence of operations.

Connection details between close-coupled assemblies.

Composite front view and plan of close-coupled assemblies.

Description of the main-tie-main automatic throw-over system to include components and operating sequences.

Additional information for seismic:

      - Include dimensioned plans and elevations that identify the weight, and the locations of the horizontal and vertical centers or gravity.

      - Indicate field anchorage or mounting provisions to hold the equipment in place and resist forces derived from the criteria specified in [Section 01 8734] [Section 26 0548.16].

      - Identify anchors and other mounting devices.

      - Include information on the size, type, and spacing of factory-installed mounting brackets, holes, and other mounting provisions

Wiring Diagrams including detailed schematic wiring diagrams including device identifications and numbered terminals for power, control, communications and instrumentation systems, and differentiating between manufacturer-installed and field-installed wiring. [Include a wiring diagram of the modified differential ground fault system.]

Test Reports including results of factory production tests specified in IEEE C37.20.1 and field inspections and tests required by this Section.

Operation and Maintenance Instructions including step-by-step inspection and maintenance test procedures and a listing of recommended spare parts. Include instructions for testing circuit breakers. [Include a test procedure for the modified differential ground fault system using high current injection equipment.]

*****************************************************************************************************

Edit the following article to match project requirements; include the last sentence for “double-ended” switchgear or switchgear with multiple sources.

*****************************************************************************************************

QUALITY ASSURANCE

Comply with the National Electrical Code (NEC) for installation requirements, such as wire bending space.

Furnish products that are listed and labeled by a Nationally Recognized Testing Laboratory (NRTL)

Comply with the following ANSI/IEEE standards:

IEEE C37.13 / ANSI C37.50 – Test Procedures for Low-Voltage AC Power Circuit Breakers Used in Enclosures.

ANSI C37.16 – Preferred Ratings, Related Requirements, and Application Recommendations for Low Voltage AC Power Circuit Breakers

ANSI C37.17 – Standard for Trip Devices for AC and General Purpose DC Low-voltage Power Circuit Breakers

IEEE C37.20.1 – Standard for Metal-Enclosed Low-Voltage Power Circuit Breaker Switchgear

Comply with NEMA C37.50 – Switchgear Low Voltage AC Power Circuit Breakers Used in Enclosures - Test Procedures and NEMA C37.51 – Metal-Enclosed Low-Voltage AC Power Circuit Breaker Switchgear Assemblies – Conformance Test Procedures.

Comply with UL 1066 – Low-Voltage AC and DC Power Circuit Breakers Used in Enclosures and UL Standard 1558 – Low Voltage Power Circuit Breaker Switchgear.

*****************************************************************************************************

Edit the following article to match renovation project requirements; delete if not required.

*****************************************************************************************************

Receiving, Storing, and Protecting

Receive, inspect, handle, and store low-voltage switchgear according to the following:

Manufacturer's written instructions.

ANSI/IEEE C37.20.1

NECA 1 – Standard Practices for Good Workmanship in Electrical Construction (ANSI).

MAINTENANCE MATERIALS

For each switchgear assembly furnish one set of any special tools required to operate and maintain the equipment.

For each switchgear assembly furnish two sets of keys for key interlocks.

Furnish one spray can of touch-up paint that matches finish for each switchgear assembly. Provide Material Safety Data Sheet (MSDS) for touch-up paint.

*************************************************************************************************************

Edit the following article to match project requirements; delete if there is no automatic throw-over system not needed.

*************************************************************************************************************

Supply backup copies of automatic throw-over system PLC programming plus software, interface hardware, and passwords required to modify programming or re-load programming.

EXTRA PRODUCTS

Furnish a total of three (3) of each size and type power and control fuse installed in the low-voltage switchgear.

Furnish one of each type circuit breaker electronic trip unit installed in the low-voltage switchgear.

For each size and type power circuit breaker in the switchgear furnish the following:

Four spare blank nameplates for circuit breaker cell doors.

*************************************************************************************************************

Edit the following article to match project requirements; delete if there is no automatic throw-over system not needed.

*************************************************************************************************************

Furnish one of each type digital input module and one of each type digital output module for the programmable logic controller (PLC) associated with the automatic throw-over system.

SERVICE CONDITIONS

Furnish low-voltage switchgear that will perform satisfactorily in the following service conditions without mechanical or electrical damage or degradation of operating characteristics:

Operating elevation of 7500 feet above sea level.

Operating ambient temperature extremes of 32 to 104 °F.

Operating relative humidity: 0 to 80 percent, without condensation.

*****************************************************************************************************

Edit the following article to match project requirements; use only for outdoor equipment.

*****************************************************************************************************

Maximum solar heat gain: 110 W/sq ft.

FIELD MEASUREMENTS

Make field measurements to assure that the low voltage switchgear will fit in allocated space in full compliance with minimum clearances recommended by the manufacturer, required by NEC, and the following minimum clearances:

Each end: 3’-0” plus space to add one switchgear section at one end.

Verify field measurements against manufacturer’s shop drawings prior to fabrication.

Notify the LANL STR if the allocated space is inadequate for the switchgear.

PRODUCTS

*************************************************************************************************************

For Switchgear that is exempt from seismic, if Project Spec includes 26 0548.16, and if mounting and/or anchorage devices are to be used that differ from those specified in 26 0548.16, they must be described herein (in PART 2).

*************************************************************************************************************

  - PRODUCT OPTIONS AND SUBSTITUTIONS

    - Alternate products may be accepted; follow Section 01 2500 – Substitution Procedures.

*************************************************************************************************************

Delete the following section if the switchgear is exempt from seismic.

If retaining, edit the article in accordance with related edits made in PART 1.

If DSS applies, this shall (also) be indicated on the drawings (i.e., as a minimum, on the sheet where the component is first shown/ indicated.).

*************************************************************************************************************

  - SEISMIC PERFORMANCE REQUIREMENTS

The Switchgear shall withstand the effects of earthquake motions as represented by the [design basis earthquake in Section 01 8734] [seismic hazard indicated on the drawings] [the forces derived from the criteria specified in Section 26 0548.16].

The term “withstand” means “the switchgear will remain in place without separation of any parts when subjected to the seismic [forces derived from the specified criteria] [hazard indicated on the drawings].”

DSS: The switchgear is a Designated Seismic System and, as such, it shall withstand the effects of earthquake motions as represented by the design basis earthquake in Section 01 8734.

The term “withstand” means “the switchgear will remain in place without separation of any parts when subjected to the seismic forces derived from the specified criteria, and it will be fully operational after the design basis earthquake.”

  - LOW-VOLTAGE SWITCHGEAR

Manufacturers:

Square D Company, “POWER ZONE 4”

Eaton, “Magnum DS”

Siemens Energy & Automation, Inc., “Type WL”

*************************************************************************************************************

Edit the following article to match project requirements.

*************************************************************************************************************

Furnish NRTL-listed [indoor] [outdoor, walk-in], low-voltage switchgear that meets the requirements of ANSI/IEEE C37.20.1 and UL Standard 1558 and has the following ratings:

Operating Voltage: 480Y/277 volts

Rated Maximum Voltage: 635 volts (RMS)

Rated Frequency: 60 Hz

Rated Insulation Level: 2.2 kV (RMS)

*************************************************************************************************************

Edit the following article to match project requirements; main bus rating need not exceed main breaker frame size.

*************************************************************************************************************

Main Bus Rated Current: [1600] [2000] [3200] [4000] [5000] amperes. [As scheduled on the Drawings.]

Neutral Bus Rated Current: 100% of the main bus rating.

*************************************************************************************************************

Edit the following article to match project requirements; rated short time current need not be greater than the corresponding rating of the main circuit breaker.

*************************************************************************************************************

Rated Short Time Current: [50,000] [65,000] [85,000] amperes (RMS symmetrical) [As scheduled on the Drawings.]

*************************************************************************************************************

Edit the following article to match project requirements; rated short circuit current need not be more than the corresponding rating of the main circuit breaker.

*************************************************************************************************************

Rated Short Circuit Current: [50,000] [65,000] [85,000] amperes (RMS symmetrical) [As scheduled on the Drawings.]

*************************************************************************************************************

Edit the following article to match project requirements.

*************************************************************************************************************

[Low-voltage switchgear assembly shall be suitable for use as service entrance equipment and so labeled according to UL requirements.]

Fabricate enclosure frame, internal barriers and outer panels following ANSI/IEEE C37.20.1.

Finish interior panels and barriers with light or medium gray paint or powder coat applied using an electro-deposition process over rust-inhibiting phosphate primer.

Enclosure construction shall prevent entry of rodents and reptiles into the switchgear interior.

Rear cable compartments shall have full-height removable hinged doors with padlocking provisions.

Each circuit breaker cell shall have a hinged outer steel door with padlocking provisions. Circuit breaker cell doors shall be free of any ventilation openings.

Use Type SIS flexible stranded 90 °C wire that is VW-1 flame test rated per UL 1581 for control and communications wiring.

Secure wires in bundles using nylon ties; anchor bundles to the switchgear assembly using pre-punched wire lances.

Connect current transformer secondary leads to accessible short-circuiting terminal blocks before connecting to any other device.

Terminate control and communications conductors on terminal blocks with suitable numbering strips; use crimp-on ring-type lugs.

Install wire markers at each end of all control and communications wiring.

Mount prominent nameplates on the front of the low-voltage switchgear assembly showing equipment designation, ratings, manufacturer identification, reference serial numbers, and special operations instructions such as for key interlocks.

Fabricate main, riser, run-back, neutral and ground busses from silver-plated copper, with joints made up with SAE grade 5 bolts and Belleville-type spring washers.

Silver plating shall be a minimum of 0.0002 inch thick and cover the entire length of each bus bar.

The through-bus shall be rated at the full ampacity of the main throughout the switchgear.

A minimum one quarter by 2 inches ground bus shall be firmly secured to each vertical section structure and shall extend the entire length of the switchgear.

*************************************************************************************************************

Edit the following article to match project requirements. Refer to LANL ESM Chapter 7 Section D5010 Article 2.0 for grounded conductor (neutral) requirements.

*************************************************************************************************************

The neutral bus shall be rated [100][     ] percent of the main bus continuous current rating [as indicated on the Drawings].

Phase bus bars shall be insulated with factory applied fire retardant NRTL-recognized insulation system.  Bolted bus joints shall be insulated with secure joint covers than can be removed and reinstalled.

Insulating barriers shall separate the main bus from the rear cable compartment, separate the rear cable compartments in adjacent sections, and isolate the incoming line connections from the main horizontal and vertical bus. Insulating material shall comply with NEMA LI 1 – Industrial Laminating Thermosetting Products, Grade GPO-3.

Switchgear with calculated short circuit current exceeding 65,000 amperes shall have means for cable bracing.

  - POWER CIRCUIT BREAKERS

*************************************************************************************************************

Edit the following article to match project requirements.

*************************************************************************************************************

Main [, tie] and feeder overcurrent devices shall be NRTL labeled, 100% rated, draw-out type, low voltage AC power circuit breakers. Each circuit breaker shall meet the requirements of ANSI/IEEE C37.13, ANSI C37.16, and UL 1066.

Circuit breakers shall have the following ratings:

Operating Voltage: 480Y/277 volts

Contact ratings of 600 volts

Rated Maximum Voltage: 635 volts (RMS)

Rated Frequency: 60 Hz

Rated Continuous Current: as scheduled on Drawings

*************************************************************************************************************

Edit the following article to match project requirements.  Include all circuit breaker frames that will be furnished. Circuit breaker short time interrupting ratings must exceed the calculated bolted fault current based on an infinite source at the primary of the immediate upstream transformer.

*************************************************************************************************************

Short Time Trip Interrupting Rating at 480 volts:

800 amp frame, [42,000][65,000][85,000] amperes (RMS symmetrical)

1600 amp frame, [42,000][65,000][85,000] amperes (RMS symmetrical)

2000 amp frame, [65,000][85,000] amperes (RMS symmetrical)

3200 amp frame, [65,000][85,000] amperes (RMS symmetrical)

4000 amp frame, 85,000 amperes (RMS symmetrical)

5000 amp frame, 85,000 amperes (RMS symmetrical)

*************************************************************************************************************

Edit the following article to match project requirements.  Include all circuit breaker frames that will be furnished. Circuit breaker short time interrupting ratings must exceed the calculated bolted fault current based on an infinite source at the primary of the immediate upstream transformer.

*************************************************************************************************************

Instantaneous Trip Interrupting Rating at 480 volts:

800 amp frame, [42,000][65,000][85,000] amperes (RMS symmetrical)

1600 amp frame, [42,000][65,000][85,000] amperes (RMS symmetrical)

2000 amp frame, [65,000][85,000] amperes (RMS symmetrical)

3200 amp frame, [65,000][85,000] amperes (RMS symmetrical)

4000 amp frame, 85,000 amperes (RMS symmetrical)

5000 amp frame, 85,000 amperes (RMS symmetrical)

*************************************************************************************************************

Edit the following article to match project requirements. Some systems may require the dead bus control capability provided by station batteries; the use of station batteries must be approved by the ESM Chapter 7 POC due to the higher installation and maintenance costs.

*************************************************************************************************************

Rated Control Voltage: [120 Vac] [125 Vdc]

Circuit breakers shall be manually operated unless electrically operated breakers are indicated on the Drawings or specified in this Section.

*************************************************************************************************************

Edit the following article to match project requirements; coordinate with Drawings; delete if not needed.  Specify electrically operated circuit breakers only where remote opening and closing is required.

*************************************************************************************************************

Electrically operated circuit breakers shall be complete with [120 Vac] [125 Vdc] operators, [open/close pushbuttons] [control switch], plus red and green indicating lights to indicate breaker contact position], [DC source shall be supplied from a remote battery system] [AC source shall be taken from a (remote source) (control power transformer internal to the switchgear assembly)].

*************************************************************************************************************

Edit the following article to match project requirements; coordinate with Drawings; delete if not needed.  Specify fused circuit breakers only where available short circuit current exceeds the interrupting rating of the switchgear or down-stream equipment. Fused circuit breakers should only be needed on some on renovation projects; new projects should be designed to keep the available short circuit current as low as practicable.

*************************************************************************************************************

Fused power circuit breakers shall contain integral current-limiting fuses as indicated on the Drawings. Coordination of the circuit breaker and the integral fuses shall be such that on overloads or low magnitude short-circuits the circuit breaker will operate to clear the fault. For high magnitude short circuits the current-limiting fuses will clear the fault and then the circuit breaker shall trip open.

It shall be possible to rack each circuit breaker from the connected to the disconnected position with the cubicle door closed. Interlocks shall prevent racking the circuit breaker unless the breaker is open

Each circuit breaker shall have means for padlocking open to prevent manual or electric closing.  The padlocking shall also secure the breaker in the connected, test, or disconnected position.

Identify each circuit breaker with a unique serial number visible from the front.

Circuit breaker manual trip devices shall be recessed or otherwise protected to prevent accidental operation.

*************************************************************************************************************

Edit the following article to match project requirements; coordinate with Utilities; delete if not needed.

*************************************************************************************************************

[Main and tie circuit breaker cubicles shall have auxiliary switches for remote monitoring of OPEN or CLOSED position by the utility SCADA system.]

*************************************************************************************************************

Edit the following article to match project requirements; use for double ended switchgear assemblies with main-tie-main control systems; delete if not needed.

*************************************************************************************************************

[Main and tie circuit breakers shall have remote, umbilical, control devices.]

*************************************************************************************************************

Edit the following article to match project requirements.

*************************************************************************************************************

Main [, tie] and feeder circuit breaker trip units shall be NRTL listed, true RMS sensing, microprocessor based devices capable of being remotely monitoring and controlled over a communications network. Each circuit breaker trip unit shall meet the requirements of ANSI C37.17 Standard for Trip Devices for AC and General Purpose DC Low-Voltage Power Circuit Breakers and shall have the following functions as indicated on the Drawings:

Protection: Long time, short time (with and without I2T, field selectable), instantaneous and ground fault (with and without I2T, field selectable). Instantaneous pickup setting shall have an OFF position.

LED Indications: Mode of trip and unit status.

Display: Alphanumeric display of phase and ground amperes, cause of trip, fault current, peak demand, present demand, energy consumption, and service messages.

Testing: Simulated testing of all protection functions

Communications: Breaker status (open/closed/tripped), cause of trip, time of trip, current at time of trip, RMS currents per  phase and ground, peak demand, present demand, energy consumption.

Metering: Minimum metering display accuracy of the complete system shall be +/- 2% of full scale for current values, +/- 3% of full scale for power values, +/- 4% of full scale for energy values.

*************************************************************************************************************

Edit the following article to match project requirements. Refer to LANL ESM Chapter 7 Section D5010 (paragraph 2.6.3-D).

*************************************************************************************************************

Zone Selective Interlocking: Implement zone selective interlocking between main and feeder circuit breakers within the low-voltage switchgear [and with circuit breakers having electronic trip units in upstream and downstream switchgear, switchboards, and panelboards]. Interlock both short-time and ground-fault time delays with upstream and downstream devices so the circuit breaker closest to the fault trips with no delay.

Each circuit breaker shall have means to be individually set to a maintenance mode that will reduce arc-flash incident energy by providing fast tripping in response to an arc fault even when Instantaneous on the trip unit is set to OFF.

A simple operator action shall set the circuit breaker to trip without delay at a predetermined arc fault current value; the reverse operator action shall restore the circuit breaker to its normal selective coordination settings.

The operator action shall not require adjustment of the trip unit selective coordination settings. The operator interface may be either through the switchgear communications network or by operating a two-position switch located on the circuit breaker trip unit or above the circuit breaker cell door.

A blue light located either on the circuit breaker trip unit or above the circuit breaker cell door shall indicate that the circuit breaker is in the maintenance mode; provide a similar indication through the switchgear communications network.

Each circuit breaker cell shall have shutters that will automatically cover live parts when the circuit breaker is in disconnect, test, or remove position.

Furnish means to prevent insertion of an incorrect circuit breaker into a cell.

Completely equip breaker cells indicated as SPACE on the Drawings for the future insertion of circuit breakers with features specified in this Section.

  - ACCESSORIES

*************************************************************************************************************

Edit the following article to match project requirements; coordinate with Drawings; delete if not needed. Some double-ended switchgear arrangements will be divided into two physically separated assemblies connected with a tie bus; there will be tie circuit breaker in each assembly.

*************************************************************************************************************

Key interlock systems shall accomplish the following functions:

      - [Prevent operation of the secondary unit substation primary switch if the corresponding 480Y/277 volt main circuit breaker is closed.]

      - [Prevent closing tie circuit breaker[s] if both main circuit breakers are closed.]

      - [Prevent closing both main circuit breakers unless [both] tie circuit breaker[s] is [are] open.]

*************************************************************************************************************

Edit the following article to match project requirements; coordinate with Drawings; usually needed for main-tie-main automatic throw-over systems; delete if not needed.

*************************************************************************************************************

Cells shall have truck operated cell switch[es] to indicate racking position of the main [and tie] circuit breaker[s].]

*************************************************************************************************************

Edit the following article to match project requirements; coordinate with Drawings; delete if not needed.

*************************************************************************************************************

Design grounding of system neutral in the switchgear [for double-ended arrangement.] [to facilitate future conversion of the switchgear to a double-ended arrangement.]

Each switchgear assembly shall include a rail-mounted, traveling circuit breaker hoist and lifter bar.

*************************************************************************************************************

Edit the following article to match project requirements; coordinate with Drawings.

*************************************************************************************************************

Transformer[s] with 220 degrees F insulation and primary plus secondary fuses shall provide 120 volt control power as required by: metering and monitoring system; [outdoor enclosure lights, receptacles and strip heaters;] [and adequate power for transformer cooling fans].  Use fuses with blown-fuse indicators while fuse is installed in the fuse mounting.

*************************************************************************************************************

Edit the following article to match renovation project requirements; coordinate with Drawings; delete if not needed.

*************************************************************************************************************

[A bus transition section shall interface with the existing _____/_____ kVA (AA/FA) [liquid filled] [dry-type] transformer[s].  Transformer[s] was [were] manufactured by ____________ and is [are] shown on manufacturer's shop drawing number _______, dated ________.]

Install a mimic bus, showing bussing, connections and circuit breakers on the front panels of the switchgear.  Use 0.75 inch wide, 7 mil thick white vinyl plastic tape with rubber-based adhesive.]

*************************************************************************************************************

Edit the following article to match project requirements; include for double ended switchgear and switchgear with multiple sources; delete if not needed.

*************************************************************************************************************

[480Y/277V, 4-wire, connected switchgear having multiple sources shall have a modified differential ground fault system. The manufacturer shall complete the modified differential ground fault system design prior to building the switchgear and shall supply all components to insure that the proper main or tie breaker(s) operate properly during the following occurrences on the main bus.

Ensure the system will trip with the occurrence of a ground fault at any location in the switchgear.

Ensure system will not trip without ground fault and with normal current flow.

Ensure system will not trip due to large single-phase currents.

Ensure system will trip with combination of normal current flow and ground fault current flowing together.

Rear cable compartment doors shall have viewing ports on to allow closed-door thermographic inspection of all cable and bus connections in the rear cable compartment using a generic infrared (IR) camera with a 45 degree lens.

      - Each viewing port shall consist of a frame, a reinforced infrared transmitting window, and a captive cover.

      - Window material shall not be affected by moisture and shall have minimum infrared transmittances of 68 percent at 9 microns and 55 percent at 4 microns.

      - Select window diameters and place windows so all connections can be viewed with the camera at an angle not more than 30 degrees from perpendicular to the window.

      - Viewing windows shall comply with IEEE C37.20.2 and UL 746C.

************************************************************************************************************

Edit the following article to match project requirements; use for switchgear in unit-substations; delete if not needed.

*************************************************************************************************************

  - METERING

Each main circuit breaker shall have an electronic meter and associated instrument transformers, test switches and plugs, and fuses in a dedicated, barriered instrument compartment.

      - Mount top of meter readout approximately 60 inches above the floor.

      - Current transformers shall be appropriately sized for use on the main.

      - Furnish potential transformers if required by the meter.

Refer to Section 26 2713, Electricity Metering for metering system materials.

  - COMMUNICATIONS NETWORK

Each low-voltage switchgear shall have a communications network connecting the following:

      - Addressable trip unit in each draw-out circuit breaker to communicate:

Circuit breaker position in cradle (connected/test/disconnected),

Breaker status (open/closed/tripped),

Cause of trip, time of trip, current at time of trip,

RMS currents per phase and ground, peak demand, present demand, energy consumption.

      - Addressable microprocessor-based device(s) for switchgear metering.

*************************************************************************************************************

Edit the following article to match project requirements; use for switchgear in unit-substations; delete if not needed.

*************************************************************************************************************

      - Addressable unit substation transformer fan control devices.

*************************************************************************************************************

Edit the following article to match project requirements; use the first option for single-ended switchgear; use the second option for double ended switchgear with an automatic throw-over system.

*************************************************************************************************************

Install network interface hardware so that the communications network in the switchgear is prepared to communicate [over a 100 Mbps fiber optic or 10/100 Mbps UTP Ethernet communications network to remote PCs.][over an RS-485 communications network to the PLC in the switchgear.]

*************************************************************************************************************

Edit the following article to match project requirements; coordinate with Drawings; delete the entire article if not needed.

- This article describes a two-source, three breaker, closed-transition re-transfer system used in double-ended switchgear for a facility that requires the highest level of power continuity, such as a computing center.

- Less critical facilities (e.g. typical nuclear facilities) do not require the closed transition operating sequence described in this article; for such facilities use the “open transition” re-transfer scheme described in the next article.

- Other switchgear configurations, such as those with secondary tie circuits to separate switchgear, will require different automatic throw-over system specifications.

*************************************************************************************************************

  - AUTOMATIC THROW-OVER SYSTEM  (Closed-Transition)

The double-ended low-voltage switchgear shall include a two-source, three-breaker automatic throw-over control system in for the automatic operation of the main and tie circuit breakers. This system shall provide a closed-transition operating sequence to minimize disruption of power to loads during maintenance operations and when restoring the system to its normal configuration.

The control system shall be complete with programmable logic controller (PLC), two uninterruptible power supplies (UPS), control power transfer relays, control switches and indicator lights, and other components as required to accomplish the specified functions.

Install a control panel on a cell door located away from the main or tie circuit breakers, with the following features:

      - A control switch for each main and tie circuit breaker for manual tripping and closing.

      - Three indicator lights with legend plates above each circuit breaker control switch to indicate open (green), closed (red), and tripped on overcurrent (yellow).

      - Key-operated, manual-maintenance-automatic operating-mode selector switch.

      - Three operating mode indicator lights: manual (red, flashing), maintenance (yellow, flashing), automatic (green) with legend plates.

      - Key operated test switch to simulate loss of voltage on either source and to permit testing of the complete automatic throw-over control system.

      - Two source available indicator lights (green) with legend plates.

      - Two control power transfer position indicator lights (amber) with legend plates.

      - Indicator lights shall be push-to-test LED pilot lights.

Use solid-state, draw-out case mounted protective relays that conform to the requirements of ANSI/IEEE C37.90 Relays and relay Systems Associated with Electric Power Systems as follows:

      - Two 3-phase ANSI device type 47 voltage phase sequence relays that respond to phase failure, phase unbalance and reversed phase sequence.

      - One single-phase ANSI device type 25 synchronism-check relay to determine that proper phase angle and voltage exist.

In the automatic mode the control system shall have the following sequence of operation:

      - Normal configuration: both main circuit breakers closed and the tie circuit breaker open.

      - Upon phase reversal or loss of phase-to-phase voltage of either source to 70% of nominal, and after a time delay of 1 second (adjustable from 0.1 to 10 seconds), open the main circuit breaker corresponding to the failed source then immediately close the tie circuit breaker if voltage is available at the other main circuit breaker.

      - After the above operation and when the failed source has been restored to normal and synchronism check is maintained for 5 minutes (adjustable from 1 to 10 minutes, [automatically] [permit manual controls to] make a closed transition re-transfer: close the main circuit breaker corresponding to the restored source then immediately open the tie circuit breaker.  Automatic, open transition, retransfer shall occur without time delay in the event of phase reversal or loss of phase-to-phase voltage on the source feeding the closed main circuit breaker.

      - Include provisions to prevent automatic throw-over under the following conditions:

Simultaneous failure of both sources.

If a main or tie circuit breaker has tripped due to overcurrent or ground fault.

If either main or the tie circuit breaker is in the test or disconnected position.

If mode selector switch is in the manual or maintenance position.

      - When in the automatic mode, disable the breaker control switches.

In the maintenance mode the control system shall have the following sequence of operation:

      - Normal configuration: both main circuit breakers closed and the tie circuit breaker open.

      - Operating the control switch for either main circuit breaker shall, after synchronism check, close the tie circuit breaker then immediately open the main circuit breaker corresponding to the control switch.

      - After the above operation, operating the control switch for the tie circuit breaker shall, after synchronism check, close the open main circuit breaker then immediately open the tie circuit breaker.

      - Include provisions to prevent the above maintenance mode operations under the following conditions:

If main or tie circuit breaker has tripped due to overcurrent or ground fault.

Phase reversal or loss of phase-to-phase voltage of either source.

If main or either tie circuit breaker is in the test or disconnected position.

In the manual mode the control system shall have the following sequence of operation:

      - Normal configuration: both main circuit breakers closed and the tie circuit breaker open.

      - Operating the control switch for either main circuit breaker shall open or close the main circuit breaker corresponding to the control switch.

      - Operating the control switch for the tie circuit breaker shall close or open the tie circuit breaker.

      - In the manual mode, electrically interlock the main and tie circuit breakers to prevent paralleling of sources.

Use an industrial-grade PLC to control the automatic throw-over system.

      - PLC shall retain programming and data through power interruptions of four months duration.

      - PLC shall have dual power supplies connected to the two UPSs described below. Power supplies shall meet IEEE 587, Category B requirements for surge voltage protection.

      - PLC shall include digital input modules with not less than 2500 VRMS isolation between input terminals and logic. Each input channel shall have two LED indicators: an input LED that illuminates when the input receives an ON signal; a logic LED that illuminates when the input is correctly converted to a processor level logic signal. Input channels shall include but not be limited to:

Two voltage phase-sequence relays

Synchronism-check relay

Mode selector switch

Two test switches

Three circuit breaker manual close/trip control switches

Three overcurrent trip switches

Three sets of truck operated breaker cell connected/disconnected switches

Two sets of four UPS status relays (AC input present, low battery, inverter operating, bypass active)

Not less than 20 percent spare input channels.

      - PLC shall include digital output modules with not less than 2500 VRMS isolation between input terminals and logic. Each output channel shall have three LED indicators: a logic LED that illuminates when module receives an ON signal from the processor; a load LED that illuminates when the output voltage is provided at the output terminals; a blown fuse LED that illuminates when a blown fuse is detected. Digital output modules shall contain an electronic or a field replaceable fuse for each channel. Output channels shall include but not be limited to:

Three circuit breaker close circuits

Three circuit breaker trip circuits

Automatic mode indicator light circuit

Automatic mode failure indicator light circuit

Maintenance mode indicator light circuit

Manual mode indicator light circuit

Source A indicator light circuit

Source B indicator light circuit

Not less than 20 percent spare output channels.

      - PLC shall include RS 485 port to interface with the communications network in the switchgear.

      - PLC shall include both RS-232C and Ethernet ports for communication of the following switchgear status and metering information to remote PCs or the building automation system:

Automatic throw-over system status (mode selector switch position, position of each main and tie circuit breaker, source A present, source B present).

All metering and circuit breaker status information on the switchgear communications network.

PLC status (run, error, halt, battery low).

Status of each UPS (AC input present, low battery, inverter operating, bypass active).

      - Fully document the automatic throw-over control system programming in the O&M manual. Supply backup copies of programming plus software, interface hardware, and passwords required to modify programming or re-load programming as O&M material. Provide detailed procedures for functional testing of the automatic throw-over system.

Use two on-line, industrial-type UPSs to power the automatic throw-over system and the associated PLC. Each UPS shall have the following features:

      - NRTL-listed and complying with NEMA PE-1.

      - Sufficient battery capacity after 2 years of operation to support the PLC through a 10 minute power interruption then power two automatic throw-over operations at the end of the 10 minute period.

      - Sealed lead-acid batteries that are hot-swappable and user replaceable.

      - Automatic static bypass switch.

      - Operation panel indicating status, output load, battery voltage, and system faults.

      - Dry contacts to indicate:

AC input present

Low battery

Inverter operating

Bypass active.

Automatic control power transfer relays shall transfer control power bus from one control power source to the second when the first is de-energized.

*************************************************************************************************************

Edit the following article to match project requirements; coordinate with Drawings; delete the entire article if not needed.

- This article describes a two-source, three breaker, open-transition re-transfer system used in a double-ended switchgear.

- More critical facilities (e.g. large computing facilities) may require the closed transition operating sequence described in the previous article

- Other switchgear configurations, such as those with secondary tie circuits to separate switchgear, will require different automatic throw-over system specifications.

*************************************************************************************************************

  - AUTOMATIC THROW-OVER SYSTEM  (Open-Transition)

The double-ended low-voltage switchgear shall include a two-source, three-breaker automatic throw-over control system for the automatic operation of main and tie circuit breakers.

The control system shall be complete with programmable logic controller (PLC), two uninterruptible power supplies (UPSs), control power transfer relays, control switches and indicator lights, and other components as required to accomplish the specified functions.

Install a control panel on a cell door located away from the main or tie circuit breakers, with the following features:

      - A control switch for each main and tie circuit breaker for manual tripping and closing.

      - Three indicator lights with legend plates above each circuit breaker control switch to indicate open (green), closed (red), and tripped on overcurrent (yellow).

      - Key-operated manual- automatic operating mode selector switch.

      - Two operating mode indicator lights: manual (red, flashing), automatic (green) with legend plates.

      - Key-operated test switch to simulate loss of voltage on either source and to permit testing of the complete automatic throw-over control system.

      - Two source available indicator lights (green) with legend plates.

      - Two control power transfer position indicator lights (amber) with legend plates.

      - Indicator lights shall be push-to-test LED pilot lights.

Use solid-state, draw-out case mounted protective relays that conform to the requirements of ANSI/IEEE C37.90 Relays and relay Systems Associated with Electric Power Systems as follows:

      - Two 3-phase ANSI device type 47 voltage phase sequence relays that respond to phase failure, phase unbalance and reversed phase sequence.

In the automatic mode the control system shall have the following sequence of operation:

      - Normal configuration: both main circuit breakers closed and the tie circuit breaker open.

      - Upon phase reversal or loss of phase-to-phase voltage of either source to 70% of nominal, and after a time delay of 1 second (adjustable from 0.1 to 10 seconds), open the main circuit breaker corresponding to the failed source then immediately close the tie circuit breaker if voltage is available at the other main circuit breaker.

      - After the above operation and when the failed source has been restored to normal, [automatically] [permit manual controls to] make an open transition re-transfer: open the tie circuit breaker, then after a 5 second time delay (adjustable form 1 to 10 seconds), close the main circuit breaker corresponding to the restored source.

      - Include provisions to prevent automatic throw-over under the following conditions:

Simultaneous failure of both sources.

If a main or tie circuit breaker has tripped due to overcurrent or ground fault.

If tie circuit breaker is in the test or disconnected position.

If mode selector switch is in the manual position.

      - When in the automatic mode, disable the breaker control switches.

In the manual mode the control system shall have the following sequence of operation:

      - Normal configuration: both main circuit breakers closed and the tie circuit breaker open.

      - Operating the control switch for either main circuit breaker shall open or close the main circuit breaker corresponding to the control switch.

      - Operating the control switch for the tie circuit breaker shall close or open the tie circuit breaker.

      - In the manual mode, electrically interlock the main and tie circuit breakers to prevent paralleling of sources.

Use an industrial-grade PLC to control the automatic throw-over system.

      - PLC shall retain programming and data through power interruptions of four months duration.

      - PLC shall have dual power supplies connected to the two UPSs described below. Power supplies shall meet IEEE 587, Category B requirements for surge voltage protection.

      - PLC shall include digital input modules with not less than 2500 VRMS isolation between input terminals and logic. Each input channel shall have two LED indicators: an input LED that illuminates when the input receives an ON signal; a logic LED that illuminates when the input is correctly converted to a processor level logic signal. Input channels shall include but not be limited to:

Two voltage phase-sequence relays

Mode selector switch

Two test switches

Three circuit breaker manual close/trip control switches

Three overcurrent trip switches

Three sets of truck operated breaker cell connected/disconnected switches

Two sets of four UPS status relays (AC input present, low battery, inverter operating, bypass active)

Not less than 20 percent spare input channels.

      - PLC shall include digital output modules with not less than 2500 VRMS isolation between input terminals and logic. Each output channel shall have three LED indicators: a logic LED that illuminates when module receives an ON signal from the processor; a load LED that illuminates when the output voltage is provided at the output terminals; a blown fuse LED that illuminates when a blown fuse is detected. Digital output modules shall contain an electronic or a field replaceable fuse for each channel. Output channels shall include but not be limited to:

Three circuit breaker close circuits

Three circuit breaker trip circuits

Automatic mode indicator light circuit

Automatic mode failure indicator light circuit

Manual mode indicator light circuit

Source A indicator light circuit

Source B indicator light circuit

Not less than 20 percent spare output channels.

      - PLC shall include RS 485 port to interface with the communications network in the switchgear.

      - PLC shall include both RS-232C and Ethernet ports for communication of the following switchgear status and metering information to remote PCs or the building automation system:

Automatic throw-over system status (mode selector switch position, position of each main and tie circuit breaker, source A present, source B present).

All metering and circuit breaker status information on the switchgear communications network.

PLC status (run, error, halt, battery low).

Status of each UPS (AC input present, low battery, inverter operating, bypass active).

      - Fully document the automatic throw-over control system programming in the O&M manual. Supply backup copies of programming plus software, interface hardware, and passwords required to modify programming or re-load programming as O&M material. Provide detailed procedures for functional testing of the automatic throw-over system.

Use two on-line industrial type UPSs to power the automatic throw-over system and the associated PLC. Each UPS shall have the following features:

      - NRTL-listed and complying with NEMA PE-1.

      - Sufficient battery capacity after 2 years of operation to support the PLC through a 10 minute power interruption then power two automatic throw-over operations at the end of the 10 minute period.

      - Sealed lead-acid batteries that are hot-swappable and user replaceable.

      - Automatic static bypass switch.

      - Operation panel indicating status, output load, battery voltage, and system faults.

      - Dry contacts to indicate

AC input present

Low battery

Inverter operating

Bypass active.

Automatic control power transfer relays shall transfer control power bus from one control power source to the second when the first is de-energized.

*************************************************************************************************************

Edit the following article to match project requirements; coordinate with Drawings; delete if not needed.

*************************************************************************************************************

  - Surge Protection

Each low-voltage switchgear shall include surge arresters connected to the line-side of each main circuit breaker; refer to Section 26 4123 – Lightning Protection Surge Arresters and Suppressors.

Each low-voltage switchgear shall include transient voltage surge suppressors connected to the main bus on the load side of each main circuit breaker; refer to Section 26 4313 – Transient Voltage Suppressors.

*************************************************************************************************************

Edit the following article to match project requirements; delete if an outdoor enclosure is not needed.

*************************************************************************************************************

  - OUTDOOR ENCLOSURE

Outdoor low-voltage switchgear shall have a walk-in weatherproof enclosure with the following features:

      - Full length, minimum 4’-6” wide, interior aisle.

      - Access/exit doors with panic hardware at each end of aisle.

      - Hinged access doors with tamper-resistant hardware and pad-lockable handles at the rear of each switchgear section.

      - LED lighting providing 30 vertical foot candles on face of switchgear 3 ft above floor.

Refer to Section 26 5100 – Interior Lighting for material and installation requirements.

      - One GFCI duplex convenience receptacle per 10 feet of length.

      - Thermostatically-controlled exhaust fan(s). Powered outlet dampers interlocked with powered inlet dampers. Use 30% efficiency filters on air inlets. Provide exterior rain-proof louvers on air inlets and exhaust fan outlets.

      - Thermostat controlled breaker cell strip heaters.

      - Step-down transformer and panelboard to serve the enclosure loads plus 25% spare capacity.

      - Removable steel cover plates over bottom conduit entrance areas.

      - White or light gray interior paint finish.

      - ANSI #61 exterior epoxy paint finish

  - FACTORY TESTS

Perform factory production tests that conform to ANSI C37.20.2, ANSI C37.50.  Provide certification of design tests and other tests conforming to ANSI/IEEE C37.20.2, ANSI C37.50 and ANSI C37.51.

Set the circuit breaker trip units and current sensor taps to values scheduled on the Drawings or indicated in the coordination study. Test calibration of trip units and associated current sensors by primary current injection into each breaker pole, one pole at a time.

*************************************************************************************************************

Edit the following article to match project requirements; include the words “modified differential” for double ended switchgear and switchgear with multiple sources.

*************************************************************************************************************

Make performance tests of the low-voltage switchgear [modified differential] ground fault protection systems by primary current injection into each breaker pole, one pole at a time. Include neutral sensor in test circuit.

Make performance tests of the automatic throw-over system.

Make performance tests of the switchgear communications network.

Make performance tests of the switchgear metering.

EXECUTION

************************************************************************************************************

For switchgear that is exempt from seismic, if Project Spec includes 26 0548.16, and if requirements associated with installation, testing, and inspection of mounting and/or anchorage devices differ from those requirements in 26 0548.16, they must be described herein (in PART 3).  Also, if this is applicable, identify special types of seismic-control devices required for each application using the same terminology used for those devices in PART 2.

*************************************************************************************************************

  - EXISTING WORK

*************************************************************************************************************

Delete this article when existing construction is not affected.

*************************************************************************************************************

Maintain access to existing low-voltage switchgear that is to remain active.

  - EXAMINATION

Examine surfaces to receive low-voltage switchgear for compliance with installation tolerances and other conditions affecting performance of the product. Do not proceed with installation until unsatisfactory conditions have been corrected.

*************************************************************************************************************

Edit the following article to match project requirements; coordinate with Drawings; delete if not needed.

*************************************************************************************************************

  - INSTALLATION

Install switchgear where indicated on the Drawings and according to manufacturer's instructions, ANSI/IEEE C37.20.1, and the NEC. Have the manufacturer’s installation instructions available at the construction site.

Install switchgear on a reinforced concrete housekeeping pad as shown on the Drawings.

      - Refer to Section 26 0548.16 – Seismic Controls for Electrical Systems.

      - The pad must be level to within 1/8 inch per 3-foot distance in every direction.

*************************************************************************************************************

Edit the following article to match project requirements; coordinate with Drawings; delete if not needed.

*************************************************************************************************************

Install busway connections as required in Section 26 2500 – Enclosed Bus Assemblies and by the switchgear manufacturer’s installation instructions.

      - Terminate each busway in the switchgear section containing the corresponding device.

      - Provide for seismic motion at the top of the switchgear as recommended by the busway or switchgear manufacturer.

Install conduits as required in Section 26 0533 – Raceways and Boxes for Electrical Systems and Section 26 0548.16 – Seismic Controls for Electrical Systems

      - Terminate conduits in the switchgear section containing the corresponding device.

      - Provide for seismic motion at the top of top of the switchgear as recommended by the switchgear manufacturer.

      - Install plugged couplings set flush with the top of the concrete pad.  After switchgear is set in place, extend conduits to 1-1/4 inch above the pad and terminate with insulated grounding bushings.

Ground and bond the low-voltage switchgear as required in Section 26 0526 – Grounding and Bonding for Electrical Systems.

Install conductors as required in Section 26 0519, Low voltage Electrical Power Conductors and Cables.

      - Train conductors neatly in groups; bundle and secure as recommended by manufacturer to withstand fault current.

      - Tighten electrical connectors and terminals, including bus bar and grounding connections, according to the manufacturer’s published torque-tightening values. Where manufacturer's torque values are not indicated, use those specified in UL 486A.

*************************************************************************************************************

Edit the following article to match project requirements; coordinate with Drawings; delete if not needed.

*************************************************************************************************************

      - Where the calculated short circuit current exceeds 65,000 amperes, securely lace and support line and load cables in accordance with the switchgear manufacturer’s installation instructions.

*************************************************************************************************************

Edit the following article to match project requirements; coordinate with Drawings; delete if not needed.

*************************************************************************************************************

Install zone selective interlock wiring to circuit breakers in other electrical equipment as indicated on the Drawings. Follow switchgear manufacturer’s instructions.

*************************************************************************************************************

Delete the following paragraph if the switchgear is exempt from seismic

*************************************************************************************************************

Comply with requirements for seismic control devices and mounting and anchoring requirements specified in Section 26 0548.16 Seismic Controls for Electrical Systems.

  - IDENTIFICATION

Install electrical identification on low-voltage switchgear and conductors according to Section 26 0553 – Identification for Electrical Systems.

Mark floor in front and rear of switchgear to show NEC required working clearances according to Section 26 0553 – Identification for Electrical Systems.

Install engraved laminated Category I nameplate for each device. Refer to Section 26 0553 – Identification for Electrical Systems.

Post one-line diagrams data and operating instructions in accordance with Section 26 0553 – Identification for Electrical Systems.

*************************************************************************************************************

Edit the following article to match project requirements; coordinate with Drawings; delete if not needed.

*************************************************************************************************************

Install an engraved nameplate Category 2 nameplate, red background with white lettering, with operating procedures for the automatic throw-over control system. Refer to Section 26 0553 – Identification for Electrical Systems.

  - FIELD QUALITY CONTROL

Upon completion of installation, inspect interior and exterior of switchgear.  Remove paint splatters and other spots, dirt, and debris.

Adjust all access doors and operating handles for free mechanical and electrical operation as described in the manufacturer's instructions.

Verify that circuit breakers are in the proper cells and that setting of solid state trip devices and current sensor taps match values scheduled on the Drawings.

Witness proper torque of accessible bus connections and mechanical fasteners while unit is being installed.

Test the main-tie-main automatic breaker transfer system for proper functioning and accurate sequence of operation if such a system is provided.

Test each key interlock system for proper functioning if keyed interlocks are provided.

After completing installation, cleaning, and testing, touch up scratches and mars on finish to match original finish.

Coordinate inspections and tests with those required by Section 26 0813 – Electrical Acceptance Testing.

  - MANUFACTURER'S FIELD SERVICE

Provide the services of a factory trained service engineer from the manufacturer to inspect and certify the installation and to oversee energizing and testing.

Manufacturer’s service engineer shall set all adjustable protective devices to the values recommend in the final coordination study.

Manufacturer’s service engineer shall certify that the equipment has been installed, adjusted, and tested in accordance with the manufacturer’s recommendations.

Provide one full work day of training for up to three owner’s representatives at the project site. A manufacturer’s qualified representative shall conduct training. The training program shall consist of instruction on the operation and maintenance of the assembly, circuit breakers, and major components within the assembly.

END OF SECTION

*********************************************************

Do not delete the following reference information.

*********************************************************

THE FOLLOWING REFERENCE IS FOR LANL USE ONLY

This project specification is based on LANL Master Specification Section 26 2300 Rev. 3, dated April 12, 2017.

*************************************************************************************************************

NOTE TO DESIGNER: The electrical Drawings pertaining to the low-voltage switchgear should include the following information:

1.	One-line diagram; refer to Drawing ST7002 in the LANL Electrical Engineering Standards Manual.

2.	Grounding one-line diagram; refer to Drawing ST7003 in the LANL Electrical Engineering Standards Manual.

3.	Breaker trip unit setting table based on fault current and coordination studies:

a.	Circuit number.

b.	Load name.

c.	Sensor rating (amps) “S”.

d.	Rating plug (amps) “P”.

e.	Long time pickup (xP)

f.	Long time delay (sec).

g.	Short time pickup (xP) (if used).

h.	Short time delay (sec) (if used).

i.	Instantaneous pickup (xP) (if used)

j.	Ground fault pickup (xP)

k.	Ground fault delay (sec)

l.	Remarks

4.	Switchgear plan and elevation.

5.	Seismic anchoring details.

6.	Communications network diagram showing connection to other equipment and to a facilities operations computer.  (If applicable)

*************************************************************************************************************