SECTION 26 2816

Enclosed switches and circuit breakers

*************************************************************************************************************

LANL MASTER SPECIFICATION

Available online at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  Additional tailoring requirements are contained in ESM Chapter 1 Section Z10 Att. F, Specifications.

To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.
When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.
Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality Sections.

Seismic:  If the enclosed switches or circuit breakers are not exempt from seismic design per ASCE 7 paragraph 13.1.4 then, prior to attempting to edit this Section to be Project-specific, refer to Sections 26 0548.16, Seismic Controls for Electrical Systems, and 01 8734, Seismic Qualification of Nonstructural Components (IBC), as applicable.

*************************************************************************************************************

GENERAL

SECTION INCLUDES

*************************************************************************************************************

Edit the following to match project requirements.

*************************************************************************************************************

    - Safety switches

    - Fuses

    - Enclosed circuit breakers

    - Fractional horsepower motor disconnects

*************************************************************************************************************

Seismic: If the enclosed switches or circuit breakers are exempt from seismic design then delete both of the following subparagraphs.

- Otherwise, see the “seismic-portion” of the previous author note.

*************************************************************************************************************

Related sections

Section 01 8734, Seismic Qualification of Nonstructural Components (IBC), for requirements

Section 26 0548.16, Seismic Controls for Electrical Systems, for [seismic-design criteria,] submittal requirements, devices for seismic restraint, and installation requirements for these devices.

SUBMITTALS

Submit the following in accordance with project submittal procedures:

Product Data: Submit manufacturer's technical data for each type of safety switch, fuse, enclosed circuit breaker and fractional horsepower motor disconnects; including data proving that materials comply with specified requirements. Provide catalog sheets showing voltage and current ratings, short circuit ratings, dimensions, and enclosure details.

*************************************************************************************************************

Seismic: Delete the following paragraph only if electrical equipment is exempt from seismic.  If retained, edit paragraph in accordance w/ editing done in Article 1.2 and the project-specific decisions referred to in the author note on pp. 1 (e.g., whether the electrical equipment is a DSS, whether the Project Spec includes Sect. 26 0548.16, whether the project-specific design is prepared by the engineer of record or is delegated).

*************************************************************************************************************

Shop Drawings: For each type electrical equipment included in this specification

          - Include dimensioned plans and elevations that identify the weight

          - Indicate field anchorage or mounting provisions to hold the equipment in place and resist forces derived from the criteria specified in [Section 01 8734] [Section 26 0548.16].

          - Identify anchors and other mounting devices.

          - Include information on the size, type, and spacing of factory-installed mounting brackets, holes, and other mounting provisions.

Installation Instructions: Indicate application conditions and limitations of use stipulated by Product testing agency specified under Regulatory Requirements. Include instructions for storage, handling, protection, examination, preparation, installation, and starting of Product.

QUALITY ASSURANCE

Comply with the National Electrical Code (NEC) for installation requirements such as bending space for conductors.

Provide safety switches and circuit breakers that are listed and labeled by a Nationally Recognized Testing Laboratory (NRTL), where such products are required by the NEC to be listed, or such products contain an electrical hazard as follows:

For AC circuits – Greater than 50 volts

For DC circuits and/or batteries – Greater than 100 volts

Comply with the following standards as applicable:

NEMA FU 1 Low Voltage Cartridge Fuses

NEMA KS 1 - Enclosed and Miscellaneous Distribution Equipment Switches (600 Volts Maximum)

UL 50 - Enclosures for Electrical Equipment.

UL 489 – Molded Case Circuit Breakers, Molded Case Switches, and Circuit Breaker Enclosures

Receiving, Storing and Protecting

Receive, inspect, handle, and store safety switches and enclosed circuit breakers according to the manufacturer's written instructions and NECA 1 Standard Practices for Good Workmanship in Electrical Construction (ANSI).

Subcontractor-supplied, stand-alone circuit breakers must have a LANL inspection plan (Form 1952) completed by LANL project personnel and receive documented LANL QPA Division receipt inspection approval prior to installation, per Exhibit H (QC-01B).  Such breakers are defined as an automatically operated electrical device designed to protect an electrical circuit from damage caused by overload or short circuit, and tested to the requirements of UL 489, Molded-Case Circuit Breakers, Molded Case Switches, and Circuit-Breaker Enclosures – except that the term does not include a circuit breaker that is (a) part of an assembly; (b) a circuit breaking device tested to UL 1077, Standard for Safety Supplementary Protectors for Use in Electrical Equipment; or (c) a circuit breaker manufactured in accordance with a QA program based on DOE O 414.1, Quality Assurance; 10CFR 839.122, Nuclear Safety Management, Quality Assurance Criteria; International Standards Organization (ISO) 9001; and/or ASME NQA-1-2008/2009a, Quality Assurance Requirements for Nuclear Facility Applications.  For (c), this typically means a supplier (including distributor) listed in the LANL IESL with a scope of supply that includes circuit breakers.

Service Conditions

Provide safety switches and enclosed circuit breakers that will perform satisfactorily in the following service conditions:

Elevation of 7,500 feet above sea level.

Maximum ambient temperature of 104 °F.

Maximum solar heat gain: 110 W/sq/ft.

EXTRA MATERIALS

Provide one spray can of touch-up paint that matches finish of switches and enclosed circuit breakers finish.

Provide a spare set of three fuses of each type and size installed in fused safety switches.

PRODUCTS

*************************************************************************************************************

Seismic: For electrical equipment that is not exempt from seismic, if Project Spec includes 26 0548.16, and if mounting and/or anchorage devices are to be used that differ from those specified in 26 0548.16, they must be described herein (in PART 2).

*************************************************************************************************************

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

*************************************************************************************************************

Seismic: Delete the following Article if electrical equipment is exempt from seismic design.

Otherwise retain Article 2.2 and edit its content based on the following:

- 	1st paragraph is for electrical equipment that doesn’t have to operate/ function post seismic event.

- 	2nd paragraph is for electrical equipment that must operate/ function after a seismic event (i.e., it’s a Designated Seismic System, or DSS).

- If paragraph applies, the “E drawings” shall also state that the electrical equipment is a Designated Safety System.

If paragraph applies, edit it in accordance with content of 26 0548.16 and/or 01 8734.

*************************************************************************************************************

  - SEISMIC PERFORMANCE REQUIREMENTS

    - The electrical equipment shall remain in place without separation of any parts when subjected to the design basis earthquake [per Section 01 8734, Seismic Qualification of Nonstructural Components (IBC)] [as represented by the seismic forces derived from the criteria indicated [on the drawings] [in Section 26 0548.16, Seismic Controls for Electrical Systems]].

    - The electrical equipment is a Designated Seismic System and, as such, it shall remain in place and be fully operational following the design basis earthquake [per Section 01 8734, Seismic Qualification of Nonstructural Components (IBC)] [as represented by the seismic forces derived from the criteria indicated [on the drawings] [in Section 26 0548.16, Seismic Controls for Electrical Systems]].

*************************************************************************************************************

Edit the following article to match project requirements. Delete if safety switches are not required for the Project

*************************************************************************************************************

SAFETY SWITCHES

Provide NRTL-listed, NEMA KS 1 Type HD safety switches with ratings and number of poles as indicated on the Drawings.

Enclosure type shall be in accordance with NEMA KS 1 and as required by the conditions of installation and use.

Each safety switch shall have an equipment ground bar.

Furnish a neutral bar for each safety switch used on a circuit that includes a grounded “neutral” conductor.

Provide auxiliary electrical interlock switches with safety switches as indicated on the Drawings or as required by the application.

Each safety switch shall have provisions for padlocking in the OFF position.

Manufacturers:  Square D “Class 3110”, Eaton type “DH”, Siemens type HF and HNF.

*************************************************************************************************************

Edit the following article to match project requirements. Delete if fused safety switches are not required for the Project

*************************************************************************************************************

Fuses

Provide NRTL-listed fuses for fusible safety switches as indicated on the Drawings, or required by the manufacturer of supplied equipment.

Size fuses within the NEC requirements based upon load supplied.

Provide a cabinet for spare fuses, if shown on drawings

Manufacturer: Bussman “LPN-RK_SP” (250 V), “LPS-RK_SP” (600 V), and “SFC-FUSE-CAB”

*************************************************************************************************************

Edit the following to match project requirements. Delete if enclosed circuit breakers are not required for the Project

*************************************************************************************************************

ENCLOSED CIRCUIT BREAKERs

Provide enclosed molded-case circuit breakers with ratings as indicated on the Drawings.

Enclosed molded-case circuit breakers shall be NRTL-listed to UL 489.

Multi-pole circuit breakers used on 480-volt or 480Y/277-volt systems shall be 600 V rated.

Enclosure type shall be in accordance with UL 50 and as required by the conditions of installation and use.

Each circuit breaker enclosure shall have an equipment ground bar.

Furnish a neutral bar for each circuit breaker enclosure used on a circuit that includes a grounded “neutral” conductor.

Provide enclosed circuit breakers with [auxiliary electrical interlock switches] [alarm switches] [shunt trips] as indicated on the Drawings or as required by the application.

Each enclosed circuit breaker shall have a permanently-installed provision for padlocking in the OFF position.

Furnish handle lock-off device that will accept a 1/4-inch padlock shackle.

Securely attach the device to the circuit breaker case; the attachment shall not depend on a friction fit or the presence of the enclosure front for the handle lock-off device to remain in place and be functional.

Manufacturer:  Square D “Class 610” enclosure with F, K, L, or M frame circuit breaker.

FRACTIONAL HORSEPOWER MOTOR Disconnects

*************************************************************************************************************

Edit to match Project requirements. Delete if not required

*************************************************************************************************************

    - Provide general purpose, Class A, manually-operated, full voltage controllers as disconnects for AC fractional horsepower motors.

    - Conform to the requirements of NEMA ICS 2 - Industrial Control Devices, Controllers, and Assemblies.

    - Enclosure type shall be in accordance with UL 50 and as required by the conditions of installation and use.

*************************************************************************************************************

Edit to match Project requirements.

*************************************************************************************************************

    - Controller shall have a thermal overload unit, red pilot light, and toggle operator.

    - Provide handle guard with provision for padlocking in the OFF position.

    - Manufacturer:  Square D “Class 2510”.

EXECUTION

*************************************************************************************************************

For electrical equipment that is not exempt from seismic, if project spec includes 26 0548.16, and if requirements associated w/ installation, testing, and inspection of mounting and/or anchorage devices differ from those requirements in 26 0548.16, they must be described herein (in Part 3).  Also, if this is applicable, identify special types of seismic-control devices required for each application using the same terminology used for those devices in Part 2.

*************************************************************************************************************

*************************************************************************************************************

Delete this section when existing construction is not affected.

*************************************************************************************************************

  - EXISTING WORK

Maintain access to each existing safety switch and enclosed circuit breaker that is to remain active.

Clean, repair, and test existing safety switches and enclosed circuit breakers to remain or be reinstalled for the project per the Field Quality Control paragraphs of this Section.

EXAMINATION

Examine surfaces to receive safety switches and enclosed circuit breakers for compliance with installation tolerances and other conditions affecting performance of the product. Do not proceed with installation until unsatisfactory conditions have been corrected.

INSTALLATION

Install safety switches and enclosed circuit breakers where indicated on the Drawings and according to manufacturer's instructions, NECA 1, and the NEC. Have the manufacturer’s installation instructions available at the construction site.

Install each safety switch and enclosed circuit breaker so the interlock bypass will be accessible.

Ground and bond safety switches and enclosed circuit breakers as required in Section 26 0526, Grounding and Bonding for Electrical Systems.

Install conduits as required in Section 26 0533, Raceways and Boxes for Electrical Systems.

Install conductors as required in Section 26 0519, Low Voltage Electrical Power Conductors and Cables.

Tighten electrical connectors and terminals to the manufacturer’s torque-tightening values labelled on equipment.  Where manufacturer's torque values are not indicated, use those specified in UL 486A.

*************************************************************************************************************

Edit the following to match project requirements. Delete if fused safety switches are not required for the Project.

*************************************************************************************************************

Install fuses in fusible safety switches as indicated on the Drawings or as required to match installed motor or load characteristics. Apply adhesive tag on inside door of each fused switch indicating NEMA fuse class and size installed.

Install spare fuse cabinet in the main electrical room, if shown on drawings.

IDENTIFICATION

Identify safety switches and enclosed circuit breakers and install warning signs and arc-flash warning labels as required in Section 26 0553, Identification for Electrical Systems.

Provide permanent indication of trip rating of each enclosed circuit breaker or fuses installed in each enclosed switch that will be visible without opening cover and exposing energized conductors.

FIELD QUALITY CONTROL

Clean interior and exterior of safety switches and enclosed circuit breakers.

Verify that ratings for safety switches and enclosed circuit breakers match values indicated on the Drawings.

Verify proper torque of accessible bus connections and mechanical fasteners after installing safety switches and enclosed circuit breakers.

Witness torqueing of electrical terminations while the work is being performed.  Ensure witness mark is placed on terminations.

*************************************************************************************************************

Edit the following to match project requirements. Delete if formal electrical acceptance testing is not required; refer to LANL Master Specification Section 26 0813.

*************************************************************************************************************

Coordinate inspections and tests with those required by Section 26 0813, Electrical Acceptance Testing.

After completing installation, cleaning, and testing, touch up scratches and mars on finish to match original finish.

END OF SECTION

****************************************************************

Do not delete the following reference information.

****************************************************************

THE FOLLOWING REFERENCE IS FOR LANL USE ONLY

This project specification is based on LANL Master Specification Section 26 2816 Rev. 4, dated May 11, 2017.