Section 31 2000 
Earth Moving

  - ************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 11 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Civil POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

  - ************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

      - ***************************************************************************************

      - The following paragraphs are designer-choice. Include paragraphs based on project-scope. Typically potholing, excavation and trenching activities involve backfilling. Typically backfilling involves soil compaction and testing.

      - ***************************************************************************************

Potholing.

Grading: Clear, excavate topsoil, grade and dispose of materials at site.

Excavation: Excavate, place, and compact earth at site.

      - ***************************************************************************************

      - Tracer wire and test station(s) are required when burying cast iron, ductile iron, or non-metallic piping. Selection here updates related Articles/paras/subparas in remaining Section.

      - ***************************************************************************************

Trenching: Excavate trenches for utilities and install ​​​​<< tracer wire/; or  None - N/A>>​​​​​identification tape.

Backfilling.

Soil compaction and testing.

RELATED REQUIREMENTS

Section << 01 3300 - Submittal Procedures>>

Section << 01 5705 - Temporary Controls and Compliance Requirements>>

REFERENCE STANDARDS

29 CFR 1926 - Safety and Health Regulations for Construction.

ASTM D1556/D1556M - Standard Test Method for Density and Unit Weight of Soil in Place by Sand-Cone Method.

ASTM D1557 - Standard Test Methods for Laboratory Compaction Characteristics of Soil Using Modified Effort (56,000 ft-lbf/ft3 (2,700 kN-m/m3)).

ASTM D2216 - Standard Test Methods for Laboratory Determination of Water (Moisture) Content of Soil and Rock by Mass.

ASTM D4318 - Standard Test Methods for Liquid Limit, Plastic Limit, and Plasticity Index of Soils.

ASTM D4718/D4718M - Standard Practice for Correction of Unit Weight and Water Content for Soils Containing Oversize Particles.

ASTM D6913/D6913M - Standard Test Methods for Particle-Size Distribution (Gradation) of Soils Using Sieve Analysis.

ASTM D6938 - Standard Test Methods for In-Place Density and Water Content of Soil and Soil-Aggregate by Nuclear Methods (Shallow Depth).

ASTM D7928 - Standard Test Method for Particle-Size Distribution (Gradation) of Fine-Grained Soils Using the Sedimentation (Hydrometer) Analysis.

LANL PERFORMED WORK

      - ***************************************************************************************

      - The following paragraphs are designer-choice. Retain the following three paragraphs for potholing, grading, excavation, trenching or backfilling.

      - ***************************************************************************************

Obtain excavation/soil disturbance permit for Subcontractor.

Mark location of known underground utilities and issue the excavation/soil disturbance permit.

Document new and existing utility locations. LANLUI Mapping and Locating Group (LANL access only) will survey locations of new and existing exterior utilities and infrastructure. Refer to Article << 3.8; or  _______>>, Documenting Utility Location.

      - ***************************************************************************************

      - Retain the following paragraph for potholing.

      - ***************************************************************************************

Locate utility shut-off points prior to potholing.

      - ***************************************************************************************

      - Retain the following paragraph if tracer wire is used on the project.

      - ***************************************************************************************

Perform an electrical continuity test for each run of tracer wire.

DEFINITIONS

For definitions and acronyms, refer to COE Glossary of Terms.

Mechanical Excavation: Use of backhoes, jackhammers, trenchers, and similar powered digging machines; excludes vacuum excavators that are equivalent to hand digging.

Utility and Pipe: Any active or inactive buried pipe, duct, conduit, or cable in a primary or secondary utility system.

      - ***************************************************************************************

      - Retain the following Article Action Submittals and submittals if the project-scope involves excavation, trenching, backfilling, soil compaction and testing.

      - ***************************************************************************************

ACTION SUBMITTALS

Submit the following per Section << 01 3300 - Submittal Procedures>>:

        - ******************************************************************************

        - The following subparagraphs are designer-choice. Retain based on project-scope.

        - ******************************************************************************

Certifications from an independent testing laboratory that pipe bedding materials meet the requirements of this Section.

        - ******************************************************************************

        - The following subparagraph is activated automatically based on selections made in PART 2 Article Materials for backfill and base course.

        - ******************************************************************************

Certifications from an independent testing laboratory that base course materials, crushed stone or crushed or screened gravel meet the requirements of this Section.

Test reports of field-testing of material compaction.

Test reports of field-testing of tracing wire continuity.

Catalog data on identification tape​​​<< , tracing wire test station, and tracer wire; or  None - N/A>>​​​​.

QUALITY ASSURANCE

      - ***************************************************************************************

      - Retain the following paragraph if tracer wire is used and/or soil compaction and testing is in project-scope.

      - ***************************************************************************************

When work or portions of work of this Section requires testing, notify LANL Subcontractor Technical Representative (STR) 48 hrs in advance of testing.

      - ***************************************************************************************

      - Retain the following paragraph if tracer wire is used and/or soil compaction and testing is in project-scope.

      - ***************************************************************************************

Ensure compacted fills are tested in accordance with Article ​<< 3.10; or  _______>>​, Soil Compaction and Testing and in compliance before proceeding with placement of next lift.

      - ***************************************************************************************

      - Retain the following paragraph for potholing, grading, excavation, trenching or backfilling.

      - ***************************************************************************************

Do not begin any groundbreaking, fill, or soil disturbance and transfer until known utilities have been marked, and an excavation/soil disturbance permit has been issued to Subcontractor.

      - ***************************************************************************************

      - Retain the following paragraph for potholing, excavation, or trenching.

      - ***************************************************************************************

Comply with OSHA <<29 CFR 1926>>, Subpart P for excavation and trenching operation.

Maintain a copy of the following on site:

        - ******************************************************************************

        - The following subparagraphs are designer-choice. Retain based on project-scope.

        - ******************************************************************************

Excavation/Soil Disturbance Permit package

Potholing plan

Competent person excavation logs

Test reports.

Perform pre-job briefing of Permit and associated safety and hazard documentation with workers performing the work.

Ensure that engineering controls and required Personnel Protective Equipment (PPE) are used by workers during work activities to maintain safety, especially during jack hammering.  Breaking surface blacktop, curbs and gutters with a jackhammer does not require dielectric PPE, provided locates have been performed and the LANL STR is confident no other unexposed utilities are present in the surface concrete, blacktop, curb, gutter or sidewalk to be removed.

Review and maintain the work within the established boundaries established by the permit.

      - ***************************************************************************************

      - Retain the following Article Site Conditions if the project-scope involves potholing or backfilling.

      - ***************************************************************************************

SITE CONDITIONS

Areas to be backfilled are free of debris, snow, ice, and water, and surfaces are not frozen.  Backfill material shall be in a thawed state before being placed, mixed, or compacted.  Compensatory measures can be used and should be described in a cold weather protection plan and approved by the LANL STR.

PART 2 - PRODUCTS

    - **********************************************************************************************

      - Retain the following Article Materials if the project-scope involves  grading or backfilling.

    - **********************************************************************************************

MATERIALS

General: Unless otherwise noted the existing site soils shall be used for fill and backfill materials.  If the on-site soils are found by laboratory test to be unsuitable for use contact the LANL STR.  Any additional fill material used must conform to the applicable requirements of this Section.

      - ***************************************************************************************

      - The following paragraph is a designer-choice.

      - ***************************************************************************************

Topsoil

Excavated soil material, graded free of roots, rocks larger than 1 inch subsoils, and debris.

      - ***************************************************************************************

      - The following four paragraphs are designer-choice. Specify all earthen materials (soil and aggregate) to be used for fill or backfill in the paragraphs below. Note, paragraph Fill and Backfill Material below is activated automatically if potholing is part of project-scope.

      - ***************************************************************************************

Fill and Backfill Material

Material consisting of non-plastic granular soils free of organic or other deleterious materials having a maximum particle size of 2 inches.

All borrow and fill material shall be provided by the Subcontractor.  The LANL STR in consultation with LANL Utilities and Institutional Facility (UI) Group may approve a borrow/spoils area.

Engineered Backfill

General:  Excavated material may be used for fill and/or backfill under sidewalks and site.  Use only clean approved materials for engineered fill and/or backfill under buildings and structures.  Site materials which have the required properties may be used subject to the approval of the LANL STR.  If sufficient materials are not available at the site or if the site materials do not have the specified properties, materials from off-site borrow areas will be used.  Off-site materials may be mixed with on-site materials in the proportions necessary to meet the requirements of this Section.  All arrangements necessary for the use of borrow areas are the sole responsibility of the Subcontractor.  Stripped topsoil shall not be used in structural backfill.

Laboratory Testing:  Perform appropriate and specified laboratory tests as necessary to ensure that soil materials proposed for use on this project meet all specified requirements.  Provide a moisture-density curve for each material proposed for use as engineered fill.

Fill:  Engineered fill required to raise the building areas and backfill around and above structures shall be clean material, free of vegetation, debris and other deleterious materials and shall meet the following requirements as determined by << ASTM D6913/D6913M; or  ASTM D7928>> except as otherwise approved by the LANL STR.

| Sieve Size | Percent Passing |
| --- | --- |
| 2 inch | 100 |
| 1/4 inch | 40 - 100 |
| No. 200 | 25 - 45 |

        - Fill shall have a plasticity index (P. I.) of not more than 10.  Testing shall be in conformance with <<ASTM D4318>>.

Base Courses

Provide base course and aggregate composed of materials consisting of crushed stone, crushed or screened gravel, sand, RAP, or a combination of such materials. Provide base course and aggregate free from vegetable matter and other deleterious materials, including silt and clay balls. Ensure that at least 50 percent of the materials on or above the No.4 sieve have at least two fractured faces. Maximum Liquid Limit of 25 and maximum Plasticity Index of 6, per <<ASTM D4318>>. When using RAP the sieve size may be increased to 1.5 inches passing 100 percent and in accordance with <<ASTM D4718/D4718M>> in conjunction with <<ASTM D1557>>.

Base course aggregate shall conform to:

| Base Course Gradation |  |
| --- | --- |
| Sieve Size | Percent Passing |
| 1.0 inch | 100 |
| 3/4 inch | 80 - 100 |
| No. 4 | 30 - 60 |
| No. 10 | 20 - 45 |
| No. 200 | 3 - 10 |

Crushed Stone

Provide crushed stone and/or crushed or screened gravel free of any organic or deleterious substance and having 100 percent passing 1 inch sieve and 0 percent passing the 3/8 inch sieve.

      - ***************************************************************************************

      - Retain the following Article if the project-scope involves trenching.

      - ***************************************************************************************

UTILITY TRENCH BED AND FILL MATERIALS

Bedding: Provide clean sand for pipe bedding material free of any organic or deleterious substance and having 100 percent passing 3/8 inch sieve and 0-10 percent passing No. 100 sieve.

Fill: Provide fill and backfill material consisting of non-plastic granular soils free of organic or other deleterious materials having a maximum particle size of 2 inches.

Warning Tape:

Manufacturer: Bradley, Seton Name Plate Co., etc.

Use non-detectable plastic warning tape consisting of high visibility, color-coded, continuously printed, inert fiber reinforced polyethylene for direct burial service.

Provide tape meeting the following criteria:

Minimum overall thickness: 4.0 mils

Minimum tensile strength: 1500 psi

Width: 6 inches

Refer to LANL Civil Standard Detail ST-G30GEN-4, Earthwork Utilities Tables for warning tape color.

      - ***************************************************************************************

      - Retain the following two paragraphs if tracer wire is used on the project. Tracer wire and test station(s) are required when burying cast iron, ductile iron, or non-metallic piping. Refer to LANL Civil Standard Detail ST-G30GEN-3 for tracer wire detail.

      - ***************************************************************************************

Tracer Wire: #12 AWG copper clad steel, insulation of HDPE minimum 30 mil thickness rated for direct burial.  Insulation color shall meet the AWPA color code for buried utilities.

Manufacturer: Copperhead Industries, Pro-Line Safety Products.

Tracer Wire Test Station

Manufacturer: C.P. Test Services, Model-Glenn Test Station

Test Station: Plastic Pipe, cast iron cover, 2-point terminal box.

PART 3 - EXECUTION

    - **********************************************************************************************

      - Retain the following Article Inspection if the project-scope involves potholes that are to be backfilled, or backfilling activities.

    - **********************************************************************************************

INSPECTION

Verify stockpiled fill to be reused is approved by LANL STR.

Verify areas to be backfilled are free of debris, snow, ice, and water, and surfaces are not frozen.

      - ***************************************************************************************

      - Retain the following Article Protection if the project-scope involves grading, excavation or trenching or when construction activities require protection measures.

      - ***************************************************************************************

PROTECTION

Preserve staking, marking, or other designation until the designation is no longer needed for permitted work. If marking is removed or no longer visible, notify LANL STR. The LANL STR will contact LANLUI Mapping and Locating Group (LANL access only) to revalidate the excavation/soil disturbance permit by locating and marking the utility again.

Protect existing structures from equipment and vehicular traffic.

Maintain excavation free of standing water.

Notify LANL STR of unexpected subsurface conditions and discontinue affected work in area until notified to resume work.

Protect bottom of excavations and soil adjacent to and beneath foundations from frost.

Grade top perimeter of excavation to prevent subsurface water run-off into excavation.

Barricades shall be erected around the excavation area before beginning work activities to prevent accidental entry into the area.

Protect disturbed soils, drainage ways and watercourses against soil erosion and sedimentation by employing Best Management Practices (BMPs) as identified in excavation permit review (EXID (LANL access only)) comments, shown on the drawings or identified in the Storm Water Pollution Prevention (SWPP) Plan and approved by LANL STR. Remove any temporary BMP’s at the close of the project.

Approved BMPs shall be in place per SWPP plan before soil-disturbing work begins.

Stabilize all disturbed areas.

      - ***************************************************************************************

      - Retain the following Article Preparation if the project-scope involves potholing, grading, excavation, trenching or backfilling.

      - ***************************************************************************************

PREPARATION

Identify required contours and data.

Notify LANL STR 15 working days prior to startup of construction to have LANL UI Mapping and Locating Group (LANL access only) identify known underground utilities and stake and flag locations. If a conflict exists between location of such obstacles and proposed work, promptly notify LANL STR and arrange for relocations. Proceed in same manner if a rock layer or any other unforeseen conditions encountered underground make changes advisable.

      - ***************************************************************************************

      - Retain the following paragraphs if the project-scope involves backfilling.

      - ***************************************************************************************

When necessary, compact subgrade surfaces to density requirements for backfill material. Remove unsuitable and unstable subgrade material.

In rock cuts, the top of the rock cut elevation shall be considered to be the same as top of subgrade. Base course may be placed directly on top of competent rock without further processing of the rock (i.e. scarify and compaction) provided that pockets in the rock are graded to drain before base course is placed.  Any fill placed on top of competent rock needed to bring the top of subgrade to required elevation shall be compacted in accordance with subgrade requirements.

      - ***************************************************************************************

      - Retain the following Article if the project-scope involves excavation or trenching or when construction activities require working within 5 feet of utilities.

      - ***************************************************************************************

WORKING WITHIN 5 FEET OF UTILITIES

Stop work and notify the LANL STR when an unmarked utility is encountered. The LANL STR shall contact LANL UI Mapping and Locating Group (LANL access only) so the site can be re-examined by Utility Locators.

If an underground utility is damaged or severed during excavation, immediately notify LANL STR. LANL STR will take immediate action to secure the area, notify the agency responsible for the utility so that the damaged section can be isolated, repairs initiated and other notifications made as required.

Whenever practical, utilities shall be de-energized, isolated, and tagged-out.  The decision not to de-energize shall be made by LANL STR and Facility Operations Manager, as appropriate.

Do not use mechanical excavating equipment within 5 feet of a marked, non-potholed utility.  Mechanical excavation may commence within 5 feet of the underground utility only after the utility has been potholed, exposed, and well-marked and the Subcontractor is confident that there are no unexposed utilities in the excavation area.

Exception: Use of mechanical excavating equipment may be used where known utility line depths and/or site conditions exceed limitations of hand or vacuum excavation. For purposes of this exception, excavate pothole perpendicular to surface locate markings for 2 feet on each side of marking to a predetermined depth. Mechanical excavation may proceed to within 18 inches of bottom of potholes under this exception. When deemed necessary, Subcontractor will ask LANL STR to contact LANL UI Mapping and Locating Group (LANL access only) for consultation, checking of existing locate marks and remarking.

Accomplish mechanical excavation at a distance no closer than 18 inches vertically and horizontally to potholed non-fully-exposed utility lines.

Fully-exposed underground utilities shall be protected, supported, or removed and reinstalled as necessary to protect workers and the utility.

If approved by LANL STR, powered excavation equipment may be used closer than 18 inches to any fully-exposed utilities provided that these are marked/indicated with a prominent, tall flag-on-pole, plank, or other highly visible object so the equipment operator can clearly see their locations and avoid contact. Prior to such excavating, mark and obtain approval using Attachment 1, Utility Protection Plan Form.  Subcontractor shall complete the Utility Protection Plan and clearly indicate the limits of excavation/locates, utilities located, each pothole location, and description of installed marking/flagging measures.  More than one form may be required for clarity.

Take care while hand excavating adjacent to utility line since hand tools such as shovels, picks, and digging bars can damage the utility line.

During machine excavation, have a spotter in place to actively monitor the positioning of the equipment.

Hand-excavate obstructions (i.e., guy wires, anchors, bollards, fence posts, etc.) to be removed to determine their relationship to existing marked utilities prior to removal.

      - ***************************************************************************************

      - Retain the following Article if the project-scope involves potholing.

      - ***************************************************************************************

POTHOLING

Prior to potholing, the LANL STR will notify LANL UI Group to locate utility shut-off points. LANL UI Group will ensure the shut-off points are field verified and determined operable.

Pothole where existing buried utility lines are inside, or within 5 feet outside of excavation permit boundary limit.

Accomplish potholing by hand excavation or through use of vacuum potholing equipment.  The use of vacuum potholing equipment is not permitted within the boundary of a Potential Release Site (PRS).

Pothole at vertical and horizontal utility angle points, at excavation boundary limit, and as needed. Provide additional pothole where utility depths are unknown or are in sloped work areas where utility depths may vary.

When unknown utility lines are marked and hand or vacuum excavation has gone 1 foot deeper than required and 3 feet to the left and right of a locate mark without finding the utility, stop excavating and contact the LANL STR for consultation and remarking.

Manholes or valve boxes may be used as a pothole to verify depths and locations of utilities.

Parallel Utilities: Pothole at 50 feet intervals where existing utilities, parallel excavation and existing lines are located up to 6 feet outside excavation boundary.  Hand or vacuum excavate non-conductive direct burial lines within 2 feet of excavation boundary along their entire length adjacent to excavation boundary, or pothole at 5 feet intervals.

Backfill potholes to original or better than condition. For backfill material, refer to Article Materials, paragraph << 2.1.C; or  _______>>Fill and Backfill Material.

      - ***************************************************************************************

      - Retain the following Article if the project-scope involves grading.

      - ***************************************************************************************

GRADING

Excavate topsoil from areas to be further excavated or regraded, and stockpile topsoil on site in area designated by LANL STR. Topsoil may be used on areas to receive landscaping and seeding.

Remove vegetation, debris, unsatisfactory soil materials, and obstructions from ground surface prior to grading.  Properly dispose of material in accordance with Section << 01 5705 - Temporary Controls and Compliance Requirements>>.

Uniformly grade areas within limits of grading under this Section, including adjacent transition areas.

Match final grade in seeded and unpaved areas to match Drawing finish contours.

Construct the subgrade surface elevation to a tolerance of plus or minus 0.1 foot  from the specified grade and plus or minus 0.05 foot of the typical cross section, except unlined drainage ditch flow lines shown on Drawing are allowed plus or minus 0.2 foot.

Construct the base course to the design depth required and the final surface to a tolerance of plus or minus 0.04 foot within 10 feet.

Make changes in grade gradual.  Blend slopes into level areas. Prepare finish grade to accept seeding by hand raking or as designated.

Remove surplus excavated materials from the site. Movement and proper disposal of materials from the site shall be in accordance with Section << 01 5705 - Temporary Controls and Compliance Requirements>>.

      - ***************************************************************************************

      - Retain the following Article if the project-scope involves excavation or trenching.

      - ***************************************************************************************

EXCAVATING AND/OR TRENCHING

      - ***************************************************************************************

      - Specify project specific requirements.  Refer to LANL Civil Standard Detail ST-G30GEN-4 for trenching detail.

      - ***************************************************************************************

Excavate and trench subsoil as required for Work.

Cut trenches sufficiently wide to enable installation of utilities to allow inspection. Trenches shall be benched, sloped, or shored to meet OSHA <<29 CFR 1926>> Subpart P, in particular Appendix A for Soil Classification and Appendix B for Sloping and Benching requirements. Refer to trench detail on LANL Civil Standard Detail ST-G30GEN-4, Earthwork Utilities Tables for minimum trench widths.

Do not interfere with normal 45 degree bearing splay of a structure foundation during excavation work.  When excavating near or under a foundation, a New Mexico Licensed Professional Engineer shall approve a support system to stabilize the structure or determine that excavation work will not pose a hazard.

Hand trim excavation and leave free of loose matter.

Remove lumped subsoil, boulders, and rock.

Correct errors in excavation.

Take proper precaution, such as shoring, sloping, or using a trench box when working in a trench or excavation.  Provide a person who is trained and knowledgeable of soil conditions and safety requirements to make safety determinations.

Evaluate excavations 4 feet or deeper (or other excavation where worker exposure can be reasonably anticipated) daily and document by a designated competent person before workers are permitted to enter the excavation.  Documented inspections on an excavation condition log.

When an oxygen deficiency or hazardous atmosphere could be reasonably expected in trenches over 4 feet in depth, such as excavating near roadways, lift stations, sewer/gas lines, etc., the excavation shall be tested with a calibrated, intrinsically safe monitoring device before workers are allowed to enter the excavation.  If the atmosphere test indicates hazardous, then do not enter the excavation or if chemical hazards exist or are created within the excavation, stop work immediately and contact the LANL STR.

Excavation boundaries shall be adequately marked and barriers installed to avoid inadvertent entry. Excavations that present a possibility of a worker falling to a lower level shall be evaluated by a designated Fall Protection Competent Person for necessary fall protection requirements.

      - ***************************************************************************************

      - Retain the following Article if the project-scope involves potholing, grading, excavation, trenching or backfilling.

      - ***************************************************************************************

DOCUMENTING UTILITY LOCATION

Do not cover new or exposed existing utilities until LANL UI Mapping and Locating Group (LANL access only) has verified that utility locations have been documented by the use of GPS in compliance with LANL standard reference system.

Subcontractor Responsibility: Notify LANL STR 5 working days in advance that new and exposed utilities will be ready for location verification.

LANL STR Responsibility: Notify LANL  UI Mapping and Locating Group (LANL access only) at 665-1051 immediately after being notified by Subcontractor.

      - ***************************************************************************************

      - Retain the following Article if the project-scope involves backfilling.

      - ***************************************************************************************

BACKFILLING EXCAVATIONS/trenches

      - ***************************************************************************************

      - Specify project specific requirements.

      - ***************************************************************************************

Backfill and fill areas to contour lines and elevations shown on the Drawings.

Backfill and fill systematically.

Do not place backfill or fill material over frozen, wet, or spongy subgrade surfaces, including surfaces containing frost or ice.  Backfill material shall be in a thawed state before being placed, mixed, or compacted.

Recondition, reshape and recompact areas that are damaged by freezing.

Place backfill and fill materials in continuous layers not exceeding 8 inches in loose depth.

Before compacting, moisten or aerate each layer as necessary to provide the optimum moisture content.

Compact each layer to required percentage of maximum density for the area.

Compact layers uniformly before a succeeding layer is placed.

Do no disturb or damage adjacent structures during compaction.

      - ***************************************************************************************

      - Retain the following paragraph and subparagraphs within it when backfilling against structures.

      - ***************************************************************************************

Backfill against structures as follows:

Do not place backfill against structure walls prior to verifying the concrete has been properly cured and is of required strength to resist stresses due to backfill.

Take care to prevent wedging action of backfill against structures by carrying the material uniformly around the structures to approximately the same elevation in each lift.

When unbalanced pressures are likely to develop on walls:

Continuously monitor for displacements,

Erect shoring to counteract imbalance, if required, and

Leave shoring in place until LANL STR approves its removal.

      - ***************************************************************************************

      - Retain the following paragraph if the project-scope involves trenching/utility trenches.

      - ***************************************************************************************

Utility Trenches

Support pipe and conduit during placement of concrete or fill.

        - ******************************************************************************

        - Retain the following three subparagraphs if tracer wire is used on the project.

        - ******************************************************************************

Install tracer wire (no splices) directly above buried non-metallic pipes and conduits, ductile iron, and cast iron pipes and terminate at grade within a test station or valve box. If the tracer wire can be continuous, do not cut the wire in a test station or valve box but leave as a slack, uncut loop. Tracer wire shall not contact underground piping.

Visually inspect tracer wire prior to backfilling to ensure wire has not been nicked or cut, and that continuous unspliced wire runs between test station terminals.

Prior to utility tie-ins, perform an electrical continuity test for each run of tracer wire after backfill is complete. The LANL STR will notify LANL UI Mapping and Locating Group (LANL access only) to verify tracer wire continuity and GPS new and existing utility lines.

Install non-detectable plastic warning tape 12 inches below finish grade and directly above buried utility pipe or conduit. Visually inspect warning tape prior to backfilling to ensure tape is continuous and not cut.

      - ***************************************************************************************

      - Retain the following Article if the project-scope involves soil compaction and testing.

      - ***************************************************************************************

SOIL COMPACTION AND TESTING

Control soil compaction during construction to provide the minimum percentage of density specified for each area as determined according to <<ASTM D1557>>.  <<ASTM D1557>> Method A is the preferred Method with Methods B and C being acceptable based on the material gradation with oversize correction adjustments.

Where subgrade or layer of soil material must be moisture-conditioned before compacting, uniformly apply water to surface of subgrade or layer material to prevent free water appearing on surface during or subsequent to compacting operations.

Remove and replace, or scarify and air dry, soil material that is too wet to permit compacting to the specified density.

The allowable percent variation from optimum moisture is plus or minus 2 percent.

The subparagraphs below identify location and compaction required as a percentage of maximum density and optimum moisture measured using <<ASTM D1557>>.

        - ******************************************************************************

        - Retain the following subparagraphs based on project-scope.

        - ******************************************************************************

Compact fill in 8 inch lifts that will be beneath concrete and asphalt structures to 95 percent of maximum density.

Compact fill in 8 inch lifts that will be beneath unpaved areas to 90 percent of maximum density.

Compact new aggregate base course that will be beneath asphalt structures to 95  percent of maximum density.

Compact pipe bedding to 90​​ percent of maximum density.

Subcontractor shall employ an AASHTO resource (formerly AMRL) accredited independent testing agency to perform field testing of installed products to include compaction and test samples that shall verify quality control requirements and is responsible for the following:

Verify fill material to be placed is within the stated specifications, and laboratory testing is complete.

Verify that moisture-density relationship, <<ASTM D1557>>, for each soil type to be placed is completed.

Determine field density of in-place material in accordance with any of the following methods:

Nuclear Method, <<ASTM D6938>>, or

Sand-Cone Method, <<ASTM D1556/D1556M>>.

Determine field moisture content in accordance with either of the following methods:

Nuclear Method, <<ASTM D6938>>, or

Laboratory Determination, <<ASTM D2216>>.

Frequency of Tests

          - **********************************************************************

          - Specify location and frequency of testing.

          - **********************************************************************

One test per << 2000; or  _______>> square feet for each lift of compacted fill material or fraction thereof, but not less than << 3; or  _______>> tests per 8 inches maximum for each lift.

One test per << 50; or  _______>> linear feet of trench per 8 inches maximum for each lift.

END OF ​<< MAIN ; or  None - N/A>>​ SECTION​<< ; ATTACHMENT FOLLOWS; or  None - N/A>>​

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 31 2000, REV. 11, DATED APRIL 15, 2026.

    - **********************************************************************************************

      - 31 2000 Attachment 1 is located here (copy and paste link in a browser to download file): http://engstandards.lanl.gov/specs/31-2000-Att1.docx. Attach or include immediately after this section so it appears to be an attachment.

    - **********************************************************************************************

31 2000 Attachment 1 - UTILITY PROTECTION PLAN FORM