Section 33 0513 
Manholes and Structures

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 7 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Civil POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable specification sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

  - *************************************************************************************************************

PART 1 - GENERAL

    - **********************************************************************************************

      - Refer to LANL Civil Standard Detail ST-G3030-3 for storm water manhole detail and LANL Civil Standard Detail ST-G3020-1 for sanitary sewer manhole detail.

    - **********************************************************************************************

SECTION INCLUDES

      - ***************************************************************************************

      - The following paragraphs are designer-choice. Retain the first paragraph when manholes are in project-scope. Retain the second paragraph when tanks are in project-scope.

      - ***************************************************************************************

Precast concrete manhole sections and manhole frame and cover castings for use in ​​​​​​<< Click to select sanitary sewer/storm water system(s) from drop down menu;  sanitary sewer; and  storm water>>​​​​​​ systems.

​​​​​​​<< Click to select tank material from drop down menu;  Precast concrete;  Fiberglass; and  Polyethylene (HDPE)>>​​​​​​​ septic and holding tank sections, access frames and covers, and monitoring systems for use in sanitary sewer systems.

RELATED REQUIREMENTS

Section << 01 2500 - Substitution Procedures>>

Section << 01 3300 - Submittal Procedures>>

Section << 03 3053 - Miscellaneous Cast-in-Place Concrete>>

Section ​<< 33 3200 - Wastewater Utility Pumping Stations>>​

REFERENCE STANDARDS

ASTM A48/A48M - Standard Specification for Gray Iron Castings.

ASTM C478/C478M - Standard Specification for Circular Precast Reinforced Concrete Manhole Sections.

ASTM C923/C923M - Standard Specification for Resilient Connectors Between Reinforced Concrete Manhole Structures, Pipes, and Laterals.

ASTM C1227 - Standard Specification for Precast Concrete Septic Tanks.

ASTM C1478/C1478M - Standard Specification for Storm Drain Resilient Connectors Between Reinforced Concrete Storm Sewer Structures, Pipes, and Laterals.

ASTM D1557 - Standard Test Methods for Laboratory Compaction Characteristics of Soil Using Modified Effort (56,000 ft-lbf/ft3 (2,700 kN-m/m3)).

LANL PERFORMED WORK

LANL Utilities and Infrastructure (UI) group will tie into existing systems which include sanitary sewer lines, holding tanks, septic tanks, treatment plants, lift stations, and sewer manholes.

LANL Subcontract Technical Representative (STR) will coordinate required inspections and tie-ins.

      - ***************************************************************************************

      - Retain the following two paragraphs when tanks are in project-scope.

      - ***************************************************************************************

LANL STR will coordinate through LANL Water Quality Group (EPC-CP) for inspection of septic tank and holding tank for compliance by New Mexico Environmental Department (NMED).

Application for septic tank or holding tank construction permit to NMED through LANL EPC-CP​​.

ACTION SUBMITTALS

Submit the following per Section << 01 3300 - Submittal Procedures>>:

Certifications: Furnish copies of materials certificates certifying that each material item complies with, or exceeds, specified requirements.

        - ******************************************************************************

        - The following two submittals apply to tanks. Retain based on applicability when tanks are in project-scope.

        - ******************************************************************************

NMED approved septic tank list certification number.

Level alarm system product data and installation instructions for holding tank.

        - ******************************************************************************

        - Retain the following submittal when manholes for sanitary sewer systems are in project-scope.

        - ******************************************************************************

Manhole exfiltration test results within 5 working days of successful test.

PART 2 - PRODUCTS

    - **********************************************************************************************

      - The following Article Product Options and Substitutions is a designer-choice Retain when project allows for substitutions.

    - **********************************************************************************************

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section << 01 2500 - Substitution Procedures>>.

MATERIALS

      - ***************************************************************************************

      - Retain the following paragraph when manholes are in project-scope.

      - ***************************************************************************************

Provide precast concrete manhole sections (base barrel sections, risers and conical/eccentric tops, flat slab tops, grade rings, etc.) per <<ASTM C478/C478M>>.

Concrete: Compressive strength of << 4000 psi; or  _______>> for 28 days.

        - ******************************************************************************

        - Retain the following subparagraph when sanitary sewer manholes are in project-scope.

        - ******************************************************************************

Sanitary Sewer Manhole: Provide ​<< 4 foot; or  6 foot>>​ diameter manhole. Diameter furnished is dependent on depth, pipe size, number of inlet pipes, and if drop manhole.

      - ***************************************************************************************

      - The following two paragraphs apply to tanks. Retain based on material selected when tanks are in project-scope.

      - ***************************************************************************************

Provide approved precast concrete septic tanks per <<ASTM C1227>>.

Concrete: Compressive strength of ​​<< 4000 psi; or  _______>>​​ for 28 days.

Provide approved fiberglass or polyethylene (HDPE) septic or holding tanks per the Drawings.

Polyethylene/fiberglass tanks: Tanks shall have side reinforcements specifically designed to withstand the stress, when empty, from soil and surcharge loadings.

      - ***************************************************************************************

      - Retain the following paragraph when manholes are in project-scope.

      - ***************************************************************************************

Manhole Frame and Cover

Provide castings true to patterns in form and dimension, and free from pouring faults, sponginess, cracks, blowholes, or other defects in locations affecting their strength and value for the service intended.  Provide castings with fillets at angles with sharp and true risers.

Provide castings conforming to <<ASTM A48/A48M>>, Class 30B.

Machine or grind bearing surfaces of the frames and covers to furnish a uniform, flat, non-rocking seat for the cover on the frame.

          - **********************************************************************

          - Retain the applicable subparagraph depending on the type of manhole in project-scope.

          - **********************************************************************

Provide cover with the word “Sewer” cast on the sewer manhole cover.

Provide cover with the word “Storm Drain” cast on the storm water manhole cover.

      - ***************************************************************************************

      - Retain the following paragraph when precast concrete manholes and/or tanks are in project-scope.

      - ***************************************************************************************

Sealing Gasket (precast manhole or tank sections): Mastic Gasket as manufactured by RAM-NEK or Kent Seal.

      - ***************************************************************************************

      - Retain the following paragraph when tanks are in project-scope.

      - ***************************************************************************************

Septic or Holding Tank Access Ports: Install three foot diameter corrugated metal pipe (CMP) riser over tank inspection/access port. CMP shall extend one foot above finish grade. Provide 3/16 inch steel plate cover 2 inches larger in diameter than CMP, with brackets to fit CMP and two handles welded to plate. Provide a 6 inch by 6 inch hinged opening, with handle, in the steel top plate cover for access to pump the tank without having to remove entire cover.

      - ***************************************************************************************

      - Retain the following paragraph when precast concrete manholes and/or tanks are in project-scope.

      - ***************************************************************************************

Pipe Waterstop: Provide waterstop grouting ring for watertight connection between manhole or precast concrete tank wall and pipe, resilient rubber with stainless steel bands. Conform to physical property requirements of <<ASTM C923/C923M>> and <<ASTM C1478/C1478M>>. Manufacturer: Trelleborg – NPC – Waterstop Grouting Ring with NPC – Corrugated Pipe Adapter as applicable.

PART 3 - EXECUTION

INSTALLATION

Compact soil foundations for manhole base or tanks to a density of 95 percent of the maximum density per <<ASTM D1557>>.  Compaction shall be minimum 1 foot beyond perimeter of concrete base and shall be a minimum of 1 foot in depth.

Invert elevation of pipes entering or exiting manhole or tanks and interior inverts shall not vary more than 0.05 foot from the elevations shown on the Drawings.

Provide concrete per Section << 03 3053 - Miscellaneous Cast-in-Place Concrete>> for formed-in-place foundations or bases, concrete shelves, and pipe supports.

      - ***************************************************************************************

      - Retain the following paragraph when manholes are in project-scope.

      - ***************************************************************************************

Depending on size of pipe, make connections to existing and new manholes by either core drilling through manhole wall (perform for new precast units), or carefully chipping wall segment. Take care to avoid unnecessary damage to manhole surfaces or walls.

      - ***************************************************************************************

      - Retain the following paragraph when precast concrete manholes and/or tanks are in project-scope.

      - ***************************************************************************************

Install waterstop grout ring before placing high strength, non-shrink grout around piping in concrete manhole or tank wall. Coat interior surface of concrete manhole or tank to provide watertight seal, exclude storm drain manhole.

      - ***************************************************************************************

      - Retain the following paragraph when HDPE/fiberglass tanks are in project-scope.

      - ***************************************************************************************

Piping connecting to a polyethylene/fiberglass tank shall of the same or compatible material as the tank. Connections shall be waterproof and per tank manufacturer’s instructions.

Set the manhole and septic/holding tank level and plumb.  Tanks shall have an anti-flotation device installed as shown on the Drawings and per manufacturers suggested installation.

      - ***************************************************************************************

      - Retain the following Article when manholes are in project-scope.

      - ***************************************************************************************

MANHOLES

The vertical riser sections of manhole may be of different dimensions in order that manholes of various depths can be readily assembled.

Install circular precast manhole sections with sealing gasket to seal joints between sections.  Clean joints prior to installation.  Entire width of joint shall receive a layer of sealing gasket.

Fill lifting holes and gaps at joints with a non-shrink grout.

Precast concrete manhole bases may be used when approved by a LANL UI Wastewater System Representative. If approved, it is with the understanding that placing the bases at the specified elevation, location, and alignment is the Subcontractor’s responsibility.

      - ***************************************************************************************

      - Retain the following Article when tanks are in project-scope.

      - ***************************************************************************************

SEPTIC AND HOLDING TANKS

      - ***************************************************************************************

      - Retain the following paragraph when precast concrete tanks are in project-scope.

      - ***************************************************************************************

Install precast concrete tank sections with sealing gasket to seal joints between sections. Clean joints prior to installation. Entire width of joint shall receive a layer of sealing gasket.

Cut and install CMP riser to provide a flush and vertical fit with tank. Use mastic and/or grout around and between CMP and top of tank to provide watertight seal.

Provide and install conduits from the building to the holding tank (only) for power and monitoring wiring for a high level alarm system.  High level alarm, monitors, floats, and controls shall be supplied and installed per Section << 33 3200 - Wastewater Utility Pumping Stations>>.

Provide communications link between the holding tank monitoring/controls and the TA-46 Wastewater Plant PLC system.  System shall be installed and available for testing during the Acceptance Inspection.

Furnish and install all power connections and communication links to and from the control box in accordance with provisions of Division 26.

      - ***************************************************************************************

      - Grade rings are circular concrete or plastic components placed at the top of manholes or access points of septic or holding tanks. Grade rings are most commonly used in sanitary sewer and stormwater manholes. They are less commonly used in septic and holding tanks.

      - ***************************************************************************************

GRADE RINGS

Use mastic and/or grout to lay grade rings to provide watertight seal and for the prevention of displacement of rings.

Grade rings shall remain plumb and vertically aligned during backfilling and paving operations.

      - ***************************************************************************************

      - Retain the following Article when manholes are in project-scope.

      - ***************************************************************************************

MANHOLE FRAME AND COVER

Provide ductile iron castings as shown on the Drawings and as specified herein.  The castings shall include manhole frames and covers.

Seal between grade ring and frame with mastic and/or grout to provide watertight seal and for the prevention of displacement of rings and frame.

      - ***************************************************************************************

      - Retain the following Article when tanks are in project-scope.

      - ***************************************************************************************

TESTING OF SEPTIC AND HOLDING TANKS

Test sanitary sewer septic and holding tanks for leakage by a water exfiltration test.  Furnish all materials and equipment necessary to perform test and conduct test in the presence of the LANL Inspector.  Perform test prior to backfilling around tank and prior to placement of access ports and covers.  Properly plug inlet and outlet lines and fill and seal holes and joints as specified.  There shall be no allowable leakage.  If septic or holding tank fails two exfiltration tests, the container shall be spraylined to specifications.

      - ***************************************************************************************

      - Retain the following Article when manholes for sanitary sewer systems are in project-scope.

      - ***************************************************************************************

TESTING OF SEWER MANHOLES

Test sanitary sewer manholes for leakage by a water exfiltration test. Submit test reports to the LANL STR. Perform test prior to backfilling around manhole and prior to placement of manhole frame and cover. Properly plug inlet and outlet lines and fill and seal lift holes and barrel joints as specified. In lieu of water exfiltration testing the manhole interior can be coated with a two part, high build epoxy lining with 100 percent solids by volume. Material shall have chemical resistance and be designed as a structural lining for manholes and vessels in wastewater facilities. Preparation of surface and application of product shall be per the manufacturer’s instructions. If manhole(s) fail two exfiltration tests, the manhole(s) shall be spraylined to specifications.

Manufacturer: Raven Lining Systems.

Furnish all materials and equipment necessary to perform test and conduct test in the presence of the LANL Inspector.  Allow a stabilization period of 1 hour for absorption, after which, refill manhole as necessary before starting test.  Perform test for a period of 2 hours, after which refill manhole, measuring necessary quantity of water. The difference in water surface elevation from original to final level shall be measured and converted to gallons per hour lost through manhole leakage.  An allowable leakage is allowed and is represented by the following formula:

      - V = 0.20 DHT

        - where:

          - V = Allowable loss in gallons

          - D = Manhole diameter in feet

          - H = Initial depth of water to invert in feet

          - T = Duration of test in hours

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 33 0513, REV. 7, DATED APRIL 15, 2026.