Section 33 7711 
Pad-Mounted Switch Rough-In

  - ************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 5 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Electrical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable Sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

      - For the purposes of this Section, a “pad-mounted switch” consists of a single self-supporting enclosure containing up to four medium-voltage interrupter switches. Refer to LANL ESM Chapter 7 - Electrical, Section G4010, Part 7.0 for additional information.

  - ***********************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

Furnish and install rough-in for pad-mounted medium-voltage switch including the following:

        - ******************************************************************************

        - Retain either Concrete Pad or Manhole to match Project requirements. Pad-mounted switch unit will either be mounted on top of an electrical distribution manhole (standard for new construction) or on a concrete pad adjacent to an existing electrical distribution manhole.

        - ******************************************************************************

​​​​​​​​​Concrete Pad

        - *** OR ***

Manhole

Underground duct bank for medium-voltage cables.

Grounding provisions.

Related REQUIREMENTS

Section << 03 3001 - Reinforced Concrete>>

Section << 31 2000 - Earth Moving>>

Section << 33 7119 - Electrical Underground Ducts and Manholes>>

reference standards

ASTM D1557 - Standard Test Methods for Laboratory Compaction Characteristics of Soil Using Modified Effort (56,000 ft-lbf/ft3 (2,700 kN-m/m3)).

IEEE C2 - National Electrical Safety Code(R) (NESC(R)).

LANL PERFORMED WORK

LANL Utilities & Infrastructure (UI) group will furnish, install, and test the pad mounted medium-voltage switch and associated medium voltage cables.

At electrical manholes containing energized electrical cables, LANL UI will make penetrations into the manholes and will install the last 5 ft of duct into the manhole using materials furnished by the Subcontractor.

SUBMITTALS

None.

QUALITY ASSURANCE

Comply with <<IEEE C2>>.

SEQUENCING AND SCHEDULING

Coordinate rough-in for medium-voltage pad-mounted switch with LANL UI through the LANL Subcontract Technical Representative (STR).

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements; pad mounted medium-voltage switch will be installed on either a manhole or on a concrete pad adjacent to an existing manhole.  The following paragraph is automatically activated when 'concrete pad' is activated in PART 1.

      - ***************************************************************************************

After pad is formed, and conduits, reinforcing bars, and ground conductors are installed, but before concrete is placed, schedule an inspection through the LANL STR.

PART 2 - PRODUCTS

PAD-MOUNTED medium-voltage Switch (GFE)

LANL UI will furnish tamperproof and weatherproof pad-mounted medium-voltage switch.

PART 3 - EXECUTION

EXAMINATION

Examine surfaces and conditions, with Installer present, for compliance with installation tolerances and other conditions affecting rough-in for pad-mounted medium-voltage switch.  Do not proceed with installation until unsatisfactory conditions have been corrected.

      - ***************************************************************************************

      - Edit the following article to match Project requirements. Either Concrete Pad Installation or Manhole will be automatically activated by activating the corresponding paragraphs in PART 1.

      - ***************************************************************************************

CONCRETE PAD Installation

Prepare level, compacted pad site per Section << 31 2000 - Earth Moving>>. Compact to 95 percent per <<ASTM D1557>>.

      - ***************************************************************************************

      - Project-specific switch pad construction dimensions and details must be included in the Drawings. Use LANL Electrical Standard Detail ST-G4010-38 as guidance for concrete pad dimensions reinforcing, and other details.

      - ***************************************************************************************

Install reinforced concrete pad for pad-mounted switch as shown on the Drawings. Refer to Section << 03 3001 - Reinforced Concrete>>​​ for materials and installation requirements.

Form concrete pad using framing with form release compounds.

Use a Section << 03 3001 - Reinforced Concrete>> pre-approved design mix.

finish top of pad to be level within 1/4 inch in 5 ft and to have no depressions.

Chamfer top edges and corners.

Cure concrete not less than seven days before installing equipment.

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements; retain if equipment protection is required. Refer to LANL Electrical Standard Detail ST-G4010-39. Locate and detail equipment protection bollards on the Drawings.

      - ***************************************************************************************

Install equipment protection bollards around the medium-voltage switch pad as indicated on the Drawings.

Manhole

Provide manhole with top section designed for mounting ​one​ medium voltage pad mounted switch units as shown on the Drawings.

Refer to Section ​33 7119 - Electrical Underground Ducts and Manholes​.

duct INSTALLATION

Terminate medium-voltage ducts in the switch compartment areas of the medium-voltage switch pad as indicated on the Drawings.

Install 6-inch concrete-encased duct from below each switch compartment at the switch pad to within 5 ft of existing manhole. LANL UI will extend ducts into existing manhole. Furnish all duct bank materials required for this work.

Refer to Section << 33 7119 - Electrical Underground Ducts and Manholes>> for materials and installation requirements.

Terminate each duct with a bell end fitting set 2 inches above the top of the concrete pad.

Grounding

Install 4/0 AWG grounding conductor from each switch compartment area to ground conductor ring in the existing electrical manhole or to the duct bank ground conductor.

Terminate medium-voltage duct bank ground conductor in switch compartment area of the medium-voltage switch pad. Provide compression ground lug to connect ground conductor to medium-voltage switch ground pad in the switch compartment.

      - ***************************************************************************************

      - The following article will be automatically activated if 'concrete pad' is activated in PART 1.

      - ***************************************************************************************

Field Quality Control

After switch pad is formed, conduits are installed, reinforcing bars are installed, but before concrete is placed, schedule an inspection through the LANL STR.

Allow 3 working days in schedule for LANL inspection.

Correct deficiencies noted before placing concrete.

medium-voltage switch INSTALLATION (LANL PERFORMED WORK)

LANL UI will install the pad-mounted medium-voltage switch.

        - ******************************************************************************

        - Retain the following subparagraph if the switch requires anchoring.

        - ******************************************************************************

The switch will be anchored with post-installed concrete anchors per Drawings.

Ground conductor will be connected to the ground pads in switch compartments and/or to the ground ring in the electrical manhole or to the duct bank ground conductor.

LANL UI will install, test, and terminate the medium-voltage cables.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 33 7711, REV. 5, DATED APRIL 15, 2026.