Section 33 8126 
Communication Underground Ducts, Manholes, and Handholes

  - ************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 2 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Communications POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

  - ************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

      - ***************************************************************************************

      - The following paragraphs are designer-choices. Retain paragraphs based on project-scope.

      - ***************************************************************************************

Underground ductbanks for open telecommunications utility systems with ​​​​​​​​<< Click and select the applicable conduit and fitting material(s) (e.g., IMC, RMC etc.);  Intermediate Metal Conduit and Fittings;  Rigid Metal Conduit and Fittings;  Plastic-Coated Steel Conduit and Fittings; and  Rigid Non-metallic Conduit and Fittings>>​​​​​​​​.

Underground ductbanks for secure communications cables with ​​​​​<< Click and select the applicable conduit and fitting material(s) (e.g., IMC, RMC etc.);  Intermediate Metal Conduit and Fittings;  Rigid Metal Conduit and Fittings;  Plastic-Coated Steel Conduit and Fittings; and  Rigid Non-metallic Conduit and Fittings>>​​​​​.

Manholes for open telecommunications utility systems.

Manholes for secure communications cables.

RELATED REQUIREMENTS

Section << 01 2500 - Substitution Procedures>>

Section << 03 3001 - Reinforced Concrete>>

Section << 03 3053 - Miscellaneous Cast-in-Place Concrete>>

Section << 27 1500.18 - Classified Network Infrastructure Rough-In>>

Section << 31 2000 - Earth Moving>>

REFERENCE STANDARDS

29 CFR 1910.27 - Scaffolds and Rope Descent Systems.

AASHTO HB - Standard Specifications for Highway Bridges.

ANSI A14.3 - American National Standard for Ladders -- Fixed -- Safety Requirements.

ANSI C80.1 - American National Standard for Electrical Rigid Steel Conduit (ERSC).

ANSI C80.3 - American National Standard for Electrical Metallic Tubing -- Steel (EMT-S).

ANSI C80.6 - American National Standard for Electrical Intermediate Metal Conduit.

ASTM A36/A36M - Standard Specification for Carbon Structural Steel.

ASTM A48/A48M - Standard Specification for Gray Iron Castings.

ASTM B8 - Standard Specification for Concentric-Lay-Stranded Copper Conductors, Hard, Medium-Hard, or Soft.

ASTM C857 - Standard Practice for Minimum Structural Design Loading for Underground Precast Concrete Utility Structures.

ASTM C858 - Standard Specification for Underground Precast Concrete Utility Structures.

ASTM C891 - Standard Practice for Installation of Underground Precast Concrete Utility Structures.

ASTM D1056 - Standard Specification for Flexible Cellular Materials—Sponge or Expanded Rubber.

ASTM D1557 - Standard Test Methods for Laboratory Compaction Characteristics of Soil Using Modified Effort (56,000 ft-lbf/ft3 (2,700 kN-m/m3)).

ASTM F512 - Standard Specification for Smooth-Wall Poly(Vinyl Chloride) (PVC) Conduit and Fittings for Underground Installation.

IEEE 837 - Qualifying Permanent Connections Used in Substation Grounding.

IEEE C2 - National Electrical Safety Code(R) (NESC(R)).

NECA 1 - Standard for Good Workmanship in Electrical Construction.

NECA/NEMA 605 - Standard for Installing Underground Nonmetallic Utility Duct.

NEMA BI 50006 - Polyvinyl-Chloride (PVC) Externally Coated Galvanized Rigid Steel Metal Conduit and Intermediate Metal Conduit.

NEMA FB 1 - Fittings, Cast Metal Boxes, and Conduit Bodies for Conduit, Electrical Metallic Tubing, and Cable.

NEMA TC 2 - Electrical Polyvinyl Chloride (PVC) Conduit.

NEMA TC 3 - Polyvinyl Chloride (PVC) Fittings for Use with Rigid PVC Conduit and Tubing.

NEMA BI 50063 - Polyvinyl Chloride (PVC) Plastic Utilities Duct for Underground Installations.

NEMA TC 9 - Fittings for Polyvinyl Chloride (PVC) Plastic Utilities Duct for Underground Installation.

NFPA 70 - National Electrical Code.

UL 6 - Electrical Rigid Metal Conduit-Steel.

UL 514B - Conduit, Tubing, and Cable Fittings.

UL 514C - Nonmetallic Outlet Boxes, Flush-Device Boxes, and Covers.

UL 651 - Schedule 40, 80, Type EB and A Rigid PVC Conduit and Fittings.

UL 651A - High Density Polyethylene (HDPE) Conduit.

UL 1242 - Electrical Intermediate Metal Conduit-Steel.

      - ***************************************************************************************

      - Retain the following Article when telecommunication systems (open and/or secure) are in project-scope. Retain paragraphs based on project-scope.

      - ***************************************************************************************

SUBCONTRACTOR PERFORMED WORK

Subcontractor will order, install, and test open telecommunications cables.

Subcontractor will order, install, and test secure communications cables.

      - ***************************************************************************************

      - Retain the following Article and the first two paragraphs when underground ductbank systems (open and/or secure) are in project-scope.

      - ***************************************************************************************

SEQUENCING AND SCHEDULING

Notify LANL Subcontract Technical Representative (STR) to schedule inspection of each ductbank or ductbank segment before concrete is placed.

Notify LANL STR 10 days before duct tests.

      - ***************************************************************************************

      - Retain the following two paragraphs if ductbank systems are for secure communications.

      - ***************************************************************************************

For secure communication ductbank systems, notify the LANL STR at least 30 days prior to the scheduled start of construction of the ductbank to have design drawings and appropriate application forms submitted to the LANL Telecommunications Group Site Coordinator.  Once approval has been obtained from same, the LANL STR will inform Subcontractor that construction may begin.

For secure communication ductbank systems notify the LANL STR at least 3 working days prior to the scheduled concrete encasement of the ductbank. The LANL Telecommunications Group Site Coordinator must inspect the secure ductbank prior to encasing with concrete.

SUBMITTALS

      - ***************************************************************************************

      - Retain the following paragraph and subparagraph when manholes are in project-scope.

      - ***************************************************************************************

Action Submittals:

Catalog Data: Describing precast manhole(s), manhole frame(s) and lid(s), ladders, and cable racks. Include data substantiating that materials comply with specified requirements.

Informational Submittals at Closeout:

Project Record Documents: Accurately record GPS-based survey locations of:

          - **********************************************************************

          - Retain the first subparagraph when ductbanks are in project-scope. Retain the second subparagraph when manholes are in project-scope.

          - **********************************************************************

Ductbanks, and places where ductbanks cross other underground systems.

New and existing manholes.

QUALITY ASSURANCE

Furnish products that are listed and labeled by a Nationally Recognized Testing Laboratory (NRTL) for the application, installation condition, and the environment in which installed.

DELIVERY, STORAGE, AND HANDLING

Receive, store, protect, and handle products according to <<NECA 1>> and <<NECA/NEMA 605>>.

PART 2 - PRODUCTS

    - **********************************************************************************************

      - The following Article Product Options and Substitutions is a designer-choice Retain when project allows for substitutions.

    - **********************************************************************************************

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section << 01 2500 - Substitution Procedures>>.

      - ***************************************************************************************

      - For underground ductbanks, the following four Articles Intermediate Metal Conduit (IMC) and Fittings, Rigid Metal Conduit (RMC) and Fittings, Plastic-Coated Steel Conduit and Fittings, and Rigid Non-Metallic Conduit (RNMC) and Fittings are a designer-choice for conduit and fitting materials. Retain based on project-specific requirements.

      - ***************************************************************************************

INTERMEDIATE METAL CONDUIT (IMC) AND FITTINGS

IMC: <<UL 1242>> and <<ANSI C80.6>>.

Fittings and conduit bodies: Zinc-plated, threaded, malleable iron, meeting <<UL 514B>> and <<NEMA FB 1>>.

RIGID METAL CONDUIT (RMC) AND FITTINGS

Conduit per <<UL 6>>  and <<ANSI C80.1>>​.

Fittings and conduit bodies: Zinc-plated, threaded, malleable iron, meeting <<UL 514B>> and <<NEMA FB 1>>.

PLASTIC-COATED STEEL CONDUIT AND FITTINGS

Conduit or IMC: PVC exterior coated, urethane interior coated, galvanized rigid steel per <<NEMA BI 50006>>.

Conduit bends must be long, sweeping bends with a radius not less than:

Six times the internal diameter of conduits 2 inches or smaller, or

Ten times the internal diameter of conduits larger than 2 inches.

Fittings and conduit bodies: 40 mil PVC exterior coated, urethane interior coated, zinc-plated, threaded, malleable iron meeting <<UL 514B>> and <<NEMA BI 50006>>.

RIGID NON-METALLIC CONDUIT (RNMC) AND FITTINGS

Conduit: PVC per <<UL 651>> and <<NEMA TC 2>>​, <<ANSI C80.3>>.

Fittings: Solvent-welded socket fittings meeting <<UL 514C>> and <<NEMA TC 3>>.

      - ***************************************************************************************

      - Retain the following three Articles Utilities Duct and Fittings, Duct Spacers and Ground Cable when ductbanks are in project-scope.

      - ***************************************************************************************

UTILITIES DUCT AND FITTINGS

PVC type EB, 90 degree C rated, utilities duct for concrete encasement per <<NEMA BI 50063>>, <<ASTM F512>>, and <<UL 651A>>.

PVC fittings per <<NEMA TC 9>> and <<ASTM F512>>​.

DUCT SPACERS

Duct spacers must provide 6-inch separation between ducts and 6-inch concrete coverage on bottom, sides, and top.

GROUND CABLE

Use 4/0 AWG bare-stranded, soft-temper, copper cable per <<ASTM B8>>.

      - ***************************************************************************************

      - Retain the following Article Corrosion Protection Tape when IMC, RMC or plastic-coated steel conduit and fittings are used.

      - ***************************************************************************************

CORROSION PROTECTION TAPE

Pressure-sensitive, 10-mil thick, PVC-based tape for corrosion protection of metal conduit and fittings.

      - ***************************************************************************************

      - Retain the following two Articles Underground Warning Tape and Raceway Measuring/Pulling Tape when ductbanks are in project-scope.

      - ***************************************************************************************

UNDERGROUND WARNING TAPE

Furnish detectable underground warning tape for underground duct banks.

Use 6 inch wide, minimum 4.0 mils thick, high visibility, continuously printed, inert fiber reinforced polyethylene for direct burial service underground warning tape with an orange background color.

Black lettering stating:

        - "CAUTION BURIED COMMUNICATION LINE BELOW."

RACEWAY MEASURING/PULLING TAPE

Raceway measuring/pulling tape with permanently printed measurements in one-foot increments and minimum 1,200 lb. average breaking strength.

      - ***************************************************************************************

      - Edit the following Article to match Project requirements. Retain when applicable to the project.

      - ***************************************************************************************

INSULATING BUSHINGS

NRTL-listed insulating bushings with 105 degrees C rated insulation.

      - ***************************************************************************************

      - Edit the following Article to match Project requirements. Retain when applicable to the project.

      - ***************************************************************************************

GROUNDING BUSHINGS

NRTL-listed, galvanized malleable iron, 150 degrees C rated insulated throat grounding bushings with lay-in type ground cable lugs.

      - ***************************************************************************************

      - Edit the following Article to match Project requirements. Retain when applicable to the project.

      - ***************************************************************************************

DUCT PLUGS

Soft, expansible gasket material compressed with non-metallic plates and bolts to produce a positive seal against water and gas in unused ducts.

      - ***************************************************************************************

      - Edit the following article to match Project requirements. Retain when applicable to the project.

      - ***************************************************************************************

DUCT SEALANT

Expandable foam duct sealant kits to prevent water and gas from entering manholes, vaults, or structures.

      - ***************************************************************************************

      - Retain the following three Articles Precast Manholes, Premolded Joint Filler and Manhole Accessories when manholes are in project-scope. Edit manhole size(s) to match Project requirements. Refer to LANL Electrical Standard Details ST-G4010-35, ST-G4010-36, and ST-G4010-37. Provide manhole plans and details in the Drawings.

      - ***************************************************************************************

PRECAST MANHOLES

Manufacturer:

Jensen Pre-Cast

Old Castle Infrastructure

Vaughn Concrete Products, Inc.

Precast Manufacturing NM

Precast manholes shall be per <<ASTM C858>>.

Telecommunications manholes with the following minimum inside dimensions: 12 ft long, 6 ft wide, 7 ft high or 8 ft long, 6 ft wide, 7 ft high.  Coordinate requirements with LANL Telecommunications Group through the LANL STR.

Minimum thickness of floor, walls, and roof: 6 inches.

Minimum design loading shall me <<ASTM C857>>:

Manholes not subject to vehicle traffic: Design live load to be 300 lb/sq ft minimum.

Manholes installed in a street or parking area: Design live loading shall be AASHTO HS-20 per <<AASHTO HB>>.

Manhole floor shall be cast integral with walls to form the bottom ring.

Furnish a keyed joint between the bottom ring and top ring.

      - ***************************************************************************************

      - Edit knockout sizes and locations to match Project requirements.

      - ***************************************************************************************

Coordinate locations of knockout panels in telecommunications manholes with LANL Telecommunications Group through the LANL STR.

Position a 12-inch diameter sump hole with cast iron cover in the floor centered under the access opening.

Locate a minimum 36-inch diameter access opening centered in the roof of the manhole.

Furnish precast concrete grade rings: As required to place top of manhole flush with paving or 2 to 4 inches above finished grade and with minimum inside diameter of 36 inches.

Furnish cast iron manhole steps at 12 inches on-centers and the first step not to exceed 12 inches from the top of the frame.

Furnish lifting inserts in each manhole section for unloading and positioning.

Pulling irons: Hot-dip-galvanized steel with a capacity of 8,000 lb. and a safety factor of two.  Position one iron under each knockout panel and two along each side wall (total of six).

Inserts:

Manufacturer: Unistrut, P3200 series.

Embed 1-5/8 inches x 1-5/8 inches hot dip galvanized steel continuous pre-set inserts in each side wall of manhole.

Orient inserts horizontally and space 20 inches apart with bottom insert 12 inches above the floor.

Extend inserts to within 6 inches of end walls.

PREMOLDED JOINT FILLER

Manufacturer:

Williams Products, Inc., Type NN-1

ConSeal Concrete

Closed cell expanded neoprene joint filler conforming to <<ASTM D1056>>.

MANHOLE ACCESSORIES

Refer to Appendix A for acceptable manhole ring and cover types. Confirm with LANL Telecommunications Group for approval prior to selection.

Heavy duty, cast-iron manhole frame with solid lid.

Manufacturers:

Neenah Foundry Company, R-1640 Series.

EJ USA Inc., V1600-5

Material: <<ASTM A48/A48M>>​, Class 35B.

Frame and lid suitable for AASHTO HS-20 wheel loads.

Minimum clear opening through the frame: 36 inches.

Lid lettering “Communications.”

Mahole Ladder:

Manufacturer:

Condux International

INWESCO.

Furnish hooked manhole ladder meeting <<29 CFR 1910.27>> (OSHA) and <<ANSI A14.3>>.

Material: <<ASTM A36/A36M>>.

Ladder Safety Post:

Manufacturer: Bilco LU-2.

Furnish hot dip galvanized steel telescoping ladder safety post in manholes with two or more grade ring steps.

Cable Racks and Cable Rack supports:

Manufacturer:

INWESCO.

Condux International.

Furnish hot-dip-galvanized cable racks and cable-rack supports for manholes.

Furnish 7-inch-long and 3-inch-long cable rack hooks. Coordinate quantity and types with the LANL STR.

PART 3 - EXECUTION

    - **********************************************************************************************

      - Retain the following Article when underground ductbanks are in project-scope.

    - **********************************************************************************************

PREPARATION

Install underground ductbank systems per <<NFPA 70>> (NEC), <<IEEE C2>> (NESC), <<NECA/NEMA 605>>, and the requirements in this Section.

Duct bank system routing shown on Drawings is in approximate locations unless dimensioned. Route as required to complete the system.

Coordinate underground ductbank system work to avoid interference with other trades and existing utilities.

Verify routing and termination locations of duct banks before excavation for rough-in.

Verify that field measurements are as shown on Drawings.

Position trench such that the concrete envelope of the ductbanks have the following minimum horizontal and vertical separations from parallel or perpendicular runs of other utility pipes or conduits.

      - ***************************************************************************************

      - Ensure dimensions in table below meet LANL ESM Chapter 3 - Civil, Section G30 Site Civil/Mechanical Utilities, Table G30GEN-1. The Drawings should contain trench detail(s) reflecting the requirements in LANL Civil Standard Detail ST-G30GEN-4.

      - ***************************************************************************************

| Utility Type | Parallel Lines | Perpendicular Crossings |
| --- | --- | --- |
| Water | 36 inches | 24 inches |
| Gravity Sewer | 36 inches | 24 inches |
| Force Main Sewer | 36 inches | 24 inches |
| Storm Drain | 36 inches | 24 inches |
| Natural Gas | 60 inches | 24 inches |
| Steam or Hot Water | 60 inches | 24 inches |
| Open Communications | 24 inches of tamped soil or 3 inches of concrete | 12 inches of tamped soil or 3 inches of concrete |
| Secure Communications | 36 inches of tamped soil or 6 inches of concrete; verify case-by-case with LANL Telecommunications Group | 24 inches of tamped soil or 6 inches of concrete; verify case-by-case with LANL Telecommunications Group |
| Electrical | 12 inches of tamped soil or 3 inches of concrete | 12 inches of tamped soil or 3 inches of concrete |

EXCAVATION AND BACKFILL

Make excavation for manholes and underground ductbanks to depth required and to provide solid bearing.

        - ******************************************************************************

        - Retain the following subparagraph if ductbank systems are for open communications.

        - ******************************************************************************

Set excavation such that top of telecommunication ductbank concrete encasement is not less than 24 inches below finished grade or paving.

        - ******************************************************************************

        - Retain the following subparagraph if ductbank systems are for secure communications.

        - ******************************************************************************

Set excavation such that top of secure communications ductbank concrete encasement is not less than 36 inches below finished grade or paving (the secure duct is to be not less than 1 meter deep).

      - ***************************************************************************************

      - Retain the following paragraph when ductbanks are in project-scope.

      - ***************************************************************************************

Grade trenches for underground ductbanks to a minimum of 4 inches per 100 ft. toward manholes.

Keep excavation dry during installation of work.

      - ***************************************************************************************

      - Retain the following paragraph when ductbanks are in project-scope.

      - ***************************************************************************************

Make trenches of sufficient width to receive work to be installed and provide specified concrete coverage on sides.

Backfill excavations for ductbanks and manholes in 6-inch layers; use soil excavated; remove roots, rocks, and sharp objects. Furnish coarse sand as required for additional backfill material.

Moisture condition backfill soil and compact in accordance with <<ASTM D1557>> to 95 percent of maximum density under paved areas and 90 percent of maximum density under unpaved areas.

Overfill excavations to allow for settlement.

Refer to Section << 31 2000 - Earth Moving>> for additional requirements.

      - ***************************************************************************************

      - Retain the following two Articles Underground Ductbank Installation and Concrete Encasement when underground ductbanks are in project-scope. Edit the following Articles to match Project requirements. Refer to LANL Electrical Standard Detail ST-G4010-32. Provide ductbank plans and details in the Drawings.

      - ***************************************************************************************

UNDERGROUND DUCTBANK INSTALLATION

Install the number and size of ducts as indicated on the Drawings.

Use the following duct materials:

        - ******************************************************************************

        - Edit the two subparagraphs below to match Project requirements.

        - ******************************************************************************

Use Schedule 40 rigid non-metallic conduit, Type EB utility duct, galvanized intermediate metal conduit, or rigid galvanized steel conduit for communications ducts.

Use plastic-coated galvanized rigid steel conduit, tape-wrapped galvanized intermediate metal conduit, or tape-wrapped rigid galvanized steel conduit for elbow and riser where ducts turn up to the surface.

Grade ducts to a minimum of 4 inches per 100 ft to drain to manholes. Do not trap ducts. Align ducts to prevent trapping moisture at any point.

Use the smooth earth walls of trenches as forms for concrete encasement of ducts.

If a manhole is not indicated, make horizontal changes in direction of duct runs using long sweep bends with a minimum radius of 35 feet unless otherwise noted on the Drawings.

Where ducts turn up into the surface, use RGS, IMC, or PVC coated rigid steel elbows with minimum 36 inches radius; terminate in a coupling 4 inches above the surface or equipment pad. Install zinc-plated malleable iron pipe plug in each unused duct stub-up.

Support ducts with duct spacers placed at intervals not exceeding 5 ft. Stagger duct supports to prevent any discontinuity in the concrete encasement.

Anchor ducts to bottom of trench at intervals not exceeding 10 ft.

Terminate telecommunications ducts in manholes, vaults and building walls using bell end fittings.

For ducts installed through holes cut by Subcontractor in an existing building, vault, or manhole wall, pack opening with non-shrink grout. Feather the edge of the grout around each bell and conform to the curvature of the bell end. Remove sharp edges and projections and fill voids within 6 inches of bell ends.

For concrete-encased ducts installed in new manholes through a knockout panel, after removing forms from the end of the ductbank, rub the exposed concrete surface smooth. Feather the edge of the concrete around each bell and conform to the curvature of the bell end. Remove sharp edges and projections and fill voids within 6 inches of bell ends.

      - ***************************************************************************************

      - Retain the following paragraph if ductbank systems are for secure communications.

      - ***************************************************************************************

All underground secure communications ducts must meet Section << 27 1500.18 - Classified Network Infrastructure Rough-In>> requirements.

For secure ducts installed through holes cut in existing building, vault or manhole walls, pack opening with non-shrink grout.

      - ***************************************************************************************

      - Retain the following paragraph if IMC, RMC or plastic-coated steel conduits are used on the project.

      - ***************************************************************************************

Ground metallic conduit exposed to contact to <<NFPA 70>>​ (NEC) requirements. Use hydraulically irreversible crimps for concealed grounding connections.

Install a 4/0 AWG bare copper ground cable centered within each telecommunications ductbank.

Connect to ground cable in manholes using hydraulically irreversible crimps.

Connect to ground bar in Telecommunications Room using <<IEEE 837>> certified compression connectors.

Make-up joints in underground ducts to be tight, driven home on both sides and thoroughly waterproof. On non-metallic ducts use manufacturer's recommended solvent-cement. On metallic conduits, coat male threads with red colored, alkyd base, tank and structural primer that is suitable for galvanized steel; make up fittings wrench-tight.

      - ***************************************************************************************

      - Retain the following paragraph if ductbank systems are for secure communications.

      - ***************************************************************************************

Mark secure communication ducts with red painted stripes on 5-foot centers. Mark secure communications conduits in manholes with 3/4-inch-wide red plastic tape on 1-foot centers.

      - ***************************************************************************************

      - Retain the following paragraph if IMC, RMC or plastic-coated steel conduits are used on the project.

      - ***************************************************************************************

Where metallic conduits exit concrete encasement, use plastic coated rigid steel conduit or tape wrap with corrosion protection tape, half-lapped. Wrap IMC or RGS conduit 12 inches on each side of exit point and wrap all metal conduits in contact with earth.

Schedule inspection of each ductbank or ductbank segment with LANL Telecommunications Group Site Coordinator before concrete is placed.

Test each duct for blockage or deformation after concrete has cured for 24 hours.

Use a flexible mandrel/scraper not less than 12 inches long with a diameter approximately 1/4 inch less than the inside diameter of the duct.

Pull a mandrel behind a brush with stiff bristles.

Replace any duct section found blocked.

Notify LANL STR not less than two working days before duct tests; submit written reports of tests to LANL STR.

After ducts have been successfully inspected and tested:

Backfill the trench as described in Article << 3.2; or  _______>> Excavation and Backfill.

Place underground warning tape in backfill 12 inches below the surface.

Install measuring and pulling tape in each duct. Leave not less than 12 inches of slack at each end of the tape. Secure each end of tape.

Stub-Up Connections:

Use rigid steel conduit or IMC for outdoor stub-up connections. Non-metallic conduit may be used for indoor stub-up connections that are not subject to physical damage.

Extend conduits through concrete pad or floor for connection to freestanding equipment with an adjustable top or coupling threaded inside for plugs; set flush with the finished floor or equipment pad.

Where equipment connections are not made under this Subcontract, install threaded insert plugs set flush with the floor.

      - ***************************************************************************************

      - Retain the following paragraph if IMC, RMC or plastic-coated steel conduits are used on the project.

      - ***************************************************************************************

Install corrosion protection tape on metal conduits and fittings in contact with soil using half-lapped wrappings.

CONCRETE ENCASEMENT

Concrete-encased underground ductbanks to provide not less than 6 inches of coverage on all sides.

Refer to ​<< Section 03 3053 - Miscellaneous Cast-in-Place Concrete; or  Section  03 3001 - Reinforced Concrete>>​ for basic material and installation requirements. Neither concrete reinforcing nor concrete testing is required for this application.

Use a LANL pre-approved concrete mix design that is suitable for exterior use exposed to freezing and thawing. LANL pre-approved concrete mix designs are included in the Listing of LBO-Approved IBC Testing, NDE and Inspection Agencies; Fabricators; and Products associated with LANL ESM Chapter 16 - Building Code Program.

Place concrete using deflecting trough directing concrete through the duct assembly.

Place concrete envelope as one monolithic pour where possible; taper any joints with a 10:1 slope.

Allow for expansion/contraction of ducts; place concrete starting at one end of ductbank allowing the free end to move.

        - ******************************************************************************

        - Retain the following subparagraph if ductbank systems are for secure communications.

        - ******************************************************************************

The LANL Telecommunications Group Site Coordinator must perform an inspection of the secure communications ductbank system prior to encasing with concrete.

      - ***************************************************************************************

      - Retain the following Article when manholes are in project-scope.

      - ***************************************************************************************

MANHOLE INSTALLATION

Install manholes at locations indicated on the Drawings.

Install manholes in accordance with <<ASTM C891>>​.

Make excavation of suitable dimensions so ducts enter manhole at proper elevation. Refer to Section << 31 2000 - Earth Moving>> for additional requirements.

Install at least 6 inches sand bedding under manholes; level and compact to 95 percent of maximum density in accordance with <<ASTM D1557>>.

Install a sump of 3/4-inch gravel below the drain sump opening in the bottom ring of the manhole.

Place pre-molded joint filler in joints between bottom ring, top ring, grade rings and manhole frame. Install following manufacturer's instructions.

Install a continuous loop of 4/0 AWG bare copper ground cable around inside walls of manholes at floor level.

Attach to walls using copper or cast bronze cable holders and masonry anchors.

Connect to duct bank ground cable using hydraulically irreversible compression fittings.

Ground metallic conduits or duct bell ends to ground cable loop using irreversible compression fittings.

Ground metal cable racks and permanent ladders using hydraulically irreversible compression fittings.

Install cable racks as required to support cables at intervals not exceeding 3 ft. Coordinate quantity and types of racks and arms with the LANL Telecommunications Group.

For manholes in unpaved areas, install an 8 ft by 8 ft by 6-inch concrete apron around manhole frame and cover. Taper the concrete one inch away from the frame to the edge of the apron for drainage.

Stamp manhole structure number on north edge of manhole ring. Use steel dies with 3/8 inch or larger characters.

      - ***************************************************************************************

      - Retain the following Article when duct plugging and/or sealing is required on the project.

      - ***************************************************************************************

DUCT PLUGGING AND SEALING

Install duct plugs in both ends of all unused ducts that cross any natural gas line.

Install duct sealant in both ends of all ducts containing cables that cross any natural gas line.

FIELD QUALITY CONTROL

Provide final protection and maintain conditions to ensure that coatings and finishes are without damage or deterioration at final inspection.

Inspection Points – Provide not less than 2 working days advance notice to the LANL STR for the following LANL inspection points. In the notice, identify the specific areas of the Project for which LANL inspection is requested. Correct deficiencies identified during inspections. If the requested LANL inspection does not occur within 3 working days of the LANL inspection point, work may proceed.

        - ******************************************************************************

        - Retain inspection points that are applicable based on project-scope and requirements. The first two subparagraphs apply to ductbanks and the third subparagraph applies to manholes.

        - ******************************************************************************

Underground Ducts: After ducts have been installed but before concrete-encasement or trench backfilling commences. Inspections may be scheduled for one or more segments. LANL inspection may include but is not limited to:

Correct duct material, quantity, and size,

Proper duct spacing and supports,

Proper anchoring of support spacers,

Proper depth and grading of ducts,

Correct duct stub-up locations,

Duct connection and coupling integrity,

Ground cable material and size,

Ground cable connection integrity.

Mandrel testing of underground ducts: After concrete-encasement has cured for 24 hours but before trench backfilling commences. LANL witnessing of Subcontractor-performed tests may be scheduled for one or more segments.

Manholes: After manholes have been installed but before concrete- backfilling commences. Inspections may be scheduled for one or more manholes. LANL inspection may include but is not limited to:

Correct manhole material and size,

Proper manhole location, orientation, leveling, and depth, and

Proper installation of pre-molded joint filler between sections.

END OF ​​​​​​​<< MAIN; or  None - N/A>>​​​​​​​ SECTION​​​​​​​<< ; APPENDIX FOLLOWS; or  None - N/A>>​​​​​​​

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 33 8126, REV. 2, DATED APRIL 15, 2026.

    - APPENDIX A - ACCEPTABLE MANHOLE RING AND COVER TYPES

      - Type 3 Manhole Ring and Cover

Type 4 Manhole Ring and Cover

- END OF SECTION