SECTION 33 3000

SANITARY SEWERAGE UTILITIES

*************************************************************************************************************

LANL MASTER SPECIFICATION

Available online at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifiers notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual (ESM) Civil POC.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Ch 1 Section Z10 Specifications and Quality sections.

*************************************************************************************************************

GENERAL

SECTION INCLUDES

Site piping, fittings, manholes, and accessories beyond 5 feet of building wall.

LANL-PERFORMED WORK

Coordinate with the LANL Subcontractor Technical Representative (STR) for ties into existing systems which include sanitary sewer lines, septic tanks, treatment plants, lift stations, and manholes.  Ties into existing systems shall be performed by LANL Utilities and Institutional Facilities Group (U&I).

LANL STR will coordinate for inspection of the interior of new and existing sanitary sewer lines (accessible by camera) with video camera for piping integrity and proper installation both before tie-in and at turnover.

*************************************************************************************************************

AE shall coordinate with LANL Projects Manager to ensure an approved WPF (Waste Profile Form) for all anticipated wastewater flows has been submitted to the LANL WAC Committee and Utility Wastewater system Operations Manager representative prior to completion of design.

*************************************************************************************************************

Subcontractor Technical Representative (STR) will ensure that an approved WPF (Waste Profile Form) for all anticipated wastewater from all drains or buildings connected to the sanitary wastewater system has been completed by LANL Project Manager and on file before scheduling tie-ins.  Documentation shall be submitted to the LANL U&I Group wastewater system representative prior to utility tie-in.

STR will coordinate all required inspections and tie-ins.

ACTION SUBMITTALS

Submit the following:

Catalog data on pipe materials, fittings and accessories, directional drilling pull (weak link) device, and casing seals.

Certifications of welders qualified welding procedure for heat fusion polyethylene joints.

[Submittals for the Horizontal Directional Drilling.]

Tracing wire continuity test report.

  - QUALITY ASSURANCE

Welders Certifications, Qualified Procedure Standards, and Weld Inspection/Testing.

      - Plastic Pipe: Comply with LANL ESM, Chapter 13 – Welding, Joining & NDE.

On-site and joining welding shall comply with LANL ESM Chapter 13 – Welding, Joining & NDE; and Master Specification 01 4455, Onsite Welding & Joining Requirements.

- Use LANL Welding Procedures

- Welders shall be qualified at LANL by LANL

Off-site welding and joining shall comply with ESM Chapter 13 – Welding, Joining & NDE; and Master Specification 01 4444, Offsite Welding & Joining Requirements.

Weld Inspection: Comply with ESM, Chapter 13 – Welding, Joining & NDE for PE pipe.

B.	LANL STR shall submit the approved material and accessory catalog data, and certification of welders and qualified welding procedure to the LANL U&I wastewater system engineer and the LANL construction inspector for verification of construction items and certifications during field quality assurance.

PRODUCTS

- PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

- SANITARY SEWER PIPING, BURIED BEYOND 5 FEET OF BUILDING

*************************************************************************************************************NOTE:  Consult with a LANL U&I Group wastewater system representative for approval when selecting piping material beyond 5 feet of the building and under roads.  Under roadways will require ductile iron or metallic pipe sleeve with spacers.  Sanitary sewer force main fittings shall have thrust blocks and restraints.

*************************************************************************************************************

    - Ductile Iron Pipe: AWWA C151, Class 150.

      - Joints: Bell and spigot, AWWA C111 rubber gaskets.

      - Fittings: AWWA C110, Ductile-Iron or Gray-Iron, Class 350 or AWWA C153, Ductile-Iron Compact Fittings, Class 350.

PVC Pipe and Fittings: ASTM D3034, SDR 35.

- Joints: Bell and spigot, ASTM D3212 rubber gaskets.

*************************************************************************************************************

Specify the following (2.2 C and D) for pressure systems (non-gravity)

*************************************************************************************************************

PVC Pipe: AWWA C900, Class 150 (DR 18).

Joints: Bell and spigot joint ASTM D3139, rubber gaskets ASTM F477.

Fittings: AWWA C110, Ductile-Iron or Gray-Iron, Class 350 or AWWA C153, Ductile-Iron Compact Fittings, Class 350.

Ductile Iron Pipe: AWWA C151, Class 150.

Joints: Bell and spigot, AWWA C111 rubber gaskets.

Fittings: AWWA C110, Ductile-Iron or Gray-Iron, Class 350 or AWWA C153, Ductile-Iron Compact Fittings, Class 350.

*************************************************************************************************************

PE Pipe may be used for gravity and pressure systems. The SDR pipe shall be sized to meet design pressure rating requirements of lift station pumps. *************************************************************************************************************

Polyethylene Pipe and Fittings.

Manufacturer:  Performance Pipe, [DriscoPlex 4100, Iron Pipe Size] or [DriscoPlex 4000, Ductile Iron Pipe Size].  Use of IPS or DIPS shall be appropriate for new system or interface with existing system.

Pipe: Polyethylene, high density, ASTM D 3035, ASTM F 714, PPI-PE4710, [SDR11] pipe size, ASTM D3350 cell classification number 445574C.

Fittings: Polyethylene, high density, butt heat fusion type, ASTM D3261, PE4710, [SDR 11], ASTM D3350 cell classification number 445574C.

Joints: Heat fusion per manufacturer’s instruction.

- FLANGES, UNIONS, AND COUPLINGS (Sewer Force Mains)

    - Mechanical or Push-On Type Pipe, and Fittings Below Grade.

Ductile Iron Pipe: Megalug Series 1100, malleable/ductile iron joint retainer/restraint gland with polymer, epoxy or bituminous outside coating and 1/2 inch minimum diameter asphalt coated tie rods.

PVC Pipe: use a compression connection and restraint system or retainer/restraint gland, Megalug Series 2000PV.

High Density Polyethylene

Transitions: MJ Adaptors shall be standard manufacturers adaptor that is butt fused to the pipe for connecting to mechanical joint pipe, fittings, and appurtenances.  Manufacturers’ complete assembly shall be supplied; including stainless steel stiffener, extended gland bolts and nuts, gland and gasket.

Coupling Sleeve Gravity Pipe

Manufacturer: Fernco Flexible Coupling or Proflex Coupling for heavy earth loadings.  Gasket suitable for the pipe material being joined.

Coupling Sleeve Pressure Pipe

Manufacturer: Tyler Union, American Cast Iron Pipe Company, Star Pipe Products, solid sleeves, long style, MJ x MJ with appropriate sized gasket material.  AWWA C153, Ductile-Iron Compact Fittings, Class 350.

- CLEANOUTS

- Cleanout

  - Manufacturer:  General Engineering Company, GENECO.

  - Ferrous metal top with gasketed bell to accept PVC schedule 40 or cast iron riser pipe.

  - Screw plug to be standard brass countersunk plug.

- Riser Pipe

  - Pipe: 4 inch minimum PVC schedule 40 or heavier or cast iron.

- Wye

  - Preformed single wye or double wye per design requirement.

- MANHOLE

********************************************************************

Refer to Civil Drawing ST-G3020-1 for manhole detail.

********************************************************************

    - Provide precast concrete manhole, concrete grade rings, and ductile iron cover per Drawings and Section 33 0513, Manholes and Structures.

EXECUTION

- EXAMINATION

Verify excavations are to required grade.  Do not over excavate.

- PREPARATION

    - Ream pipe ends and remove burrs.

Remove scale and dirt on inside and outside of piping before assembly.  Pipe interior shall be thoroughly cleaned of foreign material before lowering into the trench.

Keep open ends of pipe free from scale and dirt.  Whenever work is suspended during construction, or at the end of each workday, protect open ends with temporary plugs or caps.

- piping TIE-IN

    - Tie-ins to existing piping, lift stations, manholes, and equipment will be performed by LANL U&I group.  Excavation, backfill, and materials required for tie-in shall be provided by Subcontractor.  The tie-in will be inspected by the LANL Construction Inspector and the LANL U&I Group wastewater systems representative.

    - LANL STR will notify LANL U&I group at least 15 working days in advance to schedule tie-in of piping system and pre-tie-in video inspection described in Article 3.6.

    - Before tie-ins are scheduled the LANL STR will ensure materials required for tie-in are on site, service lines have been tested, material submittals and all test reports have been approved by LANL U&I Group and the excavation meets access and OSHA requirements.

    - Install pipe at manhole tie-ins at the same invert elevation without sags or low points.  Chip manhole wall only to allow for insertion of new pipe.  Install waterstop grout ring around the pipe before repairing the manhole wall. Caulk/seal around new pipe to provide watertight installation in manhole wall.  Seal shall be per pipe manufacturer’s instructions, in addition to ASTM F585.

    - Sleeve and caulk pipes penetrating exterior walls below grade to provide a waterproof installation.

    - Set concrete manholes level and plumb and test manholes for leakage per Section 33 0513.

- BURIED PIPING

*************************************************************************************************************

Tracer wire and test stations are required when specifying cast iron, ductile iron, and non-metallic piping.  Comply with Civil Standard Drawing ST-G30GEN-3 for tracer wire/test station details and Civil Standard Drawing ST-G30GEN-4 for trenching detail.

Refer to the LANL Engineering Standards Manual Civil Chapter, Section G30 for required minimum utility line clearances.

Use metallic pipe if PVC or PE sewer line pipe is installed less than 20 feet from steam and condensate lines.

*************************************************************************************************************

    - Refer to Drawings and Section 31 2000 Earth Moving for cover, bedding, tracer wire, wire continuity test, warning tape, documenting new or exposed existing utility location, and other requirements.

    - Slope of service lateral from building to main shall be continuous and uniform without fittings or angled pipe joints.  Slope shall be a minimum slope of 1/4 inch per foot and a maximum slope of 1/2 inch per foot.  Minimum depth of cover shall be 4 feet.

    - Comply with New Mexico Plumbing Code (IAPMO UPC and amendments).

    - Route piping in orderly manner and maintain gradient.

    - Install bell and spigot pipe with bell end upstream.

    - Thrust blocks and restraint shall be installed on sanitary sewer force mains at tees, elbows, and change in direction, per the manufacturer’s written instructions and Section 03 3053.

    - Pressure test piping system with water or air in accordance with Section [22 0813 or 33 0813].

    - Minimum cover over pipe shall be 48 inches measured from finish grade to top of pipe.

- SEWER CLEANOUT

- Cleanouts shall consist of single or double preformed wye, riser pipe, and access top.

- Double cleanout shall be placed at five feet from building wall. A cleanout shall be placed at a change in direction in service laterals.  The distance between cleanouts in service laterals shall not exceed 100 feet.

- Riser pipes shall be one piece extended to grade with top adapter for a countersunk threaded plug.

- Sand bedding or fine graded backfill material shall be compacted around riser pipe.

- Cleanouts at grade shall have concrete collars eighteen (18) square by six (6) inches thick with 6X6X10 gauge (W1.4) wire fabric reinforcement.  Concrete shall be continuous at double cleanouts.  Collar shall be flush with finish grade or pavement.

- Horizontal Directional Drilling or Pipe Bursting

- Crossing of paved streets or roadways or other areas, if approved by LANL U&I group representative, may be accomplished by horizontal directional drilling (HDD) or pipe bursting, whenever practical.  The HDD bore backreamer diameter shall be kept to a minimum to allow the pipe to be drawn in.  For HDD the minimum slope for gravity sanitary sewer systems shall be three percent.  Care shall be exercised to ensure the paved surface and other utilities are not damaged during the drilling operation.

- Top of HDD shall have a minimum below grade bury depth of 48 inches and a minimum bury depth of 60 inches below any paved surface.  Depth shall not exceed excavation by standard, conventional means and shall be approved by LANL U&I group representative.

- When pulling in pipe the pulling force shall be monitored and kept below the Allowable Tensile Load (ATL) value of the pipe size and material per manufacturers’ recommendation.  Both pipe ends shall be monitored for continuous, smooth movement.  Pulling load from the equipment shall be monitored and the pipe lead end shall be equipped with a weak link device to disengage at the ATL or below.  Manufacturer’s procedures and design parameters shall be followed, in addition to ASTM F1962.

- Polyethylene pipe shall extend 3-5% of the pulled-in length past the termination points to allow for contraction.  Polyethylene pipe shall be allowed 24 hours to recover from the pulling stress and contract to original pre-pull length and allowed to stabilize to buried soil temperature before final tie-ins are accomplished.  A minimum of five (5) feet of pipe shall extend beyond the drilling entrance/exit hole to allow for pipe damage assessment. Tracing wire shall be pulled in with the polyethylene pipe.

- LANL ACCEPTANCE INSPECTION AND TESTING

    - Notify STR at least 15 working days before tie-in to schedule video inspection of piping system.  Inspection will verify that new and existing lines are clean and acceptable for tie-in to commence.

    - Notify STR at least 7 working days before system turnover to schedule second and final video inspection of piping system.  The re-inspection is to assure no debris from construction activity has entered the new or existing system.

END OF SECTION

************************************************************

Do not delete the following reference information:

************************************************************

THE FOLLOWING REFERENCE IS FOR LANL USE ONLY

This project specification is based on LANL Master Specification 33 3000 Rev. 7, June 29, 2015.