SECTION 33 3200

wastewater utility pumping stations

*************************************************************************************************************

LANL MASTER SPECIFICATION

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Civil POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

This specification is intended for multiple or large (e.g., Line Item) buildings.  Single GPP-type building should install a small interior station.

Coordinate this Specification with Civil Standard Drawings ST-G3020-2, Exterior Sewage Lift Station.

*************************************************************************************************************

# GENERAL

## SECTION INCLUDES

Submersible pumps and equipment for sanitary sewer lift station.

## LANL PERFORMED WORK

- LANL Utilities and Institutional Facilities (U&I) Group will perform acceptance inspection, testing, final adjusting and tie-in of lift station. See PART 3.

## SUBMITTALS

*************************************************************************************************************

The LANL U&I Group Wastewater Representative shall approve design, location, and submittals of sewage lift station.  Lift station depth shall not exceed 16 feet as measured from finish grade to wet well floor.

*************************************************************************************************************

Submit the following in accordance with project submittal procedures:

- Action Submittals

Catalog data on each item of equipment to be incorporated into the lift station.

Power and Control Cables.

- Closeout Submittals

- Pump curves.

Operation and maintenance data.

        - Theory of operation.

        - Test procedure.

Warranties.

## WARRANTY

- Pumps shall be supplied with manufacturer's printed warranties.

- Provide five years or 10,000 elapsed-time hours warranty after installation, including parts and labor.

- Provide for repairs to be performed at the manufacturer's authorized warranty repair station located within a 200 mile radius of this Project.

## Quality Assurance

*************************************************************************************************************

Items available with NRTL label must be NRTL listed. Refer to ESM Chapter 7, Section D5000 (e.g., paragraph 5.12) and also LANL Electrical Safety P101-13.

*************************************************************************************************************

- Provide Nationally Recognized Testing Laboratory (NRTL) listed material and equipment for the application and environment in which installed.

- Install electrical motors, equipment, and wiring in accordance with the National Electrical Code.

# PRODUCTS

## Product options and substitutions

- Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

## ACCEPTABLE PUMP MANUFACTURER

- Flygt - No Substitutions.

## PERFORMANCE AND DESIGN REQUIREMENTS

- Pumps shall be readily removable and replaceable without de-watering wet well or disconnecting any piping in wet well.

- See also Equipment Schedule in PART 3.

## PUMP MATERIALS

- Provide pumps that are NRTL listed to UL 778 Motor Operated Water Pumps.

- Volute, impeller, motor housing, discharge elbow, and other components: Gray cast iron, ANSI Class 30.

- Shaft: Stainless steel or carbon steel.

- Motor:

- Rotor bars and short circuit rings: Aluminum.

- Windings: Copper.

- Stator winding and lead insulation: NEMA Class F.

Mechanical Seals:

- Lower: Tungsten carbide/tungsten carbide.

- Upper: Tungsten carbide/carbon.

Wear Ring:

- Case wear ring: Steel with molded nitrile rubber.

- Impeller wear ring: ANSI 304 stainless steel.  Provide on pump greater than 15 HP.

Exposed Nuts and Bolts: ANSI 304 stainless steel.

## PUMP CONSTRUCTION

- Water Tight Sealings: Nitrile rubber O-rings against machined surfaces.

- Cable Entry Design:

- Seal: Torque-free mechanical compression type with strain relief.  Do not use epoxies, silicones, or other secondary sealing.  Submersible cable entry shall be field replaceable without replacing cable.

- Seal junction chamber from motor by terminal board and an elastomer compression seal.

Pump Motor:

- Squirrel cage induction type, housed in air-filled watertight chamber.

- Dip and bake stator three times in NEMA Class F varnish and heat shrink fit into the stator housing.  Do not use designs requiring penetration of stator housing.

- Motor cooling system:

Thermal radiators integrally cast into stator housing, up to 10.5 HP.

Circulation of pumped media through a cooling jacket for 15 HP and larger.

Pump Shaft Bearings:

- Permanently lubricated ball bearings.

- Upper Bearing: Single row deep groove.

- Lower Bearing: Two-row angular contact.

Sealed completely from pump liquid.

Minimum B10 Bearing Life: 20,000 elapsed-time hours at any point on head-capacity curve.

Mechanical Seals: Tandem independent and run in a standard motor oil reservoir.

Impeller: Dynamically balanced, double shrouded, non-clog, single vane capable of handling 3-inch-diameter solids, unless otherwise scheduled.

Equip each pump with stainless steel lifting chain and submersible pump cable.

Provide sliding guide bar bracket unit to guide on at least two rails which is an integral part of pump unit.  Do not permit any portion of the pump or guidance system to bear on sump floor.  Do not use guide cables.

Provide metal-to-metal discharge pump/elbow connection seal.  Do not use diaphragm or o-ring type seals.

## PERFORMANCE

- Pump motor:

- 3 phase motor.

- Non-overloading throughout pump curve.

- Capable of 15 evenly spaced starts per hour.

- Capable of running dry indefinitely without damage.

- Motor shall be rated for the site elevation.

## PROTECTIVE COATING

- Pump Exterior: PVC epoxy primer and chloric rubber paint finish.

- Impeller: PVC epoxy or Rislan.

## ACCESSORIES

- Pump accessories supplied by pump manufacturer.

- Provide pump accessories required for proper installation and/or as recommended by manufacturer, including the following.

- Upper and intermediate guide bar brackets with stainless steel nuts and bolts.

- Stainless steel guide rails and brackets with stainless steel nuts and bolts.

- Stainless steel chain lifting system with shackles.

- Safety chain hook.

- Cable holder for pump cable and float cables.

- Cable support grip.

- Anchorage.

- Cable rack for liquid level float system.

- Self-weighted float switch, Flygt Model ENM-10.  Provide complete back-up operating four part float system.

- Flygt Mix Flush Valve Model 4901, mounted on one pump in wet well.

- Check valve, flanged ends, line size, Flygt Model HDL 5087.

- Plug valve, eccentric, flanged ends, line size, BUNA packing, neoprene plug facings, lever handle, DeZuric series 100, Fig. No. 118.

- Standard discharge connection.

- Wet Well: Aluminum access frame and cover, single door with spring assist, 48 inches x 36 inches, with stainless steel hinges and accessories, locking mechanism to accept a Best brand government padlock, and hinged safety grating built-in.  Grating hinges shall be along side of door opening.

- Dry Well: Aluminum access frame and cover, single door, 36 inches x 36 inches, with stainless steel hinges and accessories, and locking mechanism to accept a Best brand government padlock, and hinged safety grating built-in.  Grating hinges shall be along side of door opening.

- Transducer Containment Fittings:

- 8 x 6 inch PVC Schedule 40 reducer coupling.

8-inch PVC Schedule 40 cap.

8-inch Schedule 40 pipe.

Controls:

  - RACO Verbatim – No substitute, including the following.

        - Enclosure – NEMA 4X.

        - Environmental – Heater.

        - Local alarm relay output.

  - Milltronics Hydro-Ranger 200, Part No. 7ML1034 - 1AA1 with Echomax XPS-10 transducer, Part No. 7ML1115 - 0CA31.

  - NEMA 4X enclosure box for mounting of RACO Verbatim outside of, but attached to, motor control center.  Provide connections in motor control center for RACO Verbatim unit.

  - Telephone line grounding/terminator box, Hoffman No. A-1086CHQRFG, with 1/2 inch plywood backing plate mounted inside. Mount box beside and connect to the RACO Verbatim box with 3/4 inch conduit nipple.

  - RACO Verbatim enclosure and backplate, Hoffman No. A-201608LP and No. A-20P16.

Standby Generator Connections:

**************************************************************************************************** If the lift station pump has a Rated Power that is greater than 10 horse power (277/480, 80 amp) do not furnish the Standby Generator Connection. Provide a Portable Pump Quick Disconnect specified in Part 2.8.E.
****************************************************************************************************

  - Furnish means to connect the lift station motor control panel to a portable standby generator; meet the requirements of NEC Article 702.

  - Provide a double-throw fusible safety switch that will serve as a manual transfer switch to connect the lift station to either utility power or a standby generator.

      - Switch shall be rated 100 amperes, 480 volts and shall include two mechanically interlocked fusible switches in a NEMA 3R enclosure. Rating shall be equal to or greater than the circuit feeder.

      - Provide switch with an external operating handle that can be padlocked in either position.

      - Switch must be NRTL-listed to UL 98 Enclosed and Dead Front Switches and NRTL-listed for use as service entrance equipment.

      - Manufacturer: Square D, Cutler-Hammer, Westinghouse

      - Provide six Class R 100 ampere dual-element time-delay fuses and six spare fuses.

      - Switch shall be installed on the circuit feeder before the controller and connected to the input terminal lugs.

3.	Provide watertight pin and sleeve power inlet device and matching connector body for connecting the generator to the double-throw safety switch.

      - Devices must be NRTL-listed to International Standards IEC 309-1 and 309-2.

      - Provide devices rated for 100 amperes, 480 Vac, 3-phase, 4-wire; the fourth wire is the equipment grounding conductor.

      - Provide closure caps for inlet device and connector body.

      - Provide metallic angle back box for the inlet device.

      - Manufacturer: Hubbell HBL4100B7W inlet, HBL4100C7W connector, BB1002W back box, PC100 closure caps.

Portable Pump Quick Disconnect

  - Furnish means to connect a portable, fuel powered sewage pump to bypass the normal lift station pumps. The outlet hose will be connected via a quick disconnect installed in the dry well down stream of the flanged plug valve.

    - Fittings: AWWA C153, Ductile-Iron Compact Fittings, Class 350. Size [4], [6], [8] inch MJ x FLG with 4” flanged outlet. MJ joints restrained with Megalug Series 1100, malleable/ductile iron joint retainer/restraint gland with polymer, epoxy or bituminous outside coating.

    - Valve: Mueller, No. A-2360-6, 4 inch FL x FL, AWWA C509, non-rising stem, open left, handwheel.

    - Riser: 4 inch stainless steel nipple 12 inch length.

    - Hose Coupling: Dixon Bayco cam and groove coupling connector male 4 inch, aluminum, Type D female coupler x female NPT with dust plug.

## MOTOR CONTROL CENTER

**************************************************************************************************** Control Center shall be installed on centerline of the wet well with the control panel access door facing the wet well. ****************************************************************************************************

- Provide motor center panel that is NRTL listed to UL 508 Industrial Control Equipment. Where directly connected to electrical utility service, provide motor control panel that is NRTL-labeled for service entrance use.

- Duplex pump control panel supplied by pump supplier.

- Manufacturer: E.G. Pumps Controls.

Provide duplex pump controls required for proper installation and/or as recommended by manufacturer including the following:

- If MCC is required provide it with separate cubicle to accommodate Milltronics unit with glass view port on door.

- Two pump Circuit Breakers:  UL interrupting rating not less than 14,000 amperes RMS symmetrical at 480 volts or 22,000 amperes RMS symmetrical at 240 volts.

- Two NEMA rated, full voltage non-reversing motor starters.

- Duplex Logic Chassis (an anodized aluminum sub-assembly) with Logic Panel Including:

- Two Hand-Off-Auto selector switches.

- Two run pilot lights (red).

- Two off pilot lights (green).

- Level alarm pilot light.

- Alarm silence pushbutton.

- Motor over temperature sensor – shut pump down.

- LED status indication pilot lights for each relay function.

- GFCI 120 Vac duplex convenience receptacle.  Mount inside on front plate.

Space heater to prevent condensation within the enclosure.

Ground lugs for pump and service connections.

Enclosure NEMA 3 R gasketed outer door with lockable latches, dead front panel.

Additional control breaker - 15 A, 1 pole.

Control power transformer - 2 KVA, 16.7 amps.

Phase Monitor Relay, 200-240 volt or 440-480 volt, 3-phase as required; capable of detecting loss of a single phase, under-voltage, over voltage, and voltage unbalance. Alarm shall be sent to the RACO Verbatim unit.

Lightning surge arrestor.

Elapsed time meter for each pump.

Lag pump time delay relay.

Seal failure relay, Flygt, with pilot light.

Alarm beacon with flasher.

Alarm memory circuit to maintain alarm beacon until manually reset.

Alarm and control enclosure.

Additional isolated dry contacts.

- Motor over-temperature (2) - contact type form "C".

- Motor overload trip (2) - contact type normally open.

- Seal failure (2) - contact type form "C".

- Power failure - contact type form "C".

- Analog 4-20MA level indicator (note this can be provided by Hydro-Ranger)

- Pump run contacts (2) form “C”

High-level float status light.

High-level float test switch.

Local control panel disconnect.  Mount beside, but exterior to, the control panel.

Main breaker.

Operating voltage sign and station name.

## POWER and control cables

- Provide for all cables to connect between motor control center, motors, control devices, and electrical devices. Cables shall be based on the pump manufacturer’s products and requirements.

## Piping

- Ductile Iron Pipe: AWWA C151.

Joints and Fittings: Flanged, ANSI/AWWA C115/A21.15.  Specially designed gaskets shall be provided per the appendices of AWWA C110, C111, and C115.

Pipe and Fittings: Cement mortar lined with bituminous outside coating.

Coupling Sleeve:  Tyler Union, Star Pipe Products, mechanical joint solid sleeve, long style.  Gasket suitable for pipe material being joined.

# EXECUTION

*************************************************************************************************************

The LANL U&I Group Wastewater Representative shall approve design, location, and submittals of sewage lift station.  Lift station depth shall not exceed 16 feet as measured from finish grade to wet well floor.

*************************************************************************************************************

## iNSTALLATION

- Wet well and dry well shall be fabricated and installed by the LANL Standard Exterior Lift Station Drawings ST-G3020-2 and per LANL Master Spec Section 33 0513, Manholes and Structures.

- Wet well bottom and walls shall be coated with a two-part, high build epoxy or polyurethane lining.  Material shall have chemical resistance and designed as a structural lining for manholes and vessels in wastewater facilities.

- Verify that surfaces and substrate conditions are ready to receive work as instructed by the product manufacturer before applying lining.

- Apply products in accordance with manufacturer’s instructions.

- Material will be 100% solids by volume.

- Manufacturer: Raven Lining Systems, Zebron Corporation.

- Install pumps and equipment in accordance with manufacturer's instructions, Subcontract Drawings and LANL Standard Drawings ST-G3020-2.

- Install pumps level, plumb, accurately aligned, with leak-proof pump connection, and easily removed without entering wet well.

- Provide vehicle accessible, level, all-weather surface adjacent to control panel that is suitable for positioning a trailer-mounted engine-generator. Install bollards per ST-G30GEN-1 to protect the lift station and prevent vehicles from inadvertently traversing the access doors for the wet and dry wells.

- Install all electrical equipment and electrical boxes outside of lift station pit except for the transducer that is installed by LANL U&I Group.

- Install Millitronics Hydro-Ranger in electrical motor control center.

- Adjust settings as directed by LANL U&I Group.

- Make no splices in cable.

- Furnish and install all power connections to and from the control box in accordance with provisions of Division 26.

- Provide communications link between the lift station monitoring/controls and the TA-46 Wastewater Plant PLC system.  System shall be installed and available for testing during the Acceptance Inspection.

## HIGH LEVEL AND BACKUP FLOAT SYSTEM

- Suspend on bracket as shown on Drawings.

- Make no splices in cable.

- Adjust float levels as directed by LANL U&I Group.

## MANUFACTURER'S ON-SITE SERVICE

- Arrange for a factory trained service engineer to be present to check installation and operation.

- Arrange for a factory trained service engineer to provide a minimum of 4 hours per pump station of training to operating personnel on operation and maintenance of pumping equipment.

- Provide a report by the service engineer certifying that equipment has been installed and is operating correctly.

## LANL ACCEPTANCE INSPECTION, TESTING, ADJUSTING, AND TIE-IN

- LANL Subcontract Technical Representative (STR) will contact LANL’s U&I Group Wastewater Representative at least 15 working days in advance to have LANL’s U&I Group perform the following:

- Video inspection of gravity and force main sewer lines.

- Inspection, testing, and adjusting of alarms and controls on lift station.

- Inspection of lift station for compliance with drawings and specifications.

- Tie-ins to existing sanitary sewer system.

LANL STR will ensure that an approved WPF (Waste Profile Form) for all anticipated wastewater from all drains or buildings connected to the sanitary wastewater system has been completed by LANL STR and on file before scheduling tie-ins.  Documentation shall be submitted to the LANL U&I Group wastewater representative prior to utility tie-in. http://enterprise.lanl.gov/forms/1346.pdf

Schedule electrical inspection by the LANL Electrical Authority Having Jurisdiction (AHJ) and Construction Inspector. Do not connect equipment to electrical service until the work has been inspected and approved by LANL.

## Identification

- Install component identification, voltage warning labels, and arc-flash warning labels on motor control center [and manual transfer switch].

- Install placard at generator power inlet indicating phase rotation.

- Refer to Section 26 0553 Identification for Electrical Systems.

## EQUIPMENT SCHEDULE

- Flygt Model [     ] with Impeller Model [     ].

- GPM/TDH (feet): [     ]

- HP: [     ]

- Discharge Pipe (inches): [     ]

- RPM: [     ]

- Volts/Phase: [     ]

- Max motor Input at design point (KW):[     ]

Site elevation: 7500 feet.

END OF SECTION

**********************************************************

Do not delete the following reference information:

**********************************************************

THE FOLLOWING REFERENCE IS FOR LANL USE ONLY

This project specification is based on LANL Master Specification 33 3200 Rev. 7, dated April 2, 2015.