Section 40 0504 
Process Piping

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 3 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Pressure Safety/Mechanical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable Sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements might be necessary if increased confidence in procurement or execution is desired, and independent review is necessary. See LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

      - ==========================================================

      - This Section was developed to meet the requirements for ASME B31.3-2022, Category D, and Normal Fluid Services except cryogenic service. The Designer is expected to select those items for the appropriate Fluid Service, for example, solder is only permitted for Category D Fluid Service. Use of this section for a different fluid category including oxidizers will require a detailed review of ASME B31.3 and LANL ESM Chapter 17 - Pressure Safety. See ASME B31.3, Appendix M, Fig. M300 and LANL ESM Chapter 17 - Pressure Safety Attachment REQ-1 for classifying fluid services.

      - The designer is encouraged to review ASME B31.3; DOE Handbook DOE-HDBK-1132, Design Considerations; and LANL ESM Chapter 13 - Welding, Joining, & NDE, and LANL ESM Chapter 17 - Pressure Safety.

      - The appendices included in this Section is a collection of typical piping specifications used at LANL for process piping. It is unnecessary and can be confusing to have piping materials and components defined in the body of the Section above and in a referenced Appendix. An item must only be identified once and duplicative requirements removed. However, all the information for the item including the Fluid Service, System Application, Location, and Assembly Method must also be identified for each piping component.

      - This Section does not address buried piping. It is the responsibility of the Designer to include provisions for corrosion control of buried piping if necessary. Consult other Sections such as Section << 23 2113 - Hydronic Piping>> for template information on buried piping.

      - All tubing and piping shall be designed to operate in the environmental conditions specified in the project requirements documents for the life of the system.

      - This template was written for, but is not limited to, the following types of ASME B31.3 fluids:

      - Category Normal Fluid Service

        - Process Vacuum (Dry and Wet Vacuum)

        - Glovebox Atmosphere Purge/Dry

        - Radioactive Liquid Waste (RLW)

        - Flammable Liquids ​​​​

        - Flammable Gases as defined by CGA P-23, Standard for Categorizing Gas Mixtures Containing Flammable and Nonflammable Components.

        - Reverse Osmosis (RO) (Membrane Filtration) and Deionized Water systems above 150 psig, below -20 degrees F, or above 366 degrees F

        - Compressed air systems above 150 psig, below -20 degrees F, or above 366 degrees F

        - Specialty Gas (e.g. Argon, Nitrogen, Helium, and other non-flammable gases) above 150 psig, below -20 degrees F, or above 366 degrees F

      - Category D Fluid Service

        - Health Physics Vacuum

        - Specialty Gas (e.g. Argon, Nitrogen, Helium, and other non-flammable gases) below 150 psig and between -20 degrees F and 366 degrees F

        - Reverse Osmosis (RO) (Membrane Filtration) and Deionized Water systems below 150 psig and between -20 degrees F and 366 degrees F

  - *************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

General requirements for tube, pipe, piping components, materials, fittings, valves, flanges, and installation of process piping systems applicable to <<ASME B31.3>>.

        - ******************************************************************************

        - The following subparagraphs are designer choices based on project-specific requirements.

        - ******************************************************************************

Piping/Tubing/Fittings

Flexible Connectors

Flexible Hose Restraints

Flexible Hose Restraint Systems

Gas Regulators

Gas Relief Valves

Strainers

Ball Valves (Thermoplastic 1/2 to 8 Inch)

Pneumatic-Actuated Ball Valves (Thermoplastic 1/2 to 8 Inch)

Diaphragm Valves (Thermoplastic 1/2 to 8 Inch)

Industrial Ball Check Valves (Thermoplastic 1/2 to 8 Inch)

Dielectric Connections

      - ***************************************************************************************

      - The following Sections are not referenced in the body of this Section. Including them are a designer choice.

      - Section << 01 4000 - Quality Requirements - Non-Nuclear>>

      - Section ​<< 01 8113.13 - Sustainable Design>>​

      - ***************************************************************************************

RELATED REQUIREMENTS

Section << 01 2500 - Substitution Procedures>>

Section << 01 3300 - Submittal Procedures>>

Section << 01 4000 - Quality Requirements - Non-Nuclear>>

Section << 01 4115 - Pressure Safety Submittals>>

Section << 01 4444 - Offsite Welding, Brazing and Joining Requirements>>

Section << 01 4455 - Onsite Welding, Brazing and Joining Requirements>>

Section << 01 4525 - Non-Destructive Examination (NDE) Requirements>>​

Section << 01 4631 - Welding, Brazing, and Soldering of Pressure Systems>>​

Section << 01 4731 - Flange Assembly for Pressure Systems>>

Section ​<< 01 8113.13 - Sustainable Design>>​

Section ​<< 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>​

Section ​<< 07 8400 - Firestopping>>​

Section ​<< 22 0529 - Hangers and Supports for Plumbing Piping and Equipment>>​

Section << 22 0548.23 - Vibration and Seismic Controls for Mechanical Systems>>

Section << 22 0554 - Identification for Plumbing,  HVAC, and Fire Piping and Equipment>>

Section << 22 0713 - Plumbing and HVAC Insulation>>​

Section << 22 0813 - Testing Piping Systems>>​

Section << 23 2500 - HVAC Water Treatment>>

Section << 31 2000 - Earth Moving>>

    - **********************************************************************************************

      - In the listing below, designer shall eliminate code and standards that are not applicable to the project and add other code and standards that are. The referenced standards editions are based on the code of record ASME B31.3-2022 and ASME BPVC-2023. If the Code of Record for the project refers to a different version of ASME B31.3 & ASME BPVC, the designer is responsible to update the years/editions for the invoked standards. If the invoked standards editions do not comply with those referenced by the Code of Record, EOR needs to evaluate and verify those for equal or better. For the standards without an edition/year, the latest edition is to be used. In addition, the designer must ensure the code and standards editions align between sections in the project specification package and the project design drawings.

      - Note: ASCE 7 edition is based on Code of Record IBC 2021.

      - The following reference standards are only listed in the Appendices form:

      - <<ASME B16.1>>

      - <<ASME B16.20>>

      - <<ASME B16.21>>

      - <<ASME B16.25>>

      - <<ASME B16.34>>

      - <<ASME B18.2.1>>

      - <<ASME B18.2.2>>

      - <<ASME B18.21.1>>

      - <<ASME B36.19M>>

      - <<ASTM A193>>

      - <<ASTM A194/A194M>>

      - <<ASTM  A307>>

      - <<ASTM A395/A395M>>

      - <<ASTM A479/A479M>>

      - <<ASTM A563/A563M>>

      - <<ASTM D2513>>

      - <<ASTM D3261>>

      - <<ASTM F436/F436M>>

      - <<MSS SP-72>>

      - Designer shall manually include applicable standards below when using Appendices in lieu of specifying in Part 2.

    - **********************************************************************************************

REFERENCE STANDARDS

ASCE 7 - Minimum Design Loads and Associated Criteria for Buildings and Other Structures.

ASME B1.1 - Unified Inch Screw Threads (UN, UNR, and UNJ Thread Forms).

ASME B1.20.1 - Pipe Threads, General Purpose, Inch.

ASME B16.1 - Gray Iron Pipe Flanges and Flanged Fittings: Classes 25, 125, and 250.

ASME B16.5 - Pipe Flanges and Flanged Fittings:  NPS 1/2 Through NPS 24 Metric/Inch Standard.

ASME B16.9 - Factory-Made Wrought Buttwelding Fittings.

ASME B16.18 - Cast Copper Alloy Solder Joint Pressure Fittings.

ASME B16.20 - Metallic Gaskets for Pipe Flanges.

ASME B16.21 - Nonmetallic Flat Gaskets for Pipe Flanges.

ASME B16.22 - Wrought Copper and Copper Alloy Solder-Joint Pressure Fittings.

ASME B16.24 - Cast Copper Alloy Pipe Flanges, Flanged Fittings, and Valves: Classes 150, 300, 600, 900, 1500, and 2500.

ASME B16.25 - Buttwelding Ends.

ASME B16.34 - Valves — Flanged, Threaded, and Welding End.

ASME B16.39 - Malleable Iron Threaded Pipe Unions:  Classes 150, 250, and 300.

ASME B16.42 - Ductile Iron Pipe Flanges and Flanged Fittings: Classes 150 and 300.

ASME B18.2.1 - Square, Hex, Heavy Hex, and Askew Head Bolts and Hex, Heavy Hex, Hex Flange, Lobed Head, and Lag Screws (Inch Series).

ASME B18.2.2 - Nuts for General Applications: Machine Screw Nuts; and Hex, Square, Hex Flange, and Coupling Nuts (Inch Series).

ASME B18.21.1 - Washers: Helical Spring-Lock, Tooth Lock, and Plain Washers (Inch Series).

ASME B31.3 - Process Piping.

ASME B36.19M - Welded and Seamless Wrought Stainless Steel Pipe.

ASME BPVC Section XIII - BPVC.XIII - BPVC Section XIII-Rules for Overpressure Protection.

ASME BPVC-IX - Boiler and Pressure Vessel Code, Section IX - Qualification Standard for Welding, Brazing, and Fusing Procedures; Welders; Brazers; and Welding, Brazing, and Fusing Operators.

ASTM  A307 - Standard Specification for Carbon Steel Bolts, Studs, and Threaded Rod 60,000 PSI Tensile Strength - 2007b (ASME B31.3).

ASTM A53/A53M - Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless - 2016 (ASME B31.3), 2012 (ASME B31.9).

ASTM A182/A182M - Standard Specification for Forged or Rolled Alloy and Stainless Steel Pipe Flanges, Forged Fittings, and Valves and Part for High-Temperature Service - 2017 (ASME B31.3).

ASTM A193 - Standard Specification for Alloy-Steel and Stainless Steel Bolting for High Temperature or High Pressure Service and Other Special Purpose Applications - 2010a (ASME B31.3).

ASTM A194/A194M - Standard Specification for Carbon Steel, Alloy Steel, and Stainless Steel Nuts for Bolts for High Pressure or High Temperature Service, or Both - 2017a (ASME B31.3).

ASTM A234/A234M - Standard Specification for Piping Fittings of Wrought Carbon Steel and Alloy Steel for Moderate and High Temperature Service - 2002 (ASME B31.3), 2015 (ASME B31.9).

ASTM A269 - Standard Specification for Seamless and Welded Austenitic Stainless Steel Tubing for General Service - 2008 (ASME B31.3).

ASTM A312/A312M - Standard Specification for Seamless, Welded, and Heavily Cold Worked Austenitic Stainless Steel Pipes - 2017 (ASME B31.3).

ASTM A351/A351M - Standard Specification for Castings, Austenitic, for Pressure-Containing Parts - 2018 (ASME B31.9).

ASTM A395/A395M - Standard Specification for Ferritic Ductile Iron Pressure-Retaining Castings for Use at Elevated Temperatures - 1999(R2018) (ASME B31.3).

ASTM A403/A403M - Standard Specification for Wrought Austenitic Stainless Steel Piping Fittings - 2016 (ASME B31.3).

ASTM A479/A479M - Standard Specification for Stainless Steel Bars and Shapes for Use in Boilers and Other Pressure Vessels - 2017 (ASME B31.3).

ASTM A563/A563M - Standard Specification for Carbon and Alloy Steel Nuts (Inch and Metric) - 2007a (ASME B31.3).

ASTM B68/B68M - Standard Specification for Seamless Copper Tube, Bright Annealed - 2002 (ASME B31.3), 2011 (ASME B31.9).

ASTM B75/B75M - Standard Specification for Seamless Copper Tube - 2002 (ASME B31.3), 2011 (ASME B31.9).

ASTM B88 - Standard Specification for Seamless Copper Water Tube - 2003 (ASME B31.3), 2014 (ASME B31.9).

ASTM B280 - Standard Specification for Seamless Copper Tube for Air Conditioning and Refrigeration Field Service - 2008 (ASME B31.3), 2018 (ASME B31.5), 2016 (ASME B31.9).

ASTM D1784 - Standard Classification System and Basis for Specification for Rigid Poly(Vinyl Chloride) (PVC) Compounds and Chlorinated Poly(Vinyl Chloride) (CPVC) Compounds.

ASTM D1785 - Standard Specification for Poly(Vinyl Chloride) (PVC) Plastic Pipe, Schedules 40, 80, and 120 - 2015 (ASME B31.3).

ASTM D2241 - Standard Specification for Poly(Vinyl Chloride) (PVC) Pressure-Rated Pipe (SDR Series) - 2015 (ASME B31.3).

ASTM D2467 - Standard Specification for Poly(Vinyl Chloride) (PVC) Plastic Pipe Fittings, Schedule 80 - 2006 (ASME B31.3).

ASTM D2513 - Standard Specification for Polyethylene (PE) Gas Pressure Pipe, Tubing, and Fittings - 2009 (ASME B31.3).

ASTM D2672 - Standard Specification for Joints for IPS PVC Pipe Using Solvent Cement - 1996a(R2003) (ASME B31.3).

ASTM D2846/D2846M - Standard Specification for Chlorinated Poly(Vinyl Chloride) (CPVC) Plastic Hot- and Cold-Water Distribution Systems - 2019 (ASME B31.3).

ASTM D3261 - Standard Specification for Butt Heat Fusion Polyethylene (PE) Plastic Fittings for Polyethylene (PE) Plastic Pipe and Tubing - 2003 (ASME B31.3).

ASTM D3350 - Standard Specification for Polyethylene Plastics Pipe and Fittings Materials.

ASTM F436/F436M - Standard Specification for Hardened Steel Washers - 2002(R2009) (ASME B31.3).

ASTM F438 - Standard Specification for Socket-Type Chlorinated Poly(Vinyl Chloride) (CPVC) Plastic Pipe Fittings, Schedule 40 - 2009 (ASME B31.3).

ASTM F439 - Standard Specification for Chlorinated Poly (Vinyl Chloride) (CPVC) Plastic Pipe Fittings, Schedule 80 - 2009 (ASME B31.3).

ASTM F441/F441M - Standard Specification for Chlorinated Poly(Vinyl Chloride) (CPVC) Plastic Pipe, Schedules 40 and 80 - 2015 (ASME B31.3).

ASTM F442/F442M - Standard Specification for Chlorinated Poly(Vinyl Chloride) (CPVC) Plastic Pipe (SDR–PR) - 2013 (ASME B31.3).

ASTM F714 - Standard Specification for Polyethylene (PE) Plastic Pipe (DR-PR) Based on Outside Diameter - 2013 (ASME B31.3).

ASTM F1970 - Standard Specification for Special Engineered Fittings, Appurtenances or Valves for use in Poly (Vinyl Chloride) (PVC) or Chlorinated Poly (Vinyl Chloride) (CPVC) Systems - 2019 (ASME B31.3).

MSS SP-25 - Standard Marking System for Valves, Fittings, Flanges, and Unions - 2018 (ASME B31.3), 2013 (ASME B31.9).

MSS SP-72 - Ball Valves with Flanged or Butt-Welding Ends for General Service - 2010a (ASME B31.3 & B31.9).

NMAC - New Mexico Administrative Code.

SAE J513 - Refrigeration Tube Fittings - General Specifications - 1999 (ASME B31.5), 1999(R2019) (ASME B31.3).

SAE J514 - Hydraulic Tube Fittings - 2012 (ASME B31.3).

SUBMITTALS

Submit the following in accordance with Section << 01 3300 - Submittal Procedures>>.

Action Submittals:

Catalog data on pipe materials, fittings, valves, and accessories. Include the Manufacturer’s name, model number, parts list, and brief description of equipment and its basic operational features.

        - ******************************************************************************

        - For high-risk applications such as ML-1 or ML-2, add submittals for “Weld Filler Material Control Procedures” and “Filler Material Certified Material Test Reports CMTRs” when required. Add “Post-Weld Heat Treatment Procedures” when required.

        - ******************************************************************************

Per the requirements of Section(s) << 01 4444 - Offsite Welding, Brazing and Joining Requirements; and  01 4455 - Onsite Welding, Brazing and Joining Requirements>>, submit:

          - *******Note: Only required as a submittal for Onsite welding, when subcontractor not using LANL WPS/PQR*******

Welding procedure specification (WPS) and supporting procedure qualification record (PQR).

          - ********Note: Only required as a submittal for Onsite welding, when subcontractor not tested at LANL*******

Welder performance qualification records (WPQR) including continuity.

        - ******************************************************************************

        - Examination requirements vary based on the ASME Fluid Service Category. See ASME B31.3 341 Examination to determine the necessary NDE submittal requirements.

        - ******************************************************************************

Per the requirements of Section ​<< 01 4525 - Non-Destructive Examination (NDE) Requirements>>​, submit:

Written Practice or Procedure for Qualification and Certification of NDE personnel.

NDE Personnel Qualification Records

NDE Procedures

NDE Procedure Qualification Records

NDE Report(s)

NTIP submitted under Section << 01 4525 - Non-Destructive Examination (NDE) Requirements>>.

Before fabrication, submit:

Proof of journeyman certificate of competence in accordance with <<NMAC>> Section 4.6.6.11

Leak test plan submitted under Section << 22 0813 - Testing Piping Systems>>.

Cleaning procedures for joint assembly preparation

          - **********************************************************************

          - The following subparagraph is a designer choice.

          - **********************************************************************

Certified Material Test Reports (CMTR) for metallic piping and components required by the code of record specified below:

<<ASTM A269>>

After fabrication, submit:

          - **********************************************************************

          - Designer shall include the subparagraph below when factory custom-fabricated piping assemblies, skids, or modular units are specified in this Section.

          - **********************************************************************

Factory Acceptance Test Report

Examination records per <<ASME B31.3>> paragraph 346.3

Informational Submittals at Closeout

Spare Parts and Maintenance Materials list

Installation, Operation, & Maintenance Manual

Warranties

        - ******************************************************************************

        - Designer shall include the subparagraph below when specifying an ASME pressure vessel in this Section.

        - ******************************************************************************

Manufacturer’s data report form for ASME pressure vessels (e.g., ASME Form U-1) showing National Board registration

QUALITY ASSURANCE

Material and Installation: Conform to <<ASME B31.3>>​ for Category D and Normal Fluid Services.

      - ***************************************************************************************

      - The following paragraph is a designer choice and should be included when welding is a joining method specified in this Section.

      - ***************************************************************************************

Welders Certification and Qualified Procedure Standards shall be in accordance with <<ASME BPVC-IX>>. Welding per Section(s) << 01 4444 - Offsite Welding, Brazing and Joining Requirements; and  01 4455 - Onsite Welding, Brazing and Joining Requirements>>.

NDE Personnel Certification and NDE Procedures shall be per Section << 01 4525 - Non-Destructive Examination (NDE) Requirements>> .

Valve Identification: Each valve shall bear markings in accordance with <<MSS SP-25>>, including manufacturer’s name or trademark, the material of construction, and symbols to indicate the service conditions for which the manufacturer rates the valve.

Component identification shall follow LANL ESM Chapter 1 - General, Section 200, Item Numbering and Labelling. At existing facilities, component labeling conventions are to be continued to be used to avoid confusion.

Design pressure and temperature of piping systems within this Section is provided in the Pressure Safety Implementation Plan, contained in << Drawing Number; or  Document Number>> << _______>>.

      - ***************************************************************************************

      - The Designer is cautioned to include sufficient training and written procedures for proprietary or unlisted fitting and/or joint assembly.

      - ***************************************************************************************

Compression fitting assembler shall be qualified by UTrain Course 30831, Compression Fittings Assembly, or factory training within 30 days of start of assembly.

LANL Owner’s Inspector shall be qualified in accordance with <<ASME B31.3>> Section 340 and LANL Engineering Services Inspection Team. LANL shall act for DOE to designate Owner’s Inspectors or Designee.

PART 2 - PRODUCTS

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted per Sections << 01 2500 - Substitution Procedures>> and << 01 4115 - Pressure Safety Submittals>>.

Proposal of unlisted components as substituted components is strongly discouraged and shall be evaluated per Section << 01 2500 - Substitution Procedures>>. Substitutions will be allowed only if the Subcontractor can demonstrate that the product can meet the same code requirements of the item specified in the design. Costs associated with evaluation of substituted unlisted components shall be the responsibility of the Subcontractor.

SEISMIC PERFORMANCE REQUIREMENTS

      - ***************************************************************************************

      - The seismic exemptions noted below are based on ASCE 7-16. If the Code of Record for the project refers to a different version of ASCE 7, the Designer is responsible to check the seismic design requirements per that applicable edition.

      - ***************************************************************************************

Piping systems with trapeze assemblies/rod hangers that meet the requirements per <<ASCE 7>>, Section 13.6.7.3 are seismically exempt.

For piping systems not meeting the above exemption, Structural EOR shall design seismic supports per LANL ESM Chapter 5 - Structural, Section II; <<ASCE 7>>, Chapter 13; <<ASME B31.3>><< ; Section  01 8734 - Seismic Qualification of Nonstructural Components (IBC);  ; Section 22 0548.23 - Vibration and Seismic Controls for Mechanical Systems; or  None - N/A>>.

      - ***************************************************************************************

      - It is unnecessary and can be confusing to have piping components defined in the body of the Section and in a referenced Attachment. An item must only be identified once, so edit Section appropriately.  However, all the information for the item including the fluid service, system application, location, and assembly method must also be identified for all piping components wherever they are in the section.

      - Threaded joints should be avoided in any service where crevice corrosion, severe erosion, or cyclic loading (pressure or thermal) may occur.

      - Buried RLW shall be double-wall piping.

      - Piping containing radiological fluid shall not be erected with a liquid hold-up (e.g., a P-trap). Piping shall be installed such that it drains continuously to its final location.

      - Gasket materials shall be compatible with the fluids and service conditions.

      - Provide safe access or remote operators where valves and fittings are not exposed or installed over 7 feet in height above finished floor.

      - If using tubing with Swagelok compression fittings in gas service, refer to Swagelok Publication MS-01-107 for minimum required wall thickness.

      - Thermoplastics shall not be used in flammable fluid service above ground unless they are approved by LANL in accordance with ASME B31.3, A323.4.2(a)(1).

      - PVC and CPVC shall not be used in compressed air or other compressed gas service.

      - All the following components (disregarding ASME BPVC items) are either standard piping components (listed items) per ASME B31.3 para. 326 or have previously LANL approved unlisted component evaluations in accordance with ASME B31.3 para. 304.7.2.

      - The types of components shown may be a non-exhaustive list. Any substitutions or additions shall be ASME B31.3 compliant. All previously LANL approved ASME B31.3 components are available in the LANL ESM Chapter 17 - Pressure Safety, Approved ASME Unlisted Material/Component List and Approval Process under Chapter References and Resources.

      - In the paragraphs/subparagraphs in the Articles below, designer is to select "Refer to Appendix..." or the sequence below it. When the latter is selected, all relevant sequences below it are activated.

      - The following PART 2 Articles are designer choices based on project-specific conditions. Within each Article, paragraphs related to pipe material types, fitting types, component size ranges, system application etc. are designer choices based on project-specific requirements.

      - ***************************************************************************************

PIPING/TUBING/FITTINGS

Stainless Steel Pipe

Refer to Appendix << _______>>.

Pipe: <<ASTM A312/A312M>>, Dual Grade TP316/316L, seamless, Schedule << 10;  40;  80; or  160>>.

Fluid Service: Category ​<< Normal;  D; or  _______>>​.

System Application(s):

Specialty Gases: << Argon;  Nitrogen;  Helium;  P-10;  Regen Gas; or  _______>> above 150 psig or below -20 degrees F or above 366 degrees F

Radioactive Liquid Waste

​<< _______>>​

        - ******************************************************************************

        - If below grade option is selected, specify Corrosion Control by adding an article in Part 3, Corrosion Control

        - ******************************************************************************

Location: << Above grade; or  Below grade>>.

Assembly Methods: ​<< Welded;  Brazed;  Solder;  Flanged;  ASME B1.20.1 NPT;  Lok-Ring ®; or  _______>>​

Flanges:  Raised Face, Weld neck, Slip-on, and Blind Flanges: <<ASME B16.5>> Material Group 2.3 Forging, Class 150

Fittings: Buttweld <<ASME B16.9>>, <<ASTM A403/A403M>> WP316/316L, Class S

<< _______>>

Size: << 4 inch; or  _______>>.

Steel Pipe

Refer to Appendix ​<< _______>>​.

Pipe: Black steel, <<ASTM A53/A53M>>, Type F, Grade A, Schedule << 40; or  80>>.

Fittings: Steel, <<ASTM A234/A234M>>, Grade WPB or WPC, <<ASME B16.9>> buttweld type, wall thickness to suit pipe schedule.

Fluid Service:  Category Normal

System Application(s):

Compressed air systems greater than 150 psig.

<< _______>>

        - ******************************************************************************

        - If below grade option is selected, specify Corrosion Control by adding an article in Part 3, Corrosion Control

        - ******************************************************************************

Location: << Above grade; or  Below grade>>.

Assembly Methods: ​​<< Welded;  Flanged;  MNPT  ASME B1.20.1;  Lok-Ring ®; and  _______>>​​.

Size: << 4 inch; or  _______>>.

PVC Pipe

Refer to Appendix ​<< _______>>​.

Pipe: ​​​<< ASTM D1785 , PVC 1120, Type I, Gr. 1, Cell Classification 12454; or  ASTM D2241 , Schedule 80, Cell Classification 12454>>​​​.

Fittings: ​<< ASTM D2467; or  ASTM D2672>>​.

Fluid Service:  Category D

System Application(s):

Deionized water system less than 150 psig and between -20 degrees F and 366 degrees F

<< _______>>

Location: << Above grade; or  Below grade>>.

Assembly Methods: << Solvent welded;  ASME B1.20.1 NPT (Schedule 80 minimum); and  _______>>

Size: ​<< 4 inch; or  _______>>​

CPVC Pipe

Refer to Appendix ​<< _______>>​.

Pipe: << ASTM F441/F441M Schedule 40;  ASTM F441/F441M  Schedule 80; or  ASTM F442/F442M  (SDR-PR)>>, cell class 23447

Fittings:  Material: ​​<< ASTM D2846/D2846M; or  ASTM D3350>>​​, Standard: ​​<< ASTM F438 (Schedule 40); or  ASTM F439  (Schedule 80)>>​​.

Fluid Service: Category << Normal; or  D>>.

System Application(s):

Radioactive Liquid Waste

Deionized water system less than 150 psig and between -20 degrees F and 366 degrees F.

<< _______>>

Location: << Above grade; or  Below grade>>.

Assembly Methods: << Solvent welded;  ASME B1.20.1 NPT (Schedule 80 minimum); and  _______>>

Size: ​<< 4 inch; or  _______>>​.

Double Wall Hi-Density Polyethylene (HDPE) Pipe

Refer to Appendix ​<< _______>>​.

Pipe: <<ASTM F714>> with Cell Classification PE445574C per <<ASTM D3350>>, HDPE PE4710

Wall Thickness: Internal wall thickness shall conform to dimension ratio DR 11. Exterior or containment pipe wall shall conform to DR 17.

Manufacturer: ASAHI (Poly-Flo or Fluid-Lok), Performance Pipe or LANL-approved equal

Fittings:  Factory Molded Fittings

Fluid Service:  Category Normal

System Application(s):  RLW Carrier and Containment Pipe

Location: ​<< Above grade; or  Below grade>>​.

Assembly Methods: << Welded;  ASME B1.20.1 NPT; and  _______>>

Size: ​<< 4x6 inch; or  _______>>​.

Stainless Steel Tubing

Refer to Appendix ​<< _______>>​.

Tubing: <<ASTM A269>>, Dual Grade 316/316L, Seamless

Tubing Wall Thickness: ​<< ____>>​.

Fluid Service: Category ​<< Normal; or  D>>​.

System Application(s):

Specialty Gases: << Argon;  Nitrogen;  Helium;  P-10;  Regen Gas; or  _______>>, above 150 psig, below -20 degrees F, or above 366 degrees F.

Specialty Gases: << Argon;  Nitrogen;  Helium;  P-10;  Regen Gas; or  _______>>, up to 150 psig, and  between -20 degrees F and 366 degrees F.

Location: ​<< Above grade; or  Below grade>>​.

Assembly Methods: ​​<< Welded;  Flanged;  CF flanges (Conflat);  Lok-Ring ®;  Swagelok compression fittings;  Flare fittings; and  _______>>​​

Size: << 1 inch; or  _______>>.

Copper Tubing

Refer to Appendix << _______>>.

Copper tubing ​​​<< ASTM B68/B68M;  ASTM B75/B75M;  ASTM B88; or  ASTM B280>>​​​, Alloy ​​​<< 102; or  122>>​​​, Temper ​​​<< O50;  O60;  O61;  O62;  H55;  H58; or  H80>>​​​.

Braze Joints

Fittings: ​​<< ASME B16.18; and  ASME B16.22>>​​ .

Unions: Copper Tube and Pipe: <<ASME B16.22>>, Class 150, bronze unions with soldered joints.

        - ******************************************************************************

        - Solder joints are only permitted for ASME B31.3 Category D fluid service.

        - ******************************************************************************

Solder joints

Fittings: ​​​​<< ASME B16.18; and  ASME B16.22>>​​​​.

45-degree Flare Joints

Fittings: <<SAE J513>>. Description: a 45-degree flare flared body and nut for use with annealed copper tubing. Materials are SAE CA 360 (half-hard), CA 345 or CA 377 (forged) brass with CA377 nuts. Fittings may have a combination of <<ASME B1.1>> UNF (5/16 to 7/8 inch) or UNS 1 1/16 inch and <<ASME B1.20.1>> NPT (1/8 through 3/4 inch). Fittings are available based on outside diameter tube.

37-degree Flare Joints

Fittings: <<SAE J514>>: description: A 37-degree flare flared body, nut, and sleeve for use only with tube that is fully annealed for flaring and bending. Materials brass, fittings may have a combination of <<ASME B1.1>> UNF (5/16 to 7/8 inch) or UNS 1 1/16 inch and <<ASME B1.20.1>> NPT (1/8 through 2 1/2 inch). Fittings are available based on outside diameter tube.

Fluid Service: Category D

System Application(s):

Inert Laboratory Gases: << Argon;  Nitrogen;  Helium;  P-10; or  ______>>, up to 150 psig, and between -20 degrees F and 366 degrees F.

<< _______>>

Location:  Above grade

Size: << 3/4 inch; or  _______>>.

Stainless Steel Tubing, 37-degree Flare Fittings

Refer to Appendix ​<< _______>>​.

Flare Joint Fittings: <<SAE J514>>. Description: A 37-degree flare flared body, nut, and sleeve for only with seamless or welded and drawn tube that is fully annealed for flaring and bending. Materials 316 stainless steel. Fittings may have a combination of <<ASME B1.1>> UNF (5/16 to 7/8 inch) or UNS 1 1/16 inch and <<ASME B1.20.1>> NPT (1/8 through 2 1/2 inch). Fittings are available based on outside diameter tube.

Location: ​​<< Above grade; or  Below grade>>​​.

Fluid Service: Normal

System Application(s):

Flammable Liquids.

Reverse Osmosis (RO) System above 150 psig or below -20 degrees F or above 366 degrees F.

<< _______>>.

Size: ​​​​​​<< 1/4 inch annealed tube outside diameter; or  _______  tube outside diameter inch>>​​​​​​.

Temperature range: -425 to +400 degrees F

Pressure: 7,500 psig 1/4 inch tube to tube (1/4 inch, 4:1 safety factor)

Manufacturer: ​​​<< Parker; or  Pressure Connections Corp>>​​​.

Model Number: ​​​<< Triple Lok®; or  37 Degree JIC Flare>>​​​ .

      - ***************************************************************************************

      - Seismic:  As necessary/applicable, edit what follows, to include PART 3, to ensure compliance with the seismic requirements for flexible connectors.

      - ***************************************************************************************

FLEXIBLE CONNECTORS

Refer to Appendix ​<< _______>>​.

Manufacturer: Swagelok.

Type: << FM;  FJ;  FL;  T;  X;  S;  C;  N;  W;  F; or  U>>.

Material: << _______>>.

Working-Pressure Rating: << _______>>.

End Connections: ​<< Compression;  ASME B1.20.1 NPT; or  _______>>​.

Fluid Service: Category << Normal; or  D>>.

System Application(s): << Flammable gases, and specialty gases above 150 psig or outside the range of -20 degrees F to 366 degrees F;  Deionized water system less than 150 psig and between -20 degrees F and 366 degrees F; or  _______>>.

Flammable Gases: ​<< ______>>​

Specialty Gases: << Argon;  Nitrogen;  Helium;  P-10;  Regen Gas; or  _______>>, above 150 psig, below -20 degrees F, or above 366 degrees F.

<< ______>>

Location:  Above grade

Size: << 3/4; or  _______>>​ inch.

Length: << 36; or  _______>> inches.

Manufacturer: ​<< Global Passive Safety Systems Lifeguard; or  Hose and U.S. Hose Corporation 402X with Spring Guard>>​.

Material: << _______>>.

Working-Pressure Rating: << _______>>.

End Connections: <<ASME B1.20.1>> NPT.

Fluid Service: Category << Normal; or  D>>.

System Application(s): ​<< Flammable gases, and specialty gases above 150 psig or outside the range of -20 degrees F to 366 degrees F; and  _______>>​

Flammable Gases: << ______>>

Specialty Gases: ​<< Argon;  Nitrogen;  Helium;  P-10;  Regen Gas; or  _______>>​, above 150 psig, below -20 degrees F, or above 366 degrees F.

Location: Above grade

Size: << 3/4; or  _______>> inch.

Length: << 36; or  _______>> inches.

      - ***************************************************************************************

      - If specifying flexible connectors greater than 12 inches in length for operating pressures greater than 150 psig, flexible hose restraints are required per LANL ESM Chapter 17 - Pressure Safety Section PS-REQUIREMENTS.

      - If specifying flexible connectors with integral safety features that prevent hose whip in the event of failure, such as Lifeguard safety hose, flexible restraints are not required regardless of hose length or service pressure.

      - ***************************************************************************************

FLEXIBLE HOSE RESTRAINTS

Refer to Appendix ​<< _______>>​.

Manufacturer: Hubbell

Model:  Kellems ® Universal Eye

Material:  Stainless steel 302-304T

Size: 0.5 to 3.99 inches

Types:  << _______>>.

Part number:  << _______>>.

Manufacturer:  Parker Hannifin

Model: ​<< Transportation 201;  Constant Working Pressure P35 or 797TC; or  Hydraulic JK or 302>>​

Size: << 1/4 inch to 4 inch; or  _______>>.

Type: << Port; or  Flange>>.

Example Part Number:  WRC1313-3 (0.51 to 0.531 inch, for Hydraulic 302)

FLEXIBLE HOSE RESTRAINT SYSTEMS

Refer to Appendix ​<< _______>>​.

Restraint

Manufacture:  Adel

Example Part Number:  MS21919-DG16 (1 inch)

Material: Aluminum band, Chloroprene Cushion (212F)

Type:  MS21919 DG

Size:  1/8 inch to 3 1/8 inch

Chain

Trade size: << 4; or  _______>>.

Material: << Low Carbon Steel; or  _______>>.

Finish: << Brass Glo; or  Zinc Plated>>

Size: << 0.12-inch; or  _______>> diameter material

Load: << 205 lbf; or  _______>> working load limit

      - ***************************************************************************************

      - The relief valve is required to have a calculation meeting the rigor of LANL AP-341-605,Calculations (LANL internal only), to show that it can accommodate the fail-open regulator fault condition and meet the design parameters of ASME B31.3 paragraph 322.6 Pressure-Relieving Systems. This requirement is for any liquid or gas. The regulator and relief device shown below are examples only and the articles must be tailored to the design requirements. The designer is cautioned that the design must accommodate flow demand requirements of the system as well as relief valve sizing.

      - ***************************************************************************************

GAS REGULATORS

Refer to Appendix ​<< _______>>​.

Manufacturer/Model: Swagelok K Series, Part Number: ​<< KPR-AGJA415C2000; or  _______>>​.

Description: ​<< Single stage; or  Dual stage>>​, ​<< Brass;  316 Stainless Steel;  Alloy 400 (Monel);  Alloy C-276 (Hastelloy); or  _______>>​ body ​<< Maximum 500 psig inlet, 0- maximum 45 psig outlet; or  _______>>​

Fluid Service: ​<< Normal; or  _______>>​.

System Application(s): ​<< Compressed Air; or  _______>>​.

Inlet Size: 1/4 inch.

Outlet Size: 1/4 inch.

Flow Coefficient (Cv): << 0.20; or  _______>>.

Maximum Inlet Pressure: << 500; or  _______>> psig.

Delivery Pressure Range: << _______>> to << _______>> psig.

Pressure Gauges: << Inlet and Outlet;  Outlet only; or  None>>.

Location: Above grade.

Assembly Method(s): <<ASME B1.20.1>> NPT.

GAS RELIEF VALVES

Refer to Appendix ​<< _______>>​.

Manufacturer/Model: ​<< Kingston Valves, M/N 118, Part Number: 118CSS-2-045; or  _______>>​.

Description: << Brass; or  Stainless Steel>><<ASME BPVC Section XIII>>  stamped relief device.

Fluid Service: << Category D; or  _______>>.

System Application(s): << Compressed Air; or  _______>>.

Inlet Size: << 1/4 inch; or  _______>>.

Outlet Size: << Open to atmosphere;  1/2 inch; or  _______>>.

Set Pressure: ​<< 45 psig; or  _______>>​.

Location: Above grade.

Assembly Methods: <<ASME B1.20.1>> NPT.

Manufacturers rating: << 69; or  _______>> .

STRAINERS

Refer to Appendix << ____>>.

Manufacturer: Spears (Thermoplastic)

Example Part Number:  YS22P12-005 (1/2-inch EPDM), 12 mesh (0.062 inch); Socket

Description:  Sediment strainers: Y-type constructed from PVC Type I, <<ASTM D1784>> Cell Classification 12454 or CPVC Type IV, ASTM D1784 Cell Classification 23447. O-rings shall be EPDM or Viton®.  Y-strainers shall have replaceable PVC, CPVC or Type 316 stainless steel screens and O-ring-sealed drain plugs with magnetic drain plug option. Threaded Y-strainers shall have Special Reinforced (SR) threads.

Rating: Y-Strainers sizes 1/2 to 2 inches pressure rated to 150 psi, sizes 3 to 4 inches to 90 psi for water at 73 degrees F

Fluid Service: Normal

System Application(s): RLW

Location: Above grade

Assembly Methods: ​​​​<< Welded; or  ASME B1.20.1  NPT>>​​​​.

Manufacturer:  Pelmar Engineering Ltd.

Example Part Number:  IFC Series Y150SST (threaded)

Description: One piece cast <<ASTM A351/A351M>>-CF8M Stainless Steel Body, 304SS screen, <<ASTM A182/A182M>> 316SS plug, Teflon gasket, 0.032-inch screen opening

Rating:  275 psig non shock, 200 psig at 400 degrees F, sizes: << 1/2 inch - 3 inch; or  _______>>

Fluid Service: Normal

System Application(s):  RLW

Location:  Above grade

Assembly Methods: ​​​<< Socket welded;  ASME B1.20.1  NPT; or  _______>>​​​.

BALL VALVES (THERMOPLASTIC 1/2 TO 8 INCH)

Refer to Appendix ​<< _______>>​.

Manufacturer:  Spears True Union 2000

Example Part Number:  1829-005 (1/2-inch Socket/ <<ASME B1.20.1>> NPT; EPDM)

Description: True Union 2000 Industrial type manufactured to <<ASTM F1970>> and constructed from PVC Type I, <<ASTM D1784>> Cell Classification 12454 or CPVC Type IV, <<ASTM D1784>> Cell Classification 23447. O-rings: EPDM or Viton®. Safe-T-Shear® stem with double O-ring stem seals. Polypropylene valve handles with built-in lockout mechanism. Valve union nuts with Buttress threads. Safe-T-Blocked® seal carriers. All valve components shall be replaceable.

Rating: All 1/2 inch through 2 inch valves shall be pressure rated to 235 psi, all 2-1/2 inch through 8 inch venturied, and all flanged valves shall be pressure rated to 150 psi for water at 73 degrees F.

Fluid Service: Normal

System Application(s): RLW

Location: Above grade

Assembly Methods: ​​​​<< Welded; or  ASME B1.20.1  NPT>>​​​​

      - ***************************************************************************************

      - Pneumatic-actuated valves are equivalent to the standard True Union 2000 Ball Valves for the purposes of ASME B31.3 (the standards of manufacture and construction are equivalent).

      - ***************************************************************************************

PNEUMATIC-ACTUATED BALL VALVES (THERMOPLASTIC 1/2 TO 8 INCH)

Refer to Appendix ​<< _______>>​.

Manufacturer: Spears True Union 2000 Pneumatic Actuated Ball Valves

Description: True Union 2000 Industrial type manufactured to <<ASTM F1970>> and constructed from PVC Type I, <<ASTM D1784>> Cell Classification 12454 or CPVC Type IV, <<ASTM D1784>> Cell Classification 23447. O-rings: EPDM or Viton®. Safe-T-Shear® stem with double O-ring stem seals. Polypropylene valve handles with built-in lockout mechanism. Valve union nuts with Buttress threads. Safe-T-Blocked® seal carriers. All valve components shall be replaceable.

Rating: All 1/2 inch through 2 inch valves shall be pressure rated to 235 psi, all 2-1/2 inch through 8 inch venturied, and all flanged valves shall be pressure rated to 150 psi for water at 73 degrees F.

Fluid Service: Normal

System Application(s): RLW

Location: Above grade

Assembly Methods: << Welded; or  ASME B1.20.1  NPT>>

DIAPHRAGM VALVES (THERMOPLASTIC 1/2 TO 8 INCH)

Refer to Appendix ​<< _______>>​.

Manufacturer:  Spears

Example Part Number:  2729-005 (1/2-inch, EPDM, Socket/ <<ASME B1.20.1>> NPT)

Description:  Weir-type manufactured to <<ASTM F1970>> and constructed from PVC Type I, <<ASTM D1784>> Cell Classification 12454 or CPVC Type IV, <<ASTM D1784>> Cell Classification 23447. Diaphragms shall be EPDM, genuine Viton® or PTFE with ​​<< EPDM; or  Viton®>>​​ bonded backing. Valves shall have built-in position indicator with polypropylene handwheel. True Union style valve union nuts shall have Buttress threads.

Rating: PVC and CPVC 1/2 inch through 2 inch valves shall be pressure rated to 235 psi, all 2-1/2 inch through 4 inch and all flanged valves shall be pressure rated to 150 psi, all 6 inch valves shall be pressure rated to 100 psi, and all 8 inch valves shall be pressure rated to 75 psi for water at 73 degrees F.

Fluid Service: Normal

System Application(s):  RLW

Location:  Above grade

Assembly Methods: << Welded; or  ASME B1.20.1  NPT>>

INDUSTRIAL BALL CHECK VALVES (THERMOPLASTIC 1/2 TO 8 INCHES)

Refer to Appendix ​<< _______>>​.

Manufacturer/Model: Spear True Union 2000

Example Part Number: 4529-005 (1/2-inch EPDM, Socket/ <<ASME B1.20.1>> NPT)

Description: True Union 2000 Industrial Ball Check type manufactured to ASTM F1970 and constructed from PVC Type I, <<ASTM D1784>>, Cell Classification 12454 or CPVC Type IV, <<ASTM D1784>> Cell Classification 23447. O-rings shall be EPDM or Viton®. Valve union nuts shall have Buttress threads. Valve seats shall be a standard O-ring type. Seal carriers shall be Safe-T-Blocked®. All valve components shall be replaceable.

Rating:  PVC and CPVC 1/2 inch through 2 inch valves shall be pressure rated to 235 psi, 2-1/2 inch through 8 inch venturied, and flanged valves pressure rated to 150 psi for water at 73 degrees F.

Fluid Service: Normal

System Application(s):  RLW

Location:  Above grade

Assembly Methods: << Welded; or  ASME B1.20.1  NPT>>

      - ***************************************************************************************

      - Provide non-conducting dielectric connections whenever joining dissimilar metals in liquid systems with galvanic corrosion potential.

      - ***************************************************************************************

DIELECTRIC CONNECTIONS

Refer to Appendix ​<< _______>>​.

Threaded/Soldered

Manufacturer:  Watts

Model: << 3001A; or  _______>>.

Description: <<ASME B16.39>> union female iron pipe thread per <<ASME B1.20.1>> to copper solder joint

Rating: 250 psig at 180 degrees F

Size: << 1/2 inch to 2 inch; or  _______>>.

Fluid Service: Category D

System Application(s):  Process Water

Location:  Above grade

Assembly Methods: ​<< ASME B1.20.1 NPT and braze; or  ASME B1.20.1  NPT and solder>>​.

Flanged

Manufacturer:  Watts

Model: ​<< 3100; or  _______>>​.

Description:  Galvanized or plated steel threaded end, copper braze (solder) end, and water impervious isolation barrier, minimum rating 250 psig at 250 degrees F. Watts Series 3000.  Flange bolts to be used with bolt insulators.

Rating: 175 psig at 180 degrees F

Size: ​<< 2 inch; or  4 inch>>​.

Fluid Service: Category D

System Application(s):  Process Water

Location:  Above grade

Assembly Methods:  <<ASME B16.42>> (iron), <<ASME B16.24>> (bronze) class 125 flanges, and << ASME B1.20.1 NPT and braze; or  ASME B1.20.1  NPT and solder>>​ ends.

PART 3  - EXECUTION

PREPARATION

Square, ream pipe and tube ends. Remove burrs.

      - ***************************************************************************************

      - Consult manufacturer’s recommendation for the use of acids and cleaning agents to prevent damage.

      - Ensure safeguards are taken to protect personnel from hazards of cleaning, which may include but not be limited to flying particulates, corrosive chemicals, and harmful vapors.

      - A suitable chemical and/or mechanical cleaning method shall be used, if necessary, to clean all surfaces to be fabricated.

      - Review LANL ESM Chapter 17 - Pressure Safety, Section PS-REQUIREMENTS, 8.8, General Pressure System Design, for information on cleaning.

      - ***************************************************************************************

Cleaning:

Remove scale and dirt on inside and outside before assembly.

Cleaning will consist of removing all non-adhering material such as loose scale, sand, weld spatter particles, rust, cutting chips, grinding residue, etc. from the inside of the piping assembly by suitable means. This level of cleaning will allow the presence of mill scale and surface rust.

        - ******************************************************************************

        - Specify any special cleaning requirements below.

        - ******************************************************************************

<< _______>>.

Prepare piping connections to equipment with flanges or unions.

Fastener materials shall be free of nicks, burrs, chips, dirt, and damage (inspect threads, shank, and nuts). All damaged fasteners must be replaced.

INSTALLATION

General

Install piping in conformance with <<ASME B31.3>>​.

Unless noted otherwise on the isometric drawing, field fit-up welds shall include 6 inches of pipe beyond the length required.

        - ******************************************************************************

        - The following subparagraph is a designer choice.

        - ******************************************************************************

Prior to operation: fill, clean, and chemically treat piping system.  Refer to Section ​<< 23 2500 - HVAC Water Treatment>>​.

Label piping system in accordance with Section << 22 0554 - Identification for Plumbing,  HVAC, and Fire Piping and Equipment>>.

        - ******************************************************************************

        - The following subparagraph is a designer choice.

        - ******************************************************************************

Insulate piping system in accordance with Section ​<< 22 0713 - Plumbing and HVAC Insulation>>​. Provide clearance for installation of insulation and access to valves and fittings.

Support piping system in accordance with Section << 22 0529 - Hangers and Supports for Plumbing Piping and Equipment>>.  Do not anchor the pipe.  Allow piping to slide and expand or contract with temperature.

        - ******************************************************************************

        - The following subparagraph is a designer choice.

        - ******************************************************************************

Sleeve and caulk pipes penetrating exterior walls or interior bearing walls.  Provide waterproof installation for exterior walls.  Provide UL/FM approved through-penetration firestop system when penetrating fire rated barriers (e.g., walls, floors, etc.). See Section ​<< 07 8400 - Firestopping>>​. Install chrome-plated steel escutcheons where pipes are not insulated in finished areas.

Route piping in orderly manner and maintain gradient. Route parallel and perpendicular to walls.

For multiple openings in piping mains, the distance between their centers shall be at least the sum of their inside diameters.

Branch connections shall utilize fittings (tee, lateral, or cross) in accordance with listed codes.

Provide non-conducting dielectric connections wherever joining dissimilar metals.  Matching of bronze with steel or copper does not require dielectrics.

Install piping to maintain headroom and neither interfere with use of space nor take more space than necessary. Piping shall not block access to manholes, access covers, etc.

Group piping whenever practical at common elevations.

Install piping to allow for expansion and contraction without stressing pipe, joints, or connected equipment.

All valves shall be installed in accordance with the manufacturer's instructions and with sufficient clearance and access for ease of operation and maintenance. Install valves with stems upright or horizontal, not inverted.

Slope liquid piping at least 1 inch per 40 feet (0.25 percent) in direction of flow and provide drain valves at low points and vents at high points. The use of vertical installation tolerance shall not increase unvented high points unless these are explicitly approved by LANL.

Install pressure gauges vertically.

Keep open ends of pipe free from scale and dirt. Whenever work is suspended during construction, protect open ends with temporary plugs, caps, or residue-free tape.

        - ******************************************************************************

        - The following subparagraph is a designer choice.

        - The Designer is cautioned to include sufficient training and written procedures for proprietary or unlisted fitting and/or joint assembly.

        - ******************************************************************************

Install flexible connections where shown on drawings.

Fabrication

Piping shall be fabricated in accordance with the provided<< Construction; or  None - N/A>> Drawings.

        - ******************************************************************************

        - Designer may allow tube bends and edit subparagraph below but must then provide thickness calculations and supporting documentation showing the bending results in acceptable thicknesses before Section will be acceptable.

        - ******************************************************************************

No pipe or tube bends are allowed. Fittings are to be used instead of bends.

Erection

Install all piping shown on the construction drawings per manufacturer’s recommended procedures and this Section.

Deviations from locations identified on the drawings must be approved by LANL and documented for incorporation into as-built drawings.

Wedges shall not be used to laterally contain or position pipe for closure fit-ups.

        - ******************************************************************************

        - The following subparagraph is a designer choice.

        - ******************************************************************************

Flanged dielectric connections shall be installed with dielectric bolt insulators.

Drain piping shall slope downward in the direction of flow. The minimum slope or grade indicated on design documents shall be maintained regardless of other installation tolerance. If low points cannot be avoided on pressurized lines, a ball valve the same size as the line with a threaded plug in the outlet shall be provided at the low point.

Identification and/or traceability marks of piping components shall not be removed or hidden by surface treatment, coating, or subdividing during installation unless other identification methods are implemented to ensure that all markings are properly transferred, and traceability documentation is maintained for the components. Installer must verify that items are correct for the installation and have legible identification markings.

        - ******************************************************************************

        - Designer shall select headings below to match the joint types of piping, components, and/or connected equipment.

        - ******************************************************************************

Welded, brazed, or soldered joints:

Welded, brazed, or soldered joining of piping/tubing and components shall be per Section ​<< 01 4631 - Welding, Brazing, and Soldering of Pressure Systems>>​.

When welding, brazing, or soldering piping/tubing to a valve, follow manufacturer’s instructions to prevent heat damage to valve internals.

Threaded joints:

Compound or lubricant used on bolt threads shall be suitable for the service conditions and shall not react unfavorably with either the service fluid or the piping material. Refer to manufacturer’s recommendations for suitable compounds and lubricants. Lubricant for stainless steel shall contain no chlorides.

The threaded joint assembly shall be in accordance with <<ASME B1.20.1>> paragraph 3.1.9 Wrench-Tight Engagement between External and Internal Taper Threads.

No more than six and no less than two threads visible after makeup of the joint.

Severe chipping or tearing of visible threads is not permitted.

Bolted joints:

Assemble flanges per Section ​<< 01 4731 - Flange Assembly for Pressure Systems>>​.

Swagelok Compression joints:

Swagelok compression joints shall be installed per Swagelok Tube Fitter’s Manual, MS-13-03 (latest edition).

Flare Joint 45-Degree (<<SAE J513>>) joints:

Cut tubing squarely and clean tube end thoroughly to remove burrs.

Place nut onto tube. Place threaded end of nut toward end of tube.

Flare tube end with flaring tool to provide 45-degree flare.

No scratches, breaks, or other mars at sealing surface of flare shall be permitted.

Clamp tube flare between nut and nose of fitting body by screwing nut on finger-tight.  Tighten with a wrench an additional 1/4 turn for a metal-to-metal seal.

Flare Joint, 37-Degree (<<SAE J514>>) joints:

Flaring of the tubing shall meet the manufacturer’s requirements.

Power flaring is quicker and produces more accurate and consistent flares compared to hand flaring. Therefore, it is the preferred method of flaring. Hand flaring should be limited to places where power flaring tools are not readily available.

Cut tubing squarely and clean tube end thoroughly to remove burrs.

Place nut and sleeve if used onto tube in the proper sequence. Place threaded end of nut toward end of tube.

Flare tube end with flaring tool.  Flares will be within the minimum and maximum flare outside diameters.  Inspect flare for surface quality.

No scratches, breaks, or other mars at sealing surface of flare shall be permitted.

Align the component and hand tighten fitting.  With proper tube flare alignment with the nose of the fitting, tighten the nut to appropriate torque value shown in the manufacturer’s literature.

Torque tolerances:

2 ft-lbs if torque value is 50 ft-lbs or less

4 ft-lbs if torque value is greater than 50 but less than 100 ft-lbs

4 percent of torque value if greater than 100 ft-lbs.

        - ******************************************************************************

        - The following subparagraph is a designer choice.

        - ******************************************************************************

Underground Piping:

Do not install underground piping when the bedding is wet or frozen.

Verify that excavations are to the required grade and depth.

Trenching, backfill, soil compaction and testing for underground pipe shall be in accordance with Section << 31 2000 - Earth Moving>>.

Provide cover, bedding, warning tape, and tracer wire per trench details and below-grade piping details in accordance with Section << 31 2000 - Earth Moving>>.

        - ******************************************************************************

        - The following subparagraph is a designer choice.

        - ******************************************************************************

Double-Wall Piping

Installation of double-wall piping shall be planned and executed to ensure that all piping joints (except connections to existing piping), terminations, and transition flanges are leak tested as new construction. <<ASME B31.3>>​ Code Cases, B31 Case 180 may be used when examination of carrier pipe joints is not feasible; see New Construction Pressure/Leak Testing paragraph in Article << 3.3; or  _______>>, Examination, Inspection, and Testing.

EXAMINATION, INSPECTION, AND TESTING

For the purposes of this Section, the Subcontractor (Constructor) is responsible for all tasks identified as examination and testing.  LANL Owner’s Inspector activities are considered inspection.

      - ***************************************************************************************

      - Include the following two paragraphs when welded, brazed, or soldered joints are specified in this Section.

      - ***************************************************************************************

All welding, brazing and soldering: Inspected, examined, and tested in accordance with Section(s) ​<< 01 4631 - Welding, Brazing, and Soldering of Pressure Systems; and  01 4525 - Non-Destructive Examination (NDE) Requirements>>​.

Externally the pressure system shall be free of weld slag, flux, and weld spatter.

Contact LANL Owner’s Inspector to determine the initial inspection points (minimum hold points).

LANL Owner’s Inspector shall have access to any and all design, fabrication, manufacture, fabrication, heat treatment, assembly, erection, examination, testing, records, documentation and other project information or activities to verify that all required examinations and testing have been completed and to inspect the piping to the extent necessary to be satisfied that it conforms to all applicable examination requirements of the Code and of the engineering design and to perform the role defined in <<ASME B31.3>>.

LANL Owner’s Inspector is the final authority on acceptance of the project examination or test.

Examination activities to verify the quality of the work must be performed by persons other than those who performed the activity being examined. Such persons must not report directly to the immediate supervisors responsible for work being examined.

The fabrication documentation must have evidence of the examination, the evidence must be maintained in the pressure system documentation package submitted to the pressure safety officer.

Pipe examinations shall be performed after fabrication, after required heat treatment, and before leak testing.

Both the extent of examination and acceptance criteria shall be in accordance with <<ASME B31.3>> paragraph 341 examination and Section A341 examination for non-metallic systems, as applicable.

When pneumatic testing is planned, 100 percent of all threaded, bolted, and other mechanical joints shall be examined.

Any items rejected because of defects shall be repaired, replaced, and examined per this Section and <<ASME B31.3>>.

Methods of examination shall be per <<ASME B31.3>> Section 344.

In-process examination of welds << may; or  may not>> replace radiographic << or; or  and>> ultrasonic volumetric analysis for << all; or  _______>>​ welding per <<ASME B31.3>> paragraph 344.7 in-process examination.

New Construction Pressure/Leak Testing

        - ******************************************************************************

        - Certified examiners are not required for code leak tests except when specified by the code, for example ASME B31.3 para. 345.8 Sensitive Leak Testing.

        - The designer has the discretion to require certified leak test examiners and examination procedures.

        - When multiple process piping systems of the same type are present, specify testing requirements for each individual system.

        - ******************************************************************************

Pressure/leak test piping system per Section << 22 0813 - Testing Piping Systems>>.

In all cases when testing above design pressure, reduce pressure to design prior to checking for leakage.

        - ******************************************************************************

        - Note: ASME B31.3 paragraph 345.2.2 only requires the test pressure to be maintained a minimum of 10 minutes. Sensitive leak test for double-wall containment piping is required to meet B31.3 Code Cases, B31 Case 180 for the carrier (inner) pipe.  ASTM E1003 Section 10 Pressure Drop method must be held for 100 minutes minimum (recommend 200 minutes) for this method.

        - Designer to select only the subparagraphs below to match pressure systems applicable to the project.

        - ******************************************************************************

Vacuum Piping: Evacuate to 1mm Hg (1 Torr or 1000 microns) measured with an electronic manometer or thermocouple gauge.  After 2 hours, if vacuum level has risen to no higher than 2.5 mm Hg (2.5 Torr or 2500 microns), the leak test is acceptable.

Piping subject to external pressure shall be tested at 1.5 times the external differential pressure, but not less than 15 psig.

Hazardous Waste, Radioactive Liquid Waste (RLW), and Vent Double-Wall Containment Piping:

Inner Pipe and Vent: If inner pipe joints can be examined, test with water at << 5; or  _______>> psig +/- << ______>>  psig for << 10; or  _______>> minutes. If inner pipe joints cannot be examined, test with water at << 5; or  _______>> psig +/- << ______>> psig for at least 100 minutes in accordance with <<ASME B31.3>> Code Cases, B31 Case 180.

Outer Pipe: Test with water at << 5; or  _______>> psig +/- << ______>> psig for << 10; or  _______>> minutes including requirements specified in manufacturer’s written instructions, if applicable.

Reverse Osmosis (RO) Water Piping:

RO piping shall be leak tested with potable water at 1.5 times system design pressure.  Test pressure << _______>> psig +/-<< _______>>  psig per <<ASME B31.3>> paragraph 345.4 and shall show no drop in pressure in a two-hour period. Calibrated gauges are required.

Upon completion of the leak testing, all piping installed shall be cleaned with chlorinated water (sodium hypochlorite, 500 ppm) for a four-hour period. After the four-hour cleaning, drain the chlorinated water and thoroughly flush piping with deionized water.

        - ******************************************************************************

        - ASME B31.3 pneumatic test pressure shall be between 1.1 and 1.33 times design pressure.

        - ******************************************************************************

Laboratory Gas Piping (Category Normal)

Test piping with oil-free, dry cylinder << nitrogen; or  air>>​ at << _______>> psig +/- << _______>> psig per <<ASME B31.3>> paragraph 345.5 Pneumatic Leak Test for at least 10 minutes.

Laboratory Gas Piping (Category D)

Test piping with system fluid at << _______>> psig +/- << _______>>  psig per <<ASME B31.3>> paragraph 345.7 Initial Service Leak Test for at least 10 minutes.

        - ******************************************************************************

        - For any process fluids not addressed above, test pressure and duration may be specified below. Designer shall provide a unique set of testing requirements for each unique pressure system.

        - Category Normal piping may be tested per ASME B31.3 when possible hydrostatically per ASME B31.3 para. 345.4. Pneumatic leak tests per ASME B31.3 para. 345.5 are permitted when hydrostatic leak tests are impracticable (see ASME B31.3 para. 345).

        - PVC and CPVC piping shall not be pneumatically tested.

        - ******************************************************************************

Other Process Piping (<<ASME B31.3>>):

Category Normal, Metallic Pipe – system fluid << _______>>

Category Normal piping shall be << hydrostatically; or  pneumatically>> leak tested at << 225; or  _______>> psig +/- << _______>> psig. Leak test pressure shall be maintained for at least 10 minutes.

Category D, Metallic Pipe – system fluid << _______>>

Category D piping shall be tested per <<ASME B31.3>> paragraph 345.7 Initial Service Leak Test. Leak test at << ______>> psig +/- << _______>> psig for at least 10 minutes.

Category M, Metallic Pipe – system fluid << _______>>

Category M piping shall be leak tested at << _______>> psig +/- << _______>> psig per <<ASME B31.3>> paragraph << 354.4; or  345.5>> for at least 10 minutes.

Category M piping shall also be sensitive leak tested per <<ASME B31.3>>​ paragraphs M345 and 345.8. A certified examiner with a procedure that can demonstrate sensitivity not less than 10-3 std mL/s is required for the sensitive leak test.

Category << Normal; or  D>> Non-Metallic Pipe – system fluid << _______>>

Test non-metallic (plastic) pipe per <<ASME B31.3>>, para A345 for the applicable <<ASME B31.3>>​ Fluid Category. Leak test at << 225; or  _______>> psig +/- << _______>>  psig for at least 10 minutes.

        - ******************************************************************************

        - When connecting to existing piping, piping joints for ASME B31.3 pressure systems shall be leak tested in accordance with LANL ESM Chapter 17 - Pressure Safety, Section PS-REQUIREMENTS, 10.3 Pressure and Leak Testing.

        - This includes the bagging of potentially radioactive contaminated pressure or vacuum joints where bags are used to cover the joint to verify the joint is leak free as part of an initial service leak test of the joint.  The bag is then evaluated using standard radiological processes to verify there is no contamination before the gas is removed.

        - ******************************************************************************

Leak/Pressure Testing Connections to Existing Piping

For modifications to existing piping, test the connection between new and existing piping at normal operating pressure. Bring system up to operating pressure gradually. Visually examine the piping for leaks at one-half the system operating pressure. Perform a final examination at the system operating pressure. No leaking from the piping indicates that the system meets the requirement of the project.

      - ***************************************************************************************

      - The following two rows are designer choices. Include the first if appendices are to be included; include the second if no appendices.

      - ***************************************************************************************

END OF MAIN SECTION; APPENDICES FOLLOW

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 40 0504, REV. 3, DATED APRIL 15, 2026.

    - **********************************************************************************************

      - If used, attach the appendices at the end of this Section & select appendix numbers below as applicable.

      - The 40 0504 Appendices are located on the Engineering Standards website at the link below (copy and paste link in a browser to download file): http://engstandards.lanl.gov/specs/40-0504-App.docx

    - **********************************************************************************************

40 0504 Appendix A

40 0504 Appendix B

40 0504 Appendix C

40 0504 Appendix D

40 0504 APPENDIX ​​<< _______>>​​